## Component UR
Summary of SPAR Component Unreliability Data and Results
Component Failure Mode | Description | Data Source | Data | [5 empty] | Industry-average Failure Probability or Rate Distribution (note a) | [8 empty] | Comments (see Appendix A for details) | [5 empty] | Effective Date
|  |  | Failures | Demands or Hours | d or h | Components | MLE | Jeffreys Mean | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Error Factor |  |  | 95% | Median | 95% | Median
ABT FTOP | Automatic Bus Transfer Switch Fail to Operate | EPIX | 0 | 163 | d | 23 | 0 | 0.0030488 | Beta (Jeffreys, SCNID) | 0.0030488 | 0.5 | 163.5 | 8.4003 | 0.003 | 0.5 | 166.1667 | 8.401 | 0 events for 1998 - 2002, so 1997 - 2004 data used |  | 0.01151 | 0.00137 | 0.011697 | 0.0013924 | 2007-02-01
ACC ELS | Air Accumulator External Leak Small | EPIX | 3 | 67346880 | h | 961 | 4.4545e-08 | 5.197e-08 | Gamma (EB/PL/KS, LL) | 4.94e-08 | 0.3 | 6072874.4939 | 18.7656 | 5e-08 | 0.3 | 6000000 | 18.7656 | 1997 - 2004 data |  | 2.2873e-07 | 1.2189e-08 | 2.2598e-07 | 1.2042e-08 | 2007-02-01
ACC ELL | Air Accumulator External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 3.458e-09 | 0.3 | 86755349.9132 | 18.7656 | 3e-09 | 0.3 | 100000000 | 18.7656 | Small leak times 0.07 |  | 1.3724e-08 | 7.3131e-10 | 1.5819e-08 | 8.4296e-10 | 2007-02-01
ADU FTOP | Air Dryer Unit Fail to Operate | WSRC |  |  | h |  |  | 5e-06 | Gamma (WSRC, LL) | 5e-06 | 0.3 | 60000 | 18.7653 | 5e-06 | 0.3 | 60000 | 18.7656 |  |  | 2.2873e-05 | 1.2189e-06 | 2.2872e-05 | 1.2189e-06 | 2007-02-01
AHU RUN FTR | Air Handling Unit (Running) Fail to Run | EPIX | 24 | 4864939 | h | 176 | 4.9333e-06 | 5.036e-06 | Gamma (EB/PL/KS, LL) | 1.37e-05 | 0.3 | 21897.8102 | 18.7656 | 1.5e-05 | 0.3 | 20000 | 18.7656 |  |  | 6.8618e-05 | 3.6566e-06 | 6.2671e-05 | 3.3397e-06 | 2007-02-01
AHU RUN FTS | Air Handling Unit (Running) Fail to Start | EPIX | 31 | 15484 | d | 176 | 0.0020021 | 0.0020342 | Beta (EB/PL/KS, LL) | 0.00273 | 0.3 | 109.5901 | 18.6544 | 0.0025 | 0.3 | 119.7 | 18.6638 |  |  | 0.011433 | 0.00061256 | 0.012484 | 0.00066923 | 2007-02-01
AHU STBY FTR≤1H | Air Handling Unit (Standby) Fail to Run During First Hour of Operation | EPIX | 4 | 6965 | h | 56 | 0.0005743 | 0.00064609 | Gamma (EB/PL/KS, LL) | 0.00228 | 0.3 | 131.5789 | 18.7656 | 0.0025 | 0.3 | 120 | 18.7656 |  |  | 0.011436 | 0.00060943 | 0.01043 | 0.0005558 | 2007-02-01
AHU STBY FTR>1H | Air Handling Unit (Standby) Fail to Run After First Hour of Operation | EPIX | 0 | 131445 | h | 175 | 0 | 3.8039e-06 | Gamma (Jeffreys, SCNID) | 3.8039e-06 | 0.5 | 131445 | 8.4439 | 4e-06 | 0.5 | 125000 | 8.4439 |  |  | 1.5366e-05 | 1.8197e-06 | 1.4612e-05 | 1.7305e-06 | 2007-02-01
AHU STBY FTS | Air Handling Unit (Standby) Fail to Start | EPIX | 10 | 22251 | d | 231 | 0.00044942 | 0.00047187 | Beta (EB/PL/KS, EB/PL/KS) | 0.000829 | 0.36 | 433.8981 | 13.5006 | 0.0008 | 0.4 | 499.6 | 11.4383 |  |  | 0.003323 | 0.00029052 | 0.00357 | 0.00026443 | 2007-02-01
AOV FC | Air-Operated Valve Fail to Control | WSRC |  |  | h |  |  | 3e-06 | Gamma(WSRC, LL) | 3e-06 | 0.3 | 100000 | 18.7655 | 3e-06 | 0.3 | 100000 | 18.7656 |  |  | 1.3724e-05 | 7.3131e-07 | 1.3723e-05 | 7.3131e-07 | 2007-02-01
AOV FTO/C | Air-Operated Valve Fail to Open or Close | EPIX | 76 | 80117 | d | 2756 | 0.00094861 | 0.00095484 | Beta (EB/PL/KS, EB/PL/KS) | 0.00111 | 1.005 | 904.4004 | 4.3003 | 0.0012 | 1 | 832.3333 | 4.316 |  |  | 0.0035927 | 0.00083243 | 0.0033176 | 0.00077147 | 2007-02-01
AOV SO | Air-Operated Valve Spurious Operation | EPIX | 20 | 120712800 | h | 2756 | 1.6568e-07 | 1.6982e-07 | Gamma (EB/PL/KS, LL) | 1.82e-07 | 0.3 | 1648351.6484 | 18.7656 | 2e-07 | 0.3 | 1500000 | 18.7656 |  |  | 9.149e-07 | 4.8754e-08 | 8.3256e-07 | 4.4366e-08 | 2007-02-01
AOV ELS | Air-Operated Valve External Leak Small | EPIX | 2 | 194191680 | h | 2771 | 1.0299e-08 | 1.2874e-08 | Gamma (Jeffreys, SCNID) | 1.2874e-08 | 0.5 | 38838336 | 8.4439 | 1.2e-08 | 0.5 | 41666666.6667 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 4.6098e-08 | 5.4592e-09 | 4.9454e-08 | 5.8568e-09 | 2007-02-01
AOV ELL | Air-Operated Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 9.0117e-10 | 0.3 | 332900022.8571 | 18.7656 | 9e-10 | 0.3 | 333333333.3333 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 4.1171e-09 | 2.1939e-10 | 4.1224e-09 | 2.1968e-10 | 2007-02-01
AOV ILS | Air-Operated Valve Internal Leak Small | EPIX | 49 | 194191680 | h | 2771 | 2.5233e-07 | 2.549e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 2.42e-07 | 0.661 | 2731404.9587 | 6.1855 | 2.5e-07 | 0.7 | 2800000 | 5.848 | 1 to 50 gpm. 1997 - 2004 data. |  | 8.5094e-07 | 1.4551e-07 | 8.4092e-07 | 1.3595e-07 | 2007-02-01
AOV ILL | Air-Operated Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 4.84e-09 | 0.3 | 61983471.0744 | 18.7656 | 5e-09 | 0.3 | 60000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 2.2873e-08 | 1.2189e-09 | 2.2141e-08 | 1.1798e-09 | 2007-02-01
BAT FTOP | Battery (dc) Fail to Operate | EPIX | 27 | 15899400 | h | 363 | 1.6982e-06 | 1.7296e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 1.86e-06 | 0.427 | 229569.8925 | 10.4135 | 2e-06 | 0.4 | 200000 | 11.4556 |  |  | 8.3098e-06 | 7.2539e-07 | 7.5546e-06 | 7.2546e-07 | 2007-02-01
BCH FTOP | Battery Charger Fail to Operate | EPIX | 80 | 17169600 | h | 392 | 4.6594e-06 | 4.6885e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 5.08e-06 | 1.585 | 312007.874 | 3.1995 | 5e-06 | 1.5 | 300000 | 3.303 |  |  | 1.3025e-05 | 3.9433e-06 | 1.2992e-05 | 4.0607e-06 | 2007-02-01
BIS FTOP | Bistable Fail to Operate | RPS SSs | 55 | 102094 | d |  | 0.00053872 | 0.00054362 | Beta (Jeffreys, SCNID) | 0.00054362 | 0.5 | 919.2658 | 8.4439 | 0.0005 | 0.5 | 999.5 | 8.4368 |  |  | 0.0019203 | 0.00022761 | 0.0020894 | 0.00024745 | 2007-02-01
BUS FTOP | Bus Fail to Operate | EPIX | 3 | 7183200 | h | 164 | 4.1764e-07 | 4.8725e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 4.34e-07 | 0.502 | 1156682.0276 | 8.4022 | 4e-07 | 0.5 | 1250000 | 8.4439 |  |  | 1.5366e-06 | 1.8197e-07 | 1.6648e-06 | 1.9814e-07 | 2007-02-01
CBK FTO/C | Circuit Breaker Fail to Open or Close | EPIX | 83 | 50226 | d | 4022 | 0.0016525 | 0.0016625 | Beta (EB/PL/KS, EB/PL/KS) | 0.00255 | 0.698 | 273.0275 | 5.8429 | 0.0025 | 0.7 | 279.3 | 5.8274 |  |  | 0.0084989 | 0.0014585 | 0.0086777 | 0.0014852 | 2007-02-01
CBK SO | Circuit Breaker Spurious Operation | EPIX | 28 | 176163600 | h | 4022 | 1.5894e-07 | 1.6178e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 1.71e-07 | 1.983 | 11596491.2281 | 2.8386 | 1.5e-07 | 2 | 13333333.3333 | 2.8265 |  |  | 3.5579e-07 | 1.2588e-07 | 4.067e-07 | 1.4327e-07 | 2007-02-01
CHL RUN FTR | Chiller (Running) Fail to Run | EPIX | 164 | 3402465 | h | 113 | 4.82e-05 | 4.8347e-05 | Gamma (EB/PL/KS, EB/PL/KS) | 9.42e-05 | 0.489 | 5191.0828 | 8.6829 | 9e-05 | 0.5 | 5555.5556 | 8.4439 |  |  | 0.00034573 | 4.0944e-05 | 0.00036474 | 4.2007e-05 | 2007-02-01
CHL RUN FTS | Chiller (Running) Fail to Start | EPIX | 66 | 6483 | d | 113 | 0.01018 | 0.010256 | Beta (EB/PL/KS, EB/PL/KS) | 0.00983 | 0.818 | 82.3966 | 5.0131 | 0.01 | 0.8 | 79.2 | 5.1084 |  |  | 0.032276 | 0.0063181 | 0.031477 | 0.006279 | 2007-02-01
CHL STBY FTR≤1H | Chiller (Standby) Fail to Run During First Hour of Operation | EPIX | 5 | 2401 | h | 38 | 0.0020825 | 0.0022907 | Gamma (Jeffreys, Jeffreys) | 0.0022907 | 5.5 | 2401 | 1.9026 | 0.0025 | 5 | 2000 | 1.9597 |  |  | 0.0045768 | 0.0023355 | 0.0040973 | 0.0021535 | 2007-02-01
CHL STBY FTR>1H | Chiller (Standby) Fail to Run After First Hour of Operation | EPIX | 13.7 | 16427 | h | 21 | 0.00083399 | 0.00086443 | Gamma (Jeffreys, SCNID) | 0.00086443 | 0.5 | 578.4155 | 8.4439 | 0.0009 | 0.5 | 555.5556 | 8.4439 |  |  | 0.0034573 | 0.00040944 | 0.0033207 | 0.00039326 | 2007-02-01
CHL STBY FTS | Chiller (Standby) Fail to Start | EPIX | 10 | 5470 | d | 59 | 0.0018282 | 0.0019192 | Beta (Jeffreys, SCNID) | 0.0019192 | 0.5 | 260.0238 | 8.4165 | 0.002 | 0.5 | 249.5 | 8.4153 |  |  | 0.0076764 | 0.00091219 | 0.0073666 | 0.00087526 | 2007-02-01
CKV FTC | Check Valve Fail to Close | EPIX | 2 | 24090 | d | 729 | 8.3022e-05 | 0.00010377 | Beta (Jeffreys, SCNID) | 0.00010377 | 0.5 | 4817.7 | 8.4425 | 0.0001 | 0.5 | 4999.5 | 8.4425 |  |  | 0.00038413 | 4.5499e-05 | 0.00039862 | 4.7216e-05 | 2007-02-01
CKV FTO | Check Valve Fail to Open | EPIX | 0 | 38550 | d | 729 | 0 | 1.297e-05 | Beta (Jeffreys, SCNID) | 1.297e-05 | 0.5 | 38550.5 | 8.4438 | 1.2e-05 | 0.5 | 41666.1667 | 8.4438 | 0 events for 1998 - 2002, so 1997 - 2004 data used |  | 4.6097e-05 | 5.4593e-06 | 4.9823e-05 | 5.9005e-06 | 2007-02-01
CKV ELS | Check Valve External Leak Small | EPIX | 1 | 51088320 | h | 729 | 1.9574e-08 | 2.9361e-08 | Gamma (Jeffreys, SCNID) | 2.9361e-08 | 0.5 | 17029440 | 8.4439 | 3e-08 | 0.5 | 16666666.6667 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.1524e-07 | 1.3648e-08 | 1.1279e-07 | 1.3357e-08 | 2007-02-01
CKV ELL | Check Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 2.0553e-09 | 0.3 | 145966628.5714 | 18.7656 | 2e-09 | 0.3 | 150000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 9.149e-09 | 4.8754e-10 | 9.4018e-09 | 5.0101e-10 | 2007-02-01
CKV ILS | Check Valve Internal Leak Small | EPIX | 23 | 51088320 | h | 729 | 4.502e-07 | 4.5999e-07 | Gamma (EB/PL/KS, LL) | 1.48e-06 | 0.3 | 202702.7027 | 18.7656 | 1.5e-06 | 0.3 | 200000 | 18.7656 | 1 to 50 gpm. 1997 - 2004 data. |  | 6.8618e-06 | 3.6566e-07 | 6.7703e-06 | 3.6078e-07 | 2007-02-01
CKV ILL | Check Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 2.96e-08 | 0.3 | 10135135.1351 | 18.7656 | 3e-08 | 0.3 | 10000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 1.3724e-07 | 7.3131e-09 | 1.3541e-07 | 7.2156e-09 | 2007-02-01
CRD FTOP | Control Rod Drive Fail to Operate | RPS SSs | 2 | 189536 | d |  | 1.0552e-05 | 1.319e-05 | Beta (Jeffreys, SCNID) | 1.319e-05 | 0.5 | 37906.7 | 8.4438 | 1.2e-05 | 0.5 | 41666.1667 | 8.4438 |  |  | 4.6097e-05 | 5.4593e-06 | 5.0669e-05 | 6.0008e-06 | 2007-02-01
CTF RUN FTR | Cooling Tower Fan (Running) Fail to Run | EPIX | 0 | 839875 | h | 34 | 0 | 5.9533e-07 | Gamma (Jeffreys, SCNID) | 5.9533e-07 | 0.5 | 839875 | 8.4439 | 6e-07 | 0.5 | 833333.3333 | 8.4439 |  |  | 2.3049e-06 | 2.7296e-07 | 2.2869e-06 | 2.7084e-07 | 2007-02-01
CTF RUN FTS | Cooling Tower Fan (Running) Fail to Start | EPIX | 1 | 13855 | d | 34 | 7.2176e-05 | 0.00010826 | Beta (Jeffreys, SCNID) | 0.00010826 | 0.5 | 4618.1667 | 8.4424 | 0.0001 | 0.5 | 4999.5 | 8.4425 |  |  | 0.00038413 | 4.5499e-05 | 0.00041584 | 4.9256e-05 | 2007-02-01
CTF STBY FTR≤1H | Cooling Tower Fan (Standby) Fail to Run During First Hour of Operation | EPIX | 2 | 1515 | h | 31 | 0.0013201 | 0.0016502 | Gamma (Jeffreys, SCNID) | 0.0016502 | 0.5 | 303 | 8.4439 | 0.0015 | 0.5 | 333.3333 | 8.4439 |  |  | 0.0057622 | 0.0006824 | 0.006339 | 0.00075072 | 2007-02-01
CTF STBY FTR>1H | Cooling Tower Fan (Standby) Fail to Run After First Hour of Operation | EPIX | 0 | 11133 | h | 31 | 0 | 4.4912e-05 | Gamma (Jeffreys, SCNID) | 4.4912e-05 | 0.5 | 11133 | 8.4439 | 4e-05 | 0.5 | 12500 | 8.4439 |  |  | 0.00015366 | 1.8197e-05 | 0.00017253 | 2.0432e-05 | 2007-02-01
CTF STBY FTS | Cooling Tower Fan (Standby) Fail to Start | EPIX | 3 | 1515 | d | 31 | 0.0019802 | 0.0023087 | Beta (Jeffreys, SCNID) | 0.0023087 | 0.5 | 216.0714 | 8.4109 | 0.0025 | 0.5 | 199.5 | 8.4082 |  |  | 0.0095935 | 0.001141 | 0.0088601 | 0.0010534 | 2007-02-01
CTG STBY FTLR | Combustion Turbine Generator (Standby) Fail to Load and Run During First Hour of Operation | EPIX | 0 | 267 | d | 2 | 0 | 0.0018657 | Beta (Jeffreys, SCNID) | 0.0018657 | 0.5 | 268 | 8.4439 | 0.002 | 0.5 | 250 | 8.4439 | 1998 - 3Q2004 data used |  | 0.0076829 | 0.00090987 | 0.0071669 | 0.00084876 | 2007-02-01
CTG STBY FTR>1H | Combustion Turbine Generator (Standby) Fail to Run After First Hour of Operation | EPIX | 0 | 16 | h | 2 | 0 | 0.03125 | Gamma (EDG FTR, SCNID) | 0.000848 | 0.3 | 353.7736 | 18.7656 | 0.0008 | 0.3 | 375 | 18.7656 | 1998 - 3Q2004 data used. Data limited so EDG FTR used |  | 0.0036596 | 0.00019502 | 0.0038792 | 0.00020672 | 2007-02-01
CTG STBY FTS | Combustion Turbine Generator (Standby) Fail to Start | EPIX | 6 | 267 | d | 2 | 0.022472 | 0.024254 | Beta (Jeffreys, SCNID) | 0.024254 | 0.5 | 20.1154 | 8.0941 | 0.025 | 0.5 | 19.5 | 8.0832 | 1998 - 3Q2004 data used |  | 0.094944 | 0.011746 | 0.092144 | 0.011384 | 2007-02-01
DDP STBY FTR≤1H | Diesel-Driven Pump (Standby) Fail to Run During First Hour of Operation | EPIX | 4 | 3277 | h | 27 | 0.0012206 | 0.0013732 | Gamma (EB/PL/KS, LL) | 0.00158 | 0.3 | 189.8734 | 18.7656 | 0.0015 | 0.3 | 200 | 18.7656 |  |  | 0.0068618 | 0.00036566 | 0.0072277 | 0.00038516 | 2007-02-01
DDP STBY FTR>1H | Diesel-Driven Pump (Standby) Fail to Run After First Hour of Operation | EPIX | No data |  | h |  |  |  | Gamma (FTR≤1H*0.06, LL) | 9.48e-05 | 0.3 | 3164.557 | 18.7656 | 9e-05 | 0.3 | 3333.3333 | 18.7656 | No data. FTR≤1H times 0.06 | 2005-10-04 | 0.00041171 | 2.1939e-05 | 0.00043366 | 2.3109e-05 | 2007-02-01
DDP STBY FTS | Diesel-Driven Pump (Standby) Fail to Start | EPIX | 9 | 5161 | d | 27 | 0.0017438 | 0.0018404 | Beta (EB/PL/KS, LL) | 0.00388 | 0.3 | 77.0196 | 18.6073 | 0.004 | 0.3 | 74.7 | 18.6025 |  |  | 0.018288 | 0.00098312 | 0.01774 | 0.00095339 | 2007-02-01
DDP ELS | Diesel-Driven Pump External Leak Small | EPIX | 0 | 2032320 | h | 29 | 0 | 2.4602e-07 | Gamma (Jeffreys, SCNID) | 2.4602e-07 | 0.5 | 2032320 | 8.4439 | 2.5e-07 | 0.5 | 2000000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 9.6036e-07 | 1.1373e-07 | 9.4509e-07 | 1.1193e-07 | 2007-02-01
DDP ELL | Diesel-Driven Pump External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 1.7222e-08 | 0.3 | 17419885.7143 | 18.7656 | 1.5e-08 | 0.3 | 20000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 6.8618e-08 | 3.6566e-09 | 7.8781e-08 | 4.1981e-09 | 2007-02-01
EDG STBY FTLR | Emergency Diesel Generator (Standby) Fail to Load and Run During First Hour of Operation | EPIX | 61 | 21342 | d | 225 | 0.0028582 | 0.0028815 | Beta (EB/PL/KS, EB/PL/KS) | 0.0029 | 1.411 | 486.5517 | 3.4257 | 0.003 | 1.5 | 500 | 3.303 |  |  | 0.0078147 | 0.002366 | 0.0077112 | 0.002251 | 2007-02-01
EDG STBY FTR>1H | Emergency Diesel Generator (Standby) Fail to Run After First Hour of Operation | EPIX | 50 | 59875 | h | 225 | 0.00083507 | 0.00084342 | Gamma (EB/PL/KS, EB/PL/KS) | 0.000848 | 2.01 | 2370.283 | 2.8195 | 0.0008 | 2 | 2500 | 2.8265 |  |  | 0.0018975 | 0.00067134 | 0.0020082 | 0.00071227 | 2007-02-01
EDG STBY FTS | Emergency Diesel Generator (Standby) Fail to Start | EPIX | 98 | 24206 | d | 225 | 0.0040486 | 0.0040691 | Beta (EB/PL/KS, EB/PL/KS) | 0.00453 | 1.075 | 236.2318 | 4.0783 | 0.005 | 1 | 199 | 4.297 |  |  | 0.014941 | 0.0034771 | 0.0132 | 0.0032365 | 2007-02-01
EOV FTO | Explosive-Operated Valve Fail to Open | EPIX | 0 | 468 | d | 53 | 0 | 0.0010661 | Beta (Jeffreys, SCNID) | 0.0010661 | 0.5 | 468.5 | 8.4287 | 0.001 | 0.5 | 499.5 | 8.4296 |  | 2005-10-04 | 0.0038398 | 0.00045552 | 0.0040935 | 0.00048567 | 2007-02-01
FAN RUN FTR | Fan (Running) Fail to Run | EPIX | 57 | 6279790 | h | 234 | 9.0767e-06 | 9.1564e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 1.08e-05 | 0.652 | 60370.3704 | 6.2713 | 1e-05 | 0.7 | 70000 | 5.848 |  |  | 3.4037e-05 | 5.8203e-06 | 3.7715e-05 | 6.0139e-06 | 2007-02-01
FAN RUN FTS | Fan (Running) Fail to Start | EPIX | 18 | 24024 | d | 234 | 0.00074925 | 0.00077003 | Beta (EB/PL/KS, LL) | 0.00179 | 0.3 | 167.2978 | 18.6928 | 0.002 | 0.3 | 149.7 | 18.6842 |  |  | 0.0091467 | 0.00048954 | 0.0081865 | 0.00043795 | 2007-02-01
FAN STBY FTR≤1H | Fan (Standby) Fail to Run During First Hour of Operation | EPIX | 19 | 17019 | h | 145 | 0.0011164 | 0.0011458 | Gamma (EB/PL/KS, EB/PL/KS) | 0.00191 | 0.348 | 182.199 | 14.3135 | 0.002 | 0.3 | 150 | 18.7656 |  |  | 0.009149 | 0.00048754 | 0.0083215 | 0.00058138 | 2007-02-01
FAN STBY FTR>1H | Fan (Standby) Fail to Run After First Hour of Operation | EPIX | 8 | 76434 | h | 103 | 0.00010467 | 0.00011121 | Gamma (Jeffreys, SCNID) | 0.00011121 | 8.5 | 76434 | 1.6885 | 0.00012 | 8 | 66666.6667 | 1.7144 |  |  | 0.00019722 | 0.00011504 | 0.00018046 | 0.00010688 | 2007-02-01
FAN STBY FTS | Fan (Standby) Fail to Start | EPIX | 33 | 25099 | d | 248 | 0.0013148 | 0.0013347 | Beta (EB/PL/KS, LL) | 0.00289 | 0.3 | 103.5062 | 18.6479 | 0.003 | 0.3 | 99.7 | 18.6434 |  |  | 0.013718 | 0.00073582 | 0.013215 | 0.00070868 | 2007-02-01
FLT PLG (CLEAN) | Filter Plug (Clean Water System) | EPIX | 1 | 15207360 | h | 217 | 6.5758e-08 | 9.8636e-08 | Gamma (Jeffreys, SCNID) | 9.8636e-08 | 0.5 | 5069120.3333 | 8.4439 | 1e-07 | 0.5 | 5000000 | 8.4439 |  |  | 3.8415e-07 | 4.5494e-08 | 3.7891e-07 | 4.4873e-08 | 2007-02-01
HOD FTO/C | Hydraulic-Operated Damper Fail to Open or Close | EPIX | 7 | 5341 | d | 113 | 0.0013106 | 0.001404 | Beta (EB/PL/KS, LL) | 0.00261 | 0.3 | 114.6425 | 18.6593 | 0.0025 | 0.3 | 119.7 | 18.6638 |  |  | 0.011433 | 0.00061256 | 0.011935 | 0.00063965 | 2007-02-01
HOD SO | Hydraulic-Operated Damper Spurious Operation | EPIX | 1 | 4949400 | h | 113 | 2.0204e-07 | 3.0307e-07 | Gamma (Jeffreys, SCNID) | 3.0307e-07 | 0.5 | 1649800 | 8.4439 | 3e-07 | 0.5 | 1666666.6667 | 8.4439 |  |  | 1.1524e-06 | 1.3648e-07 | 1.1642e-06 | 1.3788e-07 | 2007-02-01
HOV FC | Hydraulic-Operated Valve Fail to Control | WSRC |  |  | h |  |  | 3e-06 | Gamma(WSRC, LL) | 3e-06 | 0.3 | 100000 | 18.7656 | 3e-06 | 0.3 | 100000 | 18.7656 |  |  | 1.3724e-05 | 7.3131e-07 | 1.3724e-05 | 7.3131e-07 | 2007-02-01
HOV FTO/C | Hydraulic-Operated Valve Fail to Open or Close | EPIX | 8 | 11827 | d | 558 | 0.00067642 | 0.00071863 | Beta (EB/PL/KS, LL) | 0.00151 | 0.3 | 198.3755 | 18.7042 | 0.0015 | 0.3 | 199.7 | 18.7045 |  |  | 0.0068605 | 0.00036678 | 0.0069062 | 0.00036923 | 2007-02-01
HOV SO | Hydraulic-Operated Valve Spurious Operation | EPIX | 6 | 24440400 | h | 558 | 2.455e-07 | 2.6595e-07 | Gamma (EB/PL/KS, LL) | 3.61e-07 | 0.3 | 831024.9307 | 18.7656 | 4e-07 | 0.3 | 750000 | 18.7656 |  |  | 1.8298e-06 | 9.7508e-08 | 1.6514e-06 | 8.8001e-08 | 2007-02-01
HOV ELS | Hydraulic-Operated Valve External Leak Small | EPIX | 0 | 33848640 | h | 483 | 0 | 1.4772e-08 | Gamma (Jeffreys, SCNID) | 1.4772e-08 | 0.5 | 33848640 | 8.4439 | 1.5e-08 | 0.5 | 33333333.3333 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 5.7622e-08 | 6.824e-09 | 5.6745e-08 | 6.7202e-09 | 2007-02-01
HOV ELL | Hydraulic-Operated Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 1.034e-09 | 0.3 | 290131200 | 18.7656 | 1e-09 | 0.3 | 300000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 4.5745e-09 | 2.4377e-10 | 4.7301e-09 | 2.5206e-10 | 2007-02-01
HOV ILS | Hydraulic-Operated Valve Internal Leak Small | EPIX | 1 | 39314880 | h | 561 | 2.5436e-08 | 3.8153e-08 | Gamma (Jeffreys, SCNID) | 3.8153e-08 | 0.5 | 13104960 | 8.4439 | 4e-08 | 0.5 | 12500000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.5366e-07 | 1.8197e-08 | 1.4657e-07 | 1.7357e-08 | 2007-02-01
HOV ILL | Hydraulic-Operated Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 7.6307e-10 | 0.3 | 393148800 | 18.7656 | 8e-10 | 0.3 | 375000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 3.6596e-09 | 1.9502e-10 | 3.4907e-09 | 1.8601e-10 | 2007-02-01
HTG STBY FTLR | Hydro Turbine Generator (Standby) Fail to Load and Run During First Hour of Operation | EPIX | 7 | 1767 | d | 2 | 0.0039615 | 0.0042421 | Beta (Jeffreys, SCNID) | 0.0042421 | 0.5 | 117.8667 | 8.4439 | 0.004 | 0.5 | 125 | 8.4439 | 1997 - 2004 data, additional input from plant |  | 0.015366 | 0.0018197 | 0.016296 | 0.0019299 | 2007-02-01
HTG STBY FTR>1H | Hydro Turbine Generator (Standby) Fail to Run After First Hour of Operation | EPIX | 1 | 6162 | h | 2 | 0.00016228 | 0.00024343 | Gamma (Jeffreys, SCNID) | 0.00024343 | 0.5 | 2054 | 8.4439 | 0.00025 | 0.5 | 2000 | 8.4439 | 1997 - 2004 data, additional input from plant |  | 0.00096036 | 0.00011373 | 0.00093512 | 0.00011074 | 2007-02-01
HTG STBY FTS | Hydro Turbine Generator (Standby) Fail to Start | EPIX | 6 | 3322 | d | 2 | 0.0018061 | 0.0019561 | Beta (Jeffreys, SCNID) | 0.0019561 | 0.5 | 255.1154 | 8.416 | 0.002 | 0.5 | 249.5 | 8.4153 | 1997 - 2004 data, additional input from plant |  | 0.0076764 | 0.00091219 | 0.0075079 | 0.0008921 | 2007-02-01
HTX PLG CCW/RHR | Heat Exchanger Plug/Foul (CCW or RHR) | EPIX | 20 | 31229400 | h | 713 | 6.4042e-07 | 6.5643e-07 | Gamma(EB/PL/KS, EB/PL/KS) | 6.45e-07 | 1.416 | 2195348.8372 | 3.4184 | 6e-07 | 1.5 | 2500000 | 3.303 | Data limited to CCW and RHR systems |  | 1.5629e-06 | 4.7319e-07 | 1.713e-06 | 5.0112e-07 | 2007-02-01
HTX SHELL ELS | Heat Exchanger Shell External Leak Small | EPIX | 2 | 49967040 | h | 713 | 4.0026e-08 | 5.0033e-08 | Gamma(Jeffreys, SCNID) | 5.0033e-08 | 0.5 | 9993408.2 | 8.4439 | 5e-08 | 0.5 | 10000000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.9207e-07 | 2.2747e-08 | 1.922e-07 | 2.2762e-08 | 2007-02-01
HTX SHELL ELL | Heat Exchanger Shell External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 3.5023e-09 | 0.3 | 85657784.5714 | 18.7656 | 4e-09 | 0.3 | 75000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.8298e-08 | 9.7508e-10 | 1.6021e-08 | 8.5376e-10 | 2007-02-01
HTX TUBE ELS | Heat Exchanger Tube External Leak Small | EPIX | 10 | 49967040 | h | 713 | 2.0013e-07 | 2.1014e-07 | Gamma (EB/PL/KS, LL) | 2.32e-07 | 0.3 | 1293103.4483 | 18.7656 | 2.5e-07 | 0.3 | 1200000 | 18.7656 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.1436e-06 | 6.0943e-08 | 1.0613e-06 | 5.6555e-08 | 2007-02-01
HTX TUBE ELL | Heat Exchanger Tube External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.15, LL) | 3.48e-08 | 0.3 | 8620689.6552 | 18.7656 | 3e-08 | 0.3 | 10000000 | 18.7656 | > 50 gpm. Small leak times 0.15. |  | 1.3724e-07 | 7.3131e-09 | 1.5919e-07 | 8.4832e-09 | 2007-02-01
INV FTOP | Inverter Fail to Operate | EPIX | 153 | 27944400 | h | 638 | 5.4752e-06 | 5.4931e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 5.28e-06 | 1.203 | 227840.9091 | 3.792 | 5e-06 | 1.2 | 240000 | 3.7983 |  |  | 1.4053e-05 | 3.6997e-06 | 1.4827e-05 | 3.9101e-06 | 2007-02-01
MDC RUN FTR | Motor-Driven Compressor (Running) Fail to Run | EPIX | 158 | 1989420 | h | 77 | 7.942e-05 | 7.9671e-05 | Gamma (EB/PL/KS, EB/PL/KS) | 9.16e-05 | 1.423 | 15534.9345 | 3.4082 | 9e-05 | 1.5 | 16666.6667 | 3.303 |  |  | 0.00023444 | 7.0979e-05 | 0.00024287 | 7.1261e-05 | 2007-02-01
MDC RUN FTS | Motor-Driven Compressor (Running) Fail to Start | EPIX | 36 | 8980 | d | 77 | 0.0040089 | 0.0040641 | Beta (EB/PL/KS, EB/PL/KS) | 0.0133 | 0.364 | 27.0044 | 12.9264 | 0.012 | 0.4 | 32.9333 | 11.1933 |  |  | 0.04965 | 0.0044357 | 0.056847 | 0.0043977 | 2007-02-01
MDC STBY FTR≤1H | Motor-Driven Compressor (Standby) Fail to Run During First Hour of Operation | EPIX | 3 | 939 | h | 5 | 0.0031949 | 0.0037274 | Gamma (EB/PL/KS, LL) | 0.00314 | 0.3 | 95.5414 | 18.7656 | 0.003 | 0.3 | 100 | 18.7656 |  |  | 0.013724 | 0.00073131 | 0.014364 | 0.00076544 | 2007-02-01
MDC STBY FTR>1H | Motor-Driven Compressor (Standby) Fail to Run After First Hour of Operation | EPIX | 17.9 | 10999 | h | 28 | 0.0016274 | 0.0016729 | Gamma (EB/PL/KS, EB/PL/KS) | 0.00262 | 1.696 | 647.3282 | 3.0811 | 0.0025 | 1.5 | 600 | 3.303 |  |  | 0.0065123 | 0.0019716 | 0.0065531 | 0.0021269 | 2007-02-01
MDC STBY FTS | Motor-Driven Compressor (Standby) Fail to Start | EPIX | 15 | 2150 | d | 33 | 0.0069767 | 0.007206 | Beta (EB/PL/KS, EB/PL/KS) | 0.00713 | 0.476 | 66.2842 | 8.876 | 0.007 | 0.5 | 70.9286 | 8.3436 |  |  | 0.026809 | 0.0032132 | 0.02779 | 0.003131 | 2007-02-01
MDP RUN FTR | Motor-Driven Pump (Running) Fail to Run | EPIX | 87 | 19572488 | h | 758 | 4.445e-06 | 4.4706e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 4.54e-06 | 1.655 | 364537.4449 | 3.1229 | 5e-06 | 1.5 | 300000 | 3.303 |  |  | 1.3025e-05 | 3.9433e-06 | 1.1447e-05 | 3.6655e-06 | 2007-02-01
MDP RUN FTS | Motor-Driven Pump (Running) Fail to Start | EPIX | 132 | 75048 | d | 758 | 0.0017589 | 0.0017655 | Beta (EB/PL/KS, EB/PL/KS) | 0.00223 | 0.881 | 394.1863 | 4.7589 | 0.002 | 0.9 | 449.1 | 4.6789 |  |  | 0.0062137 | 0.001328 | 0.0069804 | 0.0014668 | 2007-02-01
MDP STBY FTR≤1H | Motor-Driven Pump (Standby) Fail to Run During First Hour of Operation | EPIX | 12 | 32495 | h | 437 | 0.00036929 | 0.00038467 | Gamma (EB/PL/KS, EB/PL/KS) | 0.000378 | 1.703 | 4505.291 | 3.0741 | 0.0004 | 1.5 | 3750 | 3.303 |  |  | 0.001042 | 0.00031546 | 0.00094418 | 0.00030714 | 2007-02-01
MDP STBY FTR>1H | Motor-Driven Pump (Standby) Fail to Run After First Hour of Operation | EPIX | 2.8 | 568826 | h | 450 | 4.9224e-06 | 5.8014e-06 | Gamma (Jeffreys, SCNID) | 5.8014e-06 | 0.5 | 86185.7576 | 8.4439 | 6e-06 | 0.5 | 83333.3333 | 8.4439 |  |  | 2.3049e-05 | 2.7296e-06 | 2.2286e-05 | 2.6393e-06 | 2007-02-01
MDP STBY FTS | Motor-Driven Pump (Standby) Fail to Start | EPIX | 104 | 82137 | d | 887 | 0.0012662 | 0.0012722 | Beta (EB/PL/KS, EB/PL/KS) | 0.00147 | 0.909 | 617.4583 | 4.6448 | 0.0015 | 0.9 | 599.1 | 4.6818 |  |  | 0.0046614 | 0.00099565 | 0.0045521 | 0.00098004 | 2007-02-01
MDP ELS | Motor-Driven Pump External Leak Small | EPIX | 15 | 130629120 | h | 1864 | 1.1483e-07 | 1.1866e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 1.15e-07 | 0.987 | 8582608.6957 | 4.3647 | 1.2e-07 | 1 | 8333333.3333 | 4.3219 | 1 to 50 gpm. 1997 - 2004 data. |  | 3.5949e-07 | 8.3178e-08 | 3.4611e-07 | 7.9296e-08 | 2007-02-01
MDP ELL | Motor-Driven Pump External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 8.05e-09 | 0.3 | 37267080.7453 | 18.7656 | 8e-09 | 0.3 | 37500000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 3.6596e-08 | 1.9502e-09 | 3.6825e-08 | 1.9624e-09 | 2007-02-01
MOD FTO/C | Motor-Operated Damper Fail to Open or Close | EPIX | 1 | 1320 | d | 21 | 0.00075758 | 0.0011355 | Beta (Jeffreys, SCNID) | 0.0011355 | 0.5 | 439.8333 | 8.4277 | 0.0012 | 0.5 | 416.1667 | 8.4268 |  |  | 0.0046074 | 0.00054676 | 0.0043599 | 0.00051733 | 2007-02-01
MOD SO | Motor-Operated Damper Spurious Operation | EPIX | 0 | 1471680 | h | 21 | 0 | 3.3975e-07 | Gamma (Jeffreys, SCNID) | 3.3975e-07 | 0.5 | 1471680 | 8.4439 | 3e-07 | 0.5 | 1666666.6667 | 8.4439 |  |  | 1.1524e-06 | 1.3648e-07 | 1.3051e-06 | 1.5456e-07 | 2007-02-01
MOV FC | Motor-Operated Valve Fail to Control | WSRC |  |  | h |  |  | 3e-06 | Gamma(WSRC, LL) | 3e-06 | 0.3 | 100000 | 18.7656 | 3e-06 | 0.3 | 100000 | 18.7656 |  |  | 1.3724e-05 | 7.3131e-07 | 1.3724e-05 | 7.3131e-07 | 2007-02-01
MOV FTO/C | Motor-Operated Valve Fail to Open or Close | EPIX | 244 | 232264 | d | 7441 | 0.0010505 | 0.0010527 | Beta (EB/PL/KS, EB/PL/KS) | 0.00107 | 1.277 | 1192.1809 | 3.6425 | 0.001 | 1.2 | 1198.8 | 3.7944 |  |  | 0.0028092 | 0.00074035 | 0.002942 | 0.00080769 | 2007-02-01
MOV SO | Motor-Operated Valve Spurious Operation | EPIX | 14 | 325915800 | h | 7441 | 4.2956e-08 | 4.449e-08 | Gamma (Jeffreys, SCNID) | 4.449e-08 | 0.5 | 11238475.8621 | 8.4439 | 4e-08 | 0.5 | 12500000 | 8.4439 |  |  | 1.5366e-07 | 1.8197e-08 | 1.7091e-07 | 2.024e-08 | 2007-02-01
MOV ELS | Motor-Operated Valve External Leak Small | EPIX | 7 | 533589120 | h | 7614 | 1.3119e-08 | 1.4056e-08 | Gamma (Jeffreys, SCNID) | 1.4056e-08 | 0.5 | 35572608 | 8.4439 | 1.5e-08 | 0.5 | 33333333.3333 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 5.7622e-08 | 6.824e-09 | 5.3995e-08 | 6.3945e-09 | 2007-02-01
MOV ELL | Motor-Operated Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 9.839e-10 | 0.3 | 304908068.5714 | 18.7656 | 1e-09 | 0.3 | 300000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 4.5745e-09 | 2.4377e-10 | 4.5009e-09 | 2.3985e-10 | 2007-02-01
MOV ILS | Motor-Operated Valve Internal Leak Small | EPIX | 87.5 | 528122880 | h | 7536 | 1.6568e-07 | 1.6663e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 1.67e-07 | 0.434 | 2598802.3952 | 10.1776 | 1.5e-07 | 0.5 | 3333333.3333 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 5.7622e-07 | 6.824e-08 | 6.7444e-07 | 6.6267e-08 | 2007-02-01
MOV ILL | Motor-Operated Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 3.34e-09 | 0.3 | 89820359.2814 | 18.7656 | 3e-09 | 0.3 | 100000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 1.3724e-08 | 7.3131e-10 | 1.5279e-08 | 8.1419e-10 | 2007-02-01
MSW FTO/C | Manual Switch Fail to Open or Close | RPS SSs | 2 | 19789 | d |  | 0.00010107 | 0.00012633 | Beta (Jeffreys, SCNID) | 0.00012633 | 0.5 | 3957.5 | 8.4422 | 0.00012 | 0.5 | 4166.1667 | 8.4423 |  |  | 0.00046095 | 5.4601e-05 | 0.00048525 | 5.748e-05 | 2007-02-01
ORF PLG | Orifice Plug | WSRC |  |  | h |  |  | 1e-06 | Gamma(WSRC, LL) | 1e-06 | 0.3 | 300000 | 18.7656 | 1e-06 | 0.3 | 300000 | 18.7656 |  |  | 4.5745e-06 | 2.4377e-07 | 4.5745e-06 | 2.4377e-07 | 2007-02-01
PDP RUN FTR | Positive Displacement Pump (Running) Fail to Run | EPIX | 12 | 1456663 | h | 69 | 8.238e-06 | 8.5813e-06 | Gamma (EB/PL/KS, LL) | 8.32e-06 | 0.3 | 36057.6923 | 18.7656 | 8e-06 | 0.3 | 37500 | 18.7656 |  |  | 3.6596e-05 | 1.9502e-06 | 3.806e-05 | 2.0282e-06 | 2007-02-01
PDP RUN FTS | Positive Displacement Pump (Running) Fail to Start | EPIX | 32 | 9838 | d | 69 | 0.0032527 | 0.0033032 | Beta (EB/PL/KS, EB/PL/KS) | 0.00334 | 0.519 | 154.8702 | 8.0222 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.012642 | 0.0015759 | 2007-02-01
PDP STBY FTR≤1H | Positive Displacement Pump (Standby) Fail to Run During First Hour of Operation | EPIX | 1 | 3540 | h | 66 | 0.00028249 | 0.00042373 | Gamma (Jeffreys, SCNID) | 0.00042373 | 0.5 | 1180 | 8.4439 | 0.0004 | 0.5 | 1250 | 8.4439 |  |  | 0.0015366 | 0.00018197 | 0.0016277 | 0.00019277 | 2007-02-01
PDP STBY FTR>1H | Positive Displacement Pump (Standby) Fail to Run After First Hour of Operation | EPIX | No data |  | h |  |  |  | Gamma (FTR≤1H*0.06, LL) | 2.5424e-05 | 0.3 | 11800 | 18.7656 | 2.5e-05 | 0.3 | 12000 | 18.7656 | No data. FTR≤1H times 0.06 | 2005-10-04 | 0.00011436 | 6.0943e-06 | 0.0001163 | 6.1976e-06 | 2007-02-01
PDP STBY FTS | Positive Displacement Pump (Standby) Fail to Start | EPIX | 9 | 3171 | d | 66 | 0.0028382 | 0.002995 | Beta (Jeffreys, SCNID) | 0.002995 | 0.5 | 166.4474 | 8.4011 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.01149 | 0.0013677 | 2007-02-01
PDP ELS | Positive Displacement Pump External Leak Small | EPIX | 1 | 11633280 | h | 166 | 8.596e-08 | 1.2894e-07 | Gamma (Jeffreys, SCNID) | 1.2894e-07 | 0.5 | 3877760 | 8.4439 | 1.2e-07 | 0.5 | 4166666.6667 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 4.6098e-07 | 5.4592e-08 | 4.9532e-07 | 5.866e-08 | 2007-02-01
PDP ELL | Positive Displacement Pump External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 9.0258e-09 | 0.3 | 33237942.8571 | 18.7656 | 9e-09 | 0.3 | 33333333.3333 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 4.1171e-08 | 2.1939e-09 | 4.1289e-08 | 2.2002e-09 | 2007-02-01
PIPE SWS ELS | Piping Service Water System External Leak Small | EPIX | 8.5 | 13060000000 | h-ft |  | 6.5084e-10 | 6.8913e-10 | Gamma (Jeffreys, SCNID) | 6.8913e-10 | 0.5 | 725555555.5556 | 8.4439 | 7e-10 | 0.5 | 714285714.2857 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. Leakage rate is per hour per foot. |  | 2.689e-09 | 3.1846e-10 | 2.6473e-09 | 3.1351e-10 | 2007-02-01
PIPE SWS ELL | Piping Service Water System External Leak Large | EPIX |  |  | h-ft |  |  |  | Gamma (ELS*0.2, LL) | 1.3783e-10 | 0.3 | 2176666666.6667 | 18.7656 | 1.5e-10 | 0.3 | 2000000000 | 18.7656 | > 50 gpm. Small leak times 0.2. Leakage rate is per hour per foot. |  | 6.8618e-10 | 3.6566e-11 | 6.3048e-10 | 3.3598e-11 | 2007-02-01
PIPE OTHER ELS | Piping Non-Service Water System External Leak Small | EPIX | 3.5 | 15830000000 | h-ft |  | 2.211e-10 | 2.5268e-10 | Gamma (Jeffreys, SCNID) | 2.5268e-10 | 0.5 | 1978750000 | 8.4439 | 2.5e-10 | 0.5 | 2000000000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. Leakage rate is per hour per foot. |  | 9.6036e-10 | 1.1373e-10 | 9.7068e-10 | 1.1496e-10 | 2007-02-01
PIPE OTHER ELL | Piping Non-Service Water System External Leak Large | EPIX |  |  | h-ft |  |  |  | Gamma (ELS*0.1, LL) | 2.5268e-11 | 0.3 | 11872500000 | 18.7656 | 2.5e-11 | 0.3 | 12000000000 | 18.7656 | > 50 gpm. Small leak times 0.1. Leakage rate is per hour per foot. |  | 1.1436e-10 | 6.0943e-12 | 1.1559e-10 | 6.1597e-12 | 2007-02-01
PLDT FTOP | Process Logic (Delta Temperature) Fail to Operate | RPS SSs | 24.3 | 4887 | d |  | 0.0049724 | 0.0050736 | Beta (Jeffreys, SCNID) | 0.0050736 | 0.5 | 98.0484 | 8.3712 | 0.005 | 0.5 | 99.5 | 8.3723 |  |  | 0.019166 | 0.0022892 | 0.019448 | 0.0023232 | 2007-02-01
PLF FTOP | Process Logic (Flow) Fail to Operate | RPS SSs | No data |  | d |  |  |  | Beta (PLL, SCNID) | 0.00062541 | 0.5 | 798.9737 | 8.435 | 0.0006 | 0.5 | 832.8333 | 8.4354 | No data, so PLL FTOP used |  | 0.0023043 | 0.00027317 | 0.0024019 | 0.00028475 | 2007-02-01
PLL FTOP | Process Logic (Level) Fail to Operate | RPS SSs | 3.3 | 6075 | d |  | 0.00054321 | 0.00062541 | Beta (Jeffreys, SCNID) | 0.00062541 | 0.5 | 798.9737 | 8.435 | 0.0006 | 0.5 | 832.8333 | 8.4354 |  |  | 0.0023043 | 0.00027317 | 0.0024019 | 0.00028475 | 2007-02-01
PLP FTOP | Process Logic (Pressure) Fail to Operate | RPS SSs | 5.6 | 38115 | d |  | 0.00014692 | 0.00016004 | Beta (Jeffreys, SCNID) | 0.00016004 | 0.5 | 3123.7623 | 8.4416 | 0.00015 | 0.5 | 3332.8333 | 8.4418 |  |  | 0.00057618 | 6.8253e-05 | 0.00061474 | 7.2822e-05 | 2007-02-01
PMP FTR | Pump Volute Fail to Run | EPIX | 9 | 74199 | h | 180 | 0.0001213 | 0.00012803 | Gamma (EB/PL/KS, EB/PL/KS) | 0.000135 | 1.389 | 10288.8889 | 3.4587 | 0.00012 | 1.5 | 12500 | 3.303 |  |  | 0.00031259 | 9.4639e-05 | 0.00036088 | 0.00010434 | 2007-02-01
PMP FTS | Pump Volute Fail to Start | EPIX | 4 | 16776 | d | 180 | 0.00023844 | 0.00026822 | Beta (Jeffreys, SCNID) | 0.00026822 | 0.5 | 1863.6111 | 8.4401 | 0.00025 | 0.5 | 1999.5 | 8.4404 |  |  | 0.00096026 | 0.00011377 | 0.0010303 | 0.00012207 | 2007-02-01
POD FTO/C | Pneumatic-Operated Damper Fail to Open or Close | EPIX | 2 | 2461 | d | 59 | 0.00081268 | 0.0010154 | Beta (Jeffreys, SCNID) | 0.0010154 | 0.5 | 491.9 | 8.4294 | 0.001 | 0.5 | 499.5 | 8.4296 |  |  | 0.0038398 | 0.00045552 | 0.0038991 | 0.00046256 | 2007-02-01
POD SO | Pneumatic-Operated Damper Spurious Operation | EPIX | 0 | 4134720 | h | 59 | 0 | 1.2093e-07 | Gamma (Jeffreys, SCNID) | 1.2093e-07 | 0.5 | 4134720 | 8.4439 | 1.2e-07 | 0.5 | 4166666.6667 | 8.4439 | 0 events for 1998 - 2002, so 1997 - 2004 data used |  | 4.6098e-07 | 5.4592e-08 | 4.6454e-07 | 5.5014e-08 | 2007-02-01
PORV FTC | Power-Operated Relief Valve Fail to Close | EPIX | 5 | 5054 | d | 235 | 0.00098932 | 0.001088 | Beta (Jeffreys, SCNID) | 0.001088 | 0.5 | 459.0455 | 8.4284 | 0.001 | 0.5 | 499.5 | 8.4296 |  |  | 0.0038398 | 0.00045552 | 0.0041777 | 0.00049567 | 2007-02-01
PORV FTO | Power-Operated Relief Valve Fail to Open | EPIX | 33 | 5054 | d | 235 | 0.0065295 | 0.0066271 | Beta (EB/PL/KS, EB/PL/KS) | 0.00725 | 0.435 | 59.565 | 10.0107 | 0.007 | 0.4 | 56.7429 | 11.303 |  |  | 0.029015 | 0.002567 | 0.029176 | 0.0029144 | 2007-02-01
PORV SO | Power-Operated Relief Valve Spurious Operation | EPIX | 5 | 10555800 | h | 241 | 4.7367e-07 | 5.2104e-07 | Gamma (EB/PL/KS, LL) | 4.63e-07 | 0.3 | 647948.1641 | 18.7656 | 5e-07 | 0.5 | 1000000 | 8.4439 |  |  | 1.9207e-06 | 2.2747e-07 | 2.118e-06 | 1.1287e-07 | 2007-02-01
RLY FTOP | Relay Fail to Operate | RPS SSs | 23.7 | 974417 | d |  | 2.4322e-05 | 2.4835e-05 | Beta (Jeffreys, SCNID) | 2.4835e-05 | 0.5 | 20132.0826 | 8.4436 | 2.5e-05 | 0.5 | 19999.5 | 8.4436 |  |  | 9.6036e-05 | 1.1374e-05 | 9.5403e-05 | 1.1299e-05 | 2007-02-01
RTB (BME) FTO/C | RPS Breaker (Mechanical) Fail to Open or Close | RPS SSs | 1 | 97359 | d |  | 1.0271e-05 | 1.5407e-05 | Beta (Jeffreys, SCNID) | 1.5407e-05 | 0.5 | 32452.5 | 8.4437 | 1.5e-05 | 0.5 | 33332.8333 | 8.4437 |  |  | 5.7621e-05 | 6.8242e-06 | 5.9185e-05 | 7.0093e-06 | 2007-02-01
RTB (BSN) FTOP | RPS Breaker (Shunt Trip) Fail to Operate | RPS SSs | 14 | 44104 | d |  | 0.00031743 | 0.00032877 | Beta (Jeffreys, SCNID) | 0.00032877 | 0.5 | 1520.3276 | 8.4392 | 0.0003 | 0.5 | 1666.1667 | 8.4397 |  |  | 0.0011523 | 0.00013653 | 0.0012628 | 0.00014963 | 2007-02-01
RTB (BUV) FTOP | RPS Breaker (Undervoltage Trip) Fail to Operate | RPS SSs | 23.1 | 57199 | d |  | 0.00040385 | 0.00041259 | Beta (Jeffreys, SCNID) | 0.00041259 | 0.5 | 1211.3432 | 8.4381 | 0.0004 | 0.5 | 1249.5 | 8.4382 |  |  | 0.0015363 | 0.00018207 | 0.0015847 | 0.0001878 | 2007-02-01
RTB FTO/C | RPS Breaker (Combined) Fail to Open or Close | RPS SSs |  |  | d |  |  |  | Beta (Jeffreys, SCNID) | 1.5543e-05 | 0.5 | 32169.2654 | 8.4437 | 1.5e-05 | 0.5 | 33332.8333 | 8.4437 | RTB combined failure probability is BME + BSN*BUV |  | 5.7621e-05 | 6.8242e-06 | 5.9706e-05 | 7.071e-06 | 2007-02-01
SEQ FTOP | Sequencer Fail to Operate | EPIX | 2 | 750 | d | 225 | 0.0026667 | 0.0033289 | Beta (Jeffreys, SCNID) | 0.0033289 | 0.5 | 149.7 | 8.3963 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.01277 | 0.0015209 | 2007-02-01
SOV FC | Solenoid-Operated Valve Fail to Control | WSRC |  |  | h |  |  | 3e-06 | Gamma(WSRC, LL) | 3e-06 | 0.3 | 100000 | 18.7656 | 3e-06 | 0.3 | 100000 | 18.7656 |  |  | 1.3724e-05 | 7.3131e-07 | 1.3724e-05 | 7.3131e-07 | 2007-02-01
SOV FTO/C | Solenoid-Operated Valve Fail to Open or Close | EPIX | 25 | 31813 | d | 1510 | 0.00078584 | 0.00080153 | Beta (EB/PL/KS, EB/PL/KS) | 0.000954 | 0.471 | 493.2397 | 9.0967 | 0.001 | 0.5 | 499.5 | 8.4296 |  |  | 0.0038398 | 0.00045552 | 0.0037419 | 0.00041135 | 2007-02-01
SOV SO | Solenoid-Operated Valve Spurious Operation | EPIX | 6 | 66138000 | h | 1510 | 9.0719e-08 | 9.8279e-08 | Gamma (EB/PL/KS, LL) | 9.23e-08 | 0.3 | 3250270.8559 | 18.7656 | 9e-08 | 0.3 | 3333333.3333 | 18.7656 |  |  | 4.1171e-07 | 2.1939e-08 | 4.2223e-07 | 2.25e-08 | 2007-02-01
SOV ELS | Solenoid-Operated Valve External Leak Small | EPIX | 0.5 | 107152320 | h | 1529 | 4.6663e-09 | 9.3325e-09 | Gamma (Jeffreys, SCNID) | 9.3325e-09 | 0.5 | 53576160 | 8.4439 | 9e-09 | 0.5 | 55555555.5556 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 3.4573e-08 | 4.0944e-09 | 3.585e-08 | 4.2457e-09 | 2007-02-01
SOV ELL | Solenoid-Operated Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 6.5328e-10 | 0.3 | 459224228.5714 | 18.7656 | 7e-10 | 0.3 | 428571428.5714 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 3.2022e-09 | 1.7064e-10 | 2.9884e-09 | 1.5925e-10 | 2007-02-01
SOV ILS | Solenoid-Operated Valve Internal Leak Small | EPIX | 26 | 107152320 | h | 1529 | 2.4265e-07 | 2.4731e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 2.78e-07 | 0.357 | 1284172.6619 | 13.7117 | 3e-07 | 0.4 | 1333333.3333 | 11.4556 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.2465e-06 | 1.0881e-07 | 1.2008e-06 | 8.7577e-08 | 2007-02-01
SOV ILL | Solenoid-Operated Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 5.56e-09 | 0.3 | 53956834.5324 | 18.7656 | 6e-09 | 0.3 | 50000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 2.7447e-08 | 1.4626e-09 | 2.5434e-08 | 1.3554e-09 | 2007-02-01
SRV FTC | Safety Relief Valve Fail to Close | EPIX | 2 | 3142 | d | 386 | 0.00063654 | 0.00079542 | Beta (Jeffreys, SCNID) | 0.00079542 | 0.5 | 628.1 | 8.4326 | 0.0008 | 0.5 | 624.5 | 8.4325 |  |  | 0.0030721 | 0.00036432 | 0.0030545 | 0.00036223 | 2007-02-01
SRV FTO | Safety Relief Valve Fail to Open | EPIX | 10 | 3142 | d | 386 | 0.0031827 | 0.0033408 | Beta (EB/PL/KS, LL) | 0.00771 | 0.3 | 38.6105 | 18.4502 | 0.008 | 0.3 | 37.2 | 18.4383 |  |  | 0.036555 | 0.0019825 | 0.035231 | 0.0019095 | 2007-02-01
SRV SO | Safety Relief Valve Spurious Operation | EPIX | 9 | 16906800 | h | 386 | 5.3233e-07 | 5.619e-07 | Gamma (EB/PL/KS, LL) | 5.08e-07 | 0.3 | 590550.8811 | 18.7656 | 5e-07 | 0.3 | 599999.7 | 18.7656 |  |  | 2.2873e-06 | 1.2189e-07 | 2.3238e-06 | 1.2384e-07 | 2007-02-01
SRV FTCL | Safety Relief Valve Fail to Close (Passing Liquid) | WSRC |  |  | d |  |  | 0.1 | Beta (WSRC, SCNID) | 0.1 | 0.5 | 4.5 | 6.9689 | 0.1 | 0.5 | 4.5 | 6.9689 | Average of 95th percentiles of FTC data entries |  | 0.36249 | 0.052015 | 0.36249 | 0.052015 | 2007-02-01
STF FTOP | Sensor/Transmitter (Flow) Fail to Operate | RPS SSs |  |  | d |  |  |  | Beta (STL, SCNID) | 0.00081469 | 0.5 | 613.2273 | 8.4439 | 0.0008 | 0.5 | 624.5 | 8.4325 | Level sensor/transmitter results used. Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). | [5 empty] | 2007-02-01
| Sensor/Transmitter (Flow) Fail to Operate | RPS SSs |  |  | h |  |  |  | Gamma (STL, SCNID) | 1.0171e-07 | 0.5 | 4915984 | 8.4439 | 1e-07 | 0.5 | 5000000 | 8.4439 | [6 empty] | 2007-02-01
STL FTOP | Sensor/Transmitter (Level) Fail to Operate | RPS SSs | 5 | 6750 | d |  | 0.00074074 | 0.00081469 | Beta (Jeffreys, SCNID) | 0.00081469 | 0.5 | 613.2273 | 8.4439 | 0.0008 | 0.5 | 624.5 | 8.4325 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.0030721 | 0.00036432 | 0.0031322 | 0.00037094 | 2007-02-01
| Sensor/Transmitter (Level) Fail to Operate | RPS SSs | 0.5 | 9831968 | h |  | 5.0855e-08 | 1.0171e-07 | Gamma (Jeffreys, SCNID) | 1.0171e-07 | 0.5 | 4915984 | 8.4439 | 1e-07 | 0.5 | 5000000 | 8.4439 |  |  | 3.8415e-07 | 4.5494e-08 | 3.9071e-07 | 4.6271e-08 | 2007-02-01
STP FTOP | Sensor/Transmitter (Pressure) Fail to Operate | RPS SSs | 2.3 | 23960 | d |  | 9.5993e-05 | 0.00011686 | Beta (Jeffreys, SCNID) | 0.00011686 | 0.5 | 4278.25 | 8.4439 | 0.00012 | 0.5 | 4166.1667 | 8.4423 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.00046095 | 5.4601e-05 | 0.00044895 | 5.3169e-05 | 2007-02-01
| Sensor/Transmitter (Pressure) Fail to Operate | RPS SSs | 35.2 | 43430451 | h |  | 8.1049e-07 | 8.22e-07 | Gamma (Jeffreys, SCNID) | 8.22e-07 | 0.5 | 608269.6218 | 8.4439 | 8e-07 | 0.5 | 625000 | 8.4439 |  |  | 3.0732e-06 | 3.6395e-07 | 3.1577e-06 | 3.7396e-07 | 2007-02-01
STT FTOP | Sensor/Transmitter (Temperature) Fail to Operate | RPS SSs | 17.1 | 40759 | d |  | 0.00041954 | 0.0004318 | Beta (Jeffreys, SCNID) | 0.0004318 | 0.5 | 1157.4545 | 8.4439 | 0.0004 | 0.5 | 1249.5 | 8.4382 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.0015363 | 0.00018207 | 0.0016594 | 0.00019652 | 2007-02-01
| Sensor/Transmitter (Temperature) Fail to Operate | RPS SSs | 29 | 35107399 | h |  | 8.2604e-07 | 8.4028e-07 | Gamma (Jeffreys, SCNID) | 8.4028e-07 | 0.5 | 595040.661 | 8.4439 | 8e-07 | 0.5 | 625000 | 8.4439 |  |  | 3.0732e-06 | 3.6395e-07 | 3.2279e-06 | 3.8227e-07 | 2007-02-01
STR PLG | Strainer Plug | EPIX | 34 | 5475000 | h | 125 | 6.21e-06 | 6.3014e-06 | Gamma (EB/PL/KS, LL) | 7.38e-06 | 0.3 | 40650.4065 | 18.7656 | 7e-06 | 0.3 | 42856.8429 | 18.7656 | For SWSs with potential for environmental insults |  | 3.2022e-05 | 1.7064e-06 | 3.376e-05 | 1.799e-06 | 2007-02-01
SVV FTC | Safety Valve Fail to Close | EPIX | 0 | 7393 | d | 997 | 0 | 6.7622e-05 | Beta (Jeffreys, SCNID) | 6.7622e-05 | 0.5 | 7393.5 | 8.443 | 7e-05 | 0.5 | 7142.3571 | 8.4429 |  |  | 0.00026889 | 3.1848e-05 | 0.00025976 | 3.0767e-05 | 2007-02-01
SVV FTO | Safety Valve Fail to Open | EPIX | 18 | 7393 | d | 997 | 0.0024347 | 0.002502 | Beta (EB/PL/KS, LL) | 0.00247 | 0.3 | 121.1575 | 18.665 | 0.0025 | 0.3 | 119.7 | 18.6638 |  |  | 0.011433 | 0.00061256 | 0.011295 | 0.00060517 | 2007-02-01
SVV SO | Safety Valve Spurious Operation | EPIX | 11 | 43668600 | h | 997 | 2.519e-07 | 2.6335e-07 | Gamma (EB/PL/KS, LL) | 2.12e-07 | 0.3 | 1415094.3396 | 18.7656 | 2e-07 | 0.3 | 1500000 | 18.7656 |  |  | 9.149e-07 | 4.8754e-08 | 9.6979e-07 | 5.1679e-08 | 2007-02-01
SVV FTCL | Safety Valve Fail to Close (Passing Liquid) | EPIX |  |  | d |  |  | 0.1 | Beta (WSRC, SCNID) | 0.1 | 0.5 | 4.5 | 6.9689 | 0.1 | 0.5 | 4.5 | 6.9689 | Average of 95th percentiles of FTC data entries |  | 0.36249 | 0.052015 | 0.36249 | 0.052015 | 2007-02-01
TDP RUN FTR | Turbine-Driven Pump (Running) Fail to Run | EPIX | 13 | 2231788 | h | 55 | 5.8249e-06 | 6.049e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 5.77e-06 | 3.422 | 593067.591 | 2.2357 | 6e-06 | 3 | 500000 | 2.3544 |  |  | 1.2592e-05 | 5.3481e-06 | 1.1668e-05 | 5.2187e-06 | 2007-02-01
TDP RUN FTS | Turbine-Driven Pump (Running) Fail to Start | EPIX | 11 | 502.6 | d | 55 | 0.021886 | 0.022836 | Beta (EB/PL/KS, EB/PL/KS) | 0.0222 | 1.323 | 58.2716 | 3.4875 | 0.02 | 1.2 | 58.8 | 3.7195 |  |  | 0.055653 | 0.014962 | 0.059682 | 0.017113 | 2007-02-01
TDP STBY FTR≤1H | Turbine-Driven Pump (Standby) Fail to Run During First Hour of Operation | EPIX | 18 | 7188 | h | 113 | 0.0025042 | 0.0025737 | Gamma (EB/PL/KS, EB/PL/KS) | 0.00264 | 0.796 | 301.5152 | 5.199 | 0.0025 | 0.8 | 320 | 5.1763 |  |  | 0.0081098 | 0.0015667 | 0.0085794 | 0.0016502 | 2007-02-01
TDP STBY FTR>1H | Turbine-Driven Pump (Standby) Fail to Run After First Hour of Operation | EPIX | 0 | 6803 | h | 6 | 0 | 7.3497e-05 | Gamma (Jeffreys, SCNID) | 7.3497e-05 | 0.5 | 6803 | 8.4439 | 7e-05 | 0.5 | 7142.8571 | 8.4439 | 0 events for 1998 - 2002, so 1997 - 2004 data used | 2005-10-04 | 0.0002689 | 3.1846e-05 | 0.00028234 | 3.3436e-05 | 2007-02-01
TDP STBY FTS | Turbine-Driven Pump (Standby) Fail to Start | EPIX | 46 | 7627 | d | 119 | 0.0060312 | 0.006096 | Beta (EB/PL/KS, EB/PL/KS) | 0.00688 | 0.414 | 59.7604 | 10.747 | 0.007 | 0.4 | 56.7429 | 11.303 |  |  | 0.029015 | 0.002567 | 0.028177 | 0.0026219 | 2007-02-01
TDP ELS | Turbine-Driven Pump External Leak Small | EPIX | 1 | 12264000 | h | 175 | 8.1539e-08 | 1.2231e-07 | Gamma (Jeffreys, SCNID) | 1.2231e-07 | 0.5 | 4088000 | 8.4439 | 1.2e-07 | 0.5 | 4166666.1667 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 4.6098e-07 | 5.4592e-08 | 4.6985e-07 | 5.5643e-08 | 2007-02-01
TDP ELL | Turbine-Driven Pump External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 8.5616e-09 | 0.3 | 35040000 | 18.7656 | 9e-09 | 0.3 | 33333333.0333 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 4.1171e-08 | 2.1939e-09 | 3.9165e-08 | 2.0871e-09 | 2007-02-01
TFM FTOP | Transformer Fail to Operate | EPIX | 81 | 199027200 | h | 4544 | 4.0698e-07 | 4.0949e-07 | Gamma (EB/PL/KS, EB/PL/KS) | 9.04e-07 | 0.314 | 347345.1327 | 17.1975 | 9e-07 | 0.3 | 333333.3333 | 18.7656 |  |  | 4.1171e-06 | 2.1939e-07 | 4.0748e-06 | 2.3694e-07 | 2007-02-01
TNK UNPR ELS | Tank Unpressurized External Leak Small | EPIX | 1 | 47023680 | h | 671 | 2.1266e-08 | 3.1899e-08 | Gamma (Jeffreys, SCNID) | 3.1899e-08 | 0.5 | 15674560 | 8.4439 | 3e-08 | 0.5 | 16666666.6667 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.1524e-07 | 1.3648e-08 | 1.2254e-07 | 1.4512e-08 | 2007-02-01
TNK UNPR ELL | Tank Unpressurized External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 2.2329e-09 | 0.3 | 134353371.4286 | 18.7656 | 2e-09 | 0.3 | 150000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 9.149e-09 | 4.8754e-10 | 1.0214e-08 | 5.4432e-10 | 2007-02-01
TNK PRES ELS | Tank Pressurized External Leak Small | EPIX | 1.5 | 50948160 | h | 727 | 2.9442e-08 | 3.9256e-08 | Gamma (Jeffreys, SCNID) | 3.9256e-08 | 0.5 | 12737040 | 8.4439 | 4e-08 | 0.5 | 12500000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.5366e-07 | 1.8197e-08 | 1.508e-07 | 1.7859e-08 | 2007-02-01
TNK UNPR ELL | Tank Unpressurized External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 2.7479e-09 | 0.3 | 109174628.5714 | 18.7656 | 3e-09 | 0.3 | 100000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.3724e-08 | 7.3131e-10 | 1.257e-08 | 6.6985e-10 | 2007-02-01
TSA PLG | Traveling Screen Assembly Plug | EPIX | 29 | 8584800 | h | 196 | 3.3781e-06 | 3.4363e-06 | Gamma (EB/PL/KS, EB/PL/KS) | 4.68e-06 | 0.502 | 107264.9573 | 8.4022 | 5e-06 | 0.5 | 100000 | 8.4439 | For SWSs with potential for environmental insults |  | 1.9207e-05 | 2.2747e-06 | 1.7952e-05 | 2.1366e-06 | 2007-02-01
VBV FTC | Vacuum Breaker Valve Fail to Close | EPIX | 2 | 7301 | h | 139 | 0.00027394 | 0.00034237 | Gamma (Jeffreys, SCNID) | 0.00034237 | 0.5 | 1460.4 | 8.439 | 0.0003 | 0.5 | 1666.6667 | 8.4439 |  |  | 0.0011524 | 0.00013648 | 0.0013146 | 0.00015577 | 2007-02-01
VBV FTO | Vacuum Breaker Valve Fail to Open | EPIX | 3 | 7301 | h | 139 | 0.0004109 | 0.00047932 | Gamma (Jeffreys, SCNID) | 0.00047932 | 0.5 | 1043.1429 | 8.4371 | 0.0005 | 0.5 | 1000 | 8.4439 |  |  | 0.0019207 | 0.00022747 | 0.00184 | 0.00021809 | 2007-02-01
XVM FTO/C | Manual Valve Fail to Open or Close | EPIX | 1 | 2017 | d | 107 | 0.00049579 | 0.00074331 | Beta (Jeffreys, SCNID) | 0.00074331 | 0.5 | 672.1667 | 8.4333 | 0.0007 | 0.5 | 713.7857 | 8.4339 |  |  | 0.0026882 | 0.00031874 | 0.0028545 | 0.00033848 | 2007-02-01
XVM PLG | Manual Valve Plug | EPIX | 0 | 78559680 | h | 1121 | 0 | 6.3646e-09 | Gamma (Jeffreys, SCNID) | 6.3646e-09 | 0.5 | 78559680 | 8.4439 | 6e-09 | 0.5 | 83333333.3333 | 8.4439 |  |  | 2.3049e-08 | 2.7296e-09 | 2.4449e-08 | 2.8955e-09 | 2007-02-01
XVM ELS | Manual Valve External Leak Small | EPIX | 3 | 78559680 | h | 1121 | 3.8188e-08 | 4.4552e-08 | Gamma (Jeffreys, SCNID) | 4.4552e-08 | 0.5 | 11222811.4286 | 8.4439 | 4e-08 | 0.5 | 12500000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 1.5366e-07 | 1.8197e-08 | 1.7115e-07 | 2.0268e-08 | 2007-02-01
XVM ELL | Manual Valve External Leak Large | EPIX |  |  | h |  |  |  | Gamma (ELS*0.07, LL) | 3.1186e-09 | 0.3 | 96195526.5306 | 18.7656 | 3e-09 | 0.3 | 100000000 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.3724e-08 | 7.3131e-10 | 1.4266e-08 | 7.6023e-10 | 2007-02-01
XVM ILS | Manual Valve Internal Leak Small | EPIX | 0 | 7498560 | h | 107 | 0 | 6.6679e-08 | Gamma (Jeffreys, SCNID) | 6.6679e-08 | 0.5 | 7498560 | 8.4439 | 7e-08 | 0.5 | 7142857.1429 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. |  | 2.689e-07 | 3.1846e-08 | 2.5615e-07 | 3.0335e-08 | 2007-02-01
XVM ILL | Manual Valve Internal Leak Large | EPIX |  |  | h |  |  |  | Gamma (ILS*0.02, LL) | 1.3336e-09 | 0.3 | 224956800 | 18.7656 | 1.2e-09 | 0.3 | 250000000 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 5.4894e-09 | 2.9252e-10 | 6.1005e-09 | 3.2509e-10 | 2007-02-01
2007-02-01
Total or Average | [23 empty] | 2007-02-01
2007-02-01
Note a - A sufficient data set was defined as one with >= 10 failures, >= 0.1 failures/component, and >= 8% components with failures. | [23 empty] | 2007-02-01
Acronyms - BWR (boiling water reactor), EB (empirical Bayes), EPIX (Equipment Performance and Information Exchange), KS (Kass Steffey), LL (lower limit), PL (plant level), PLL (process logic level), PWR (pressurized water reactor), SCNID (simplified constrained noninformative distribution), SS (system study), STL (sensor/transmitter level), SWS (service water system), WSRC (Westinghouse Savannah River Company)
Note a - The Jeffreys mean is obtained from a Bayesian update of the Jeffreys noninformative prior. For demand-related events, the mean is (n + 0.5)/(D + 1), where n is the number of failures and D is the number of demands. For time-related failures, the mean is (n + 0.5)/T, where T is the number of hours.
Note b - The error factor is from an empirical Bayes analysis at the plant level, with Kass-Steffey adjustment. The error factor is the 95th percentile divided by the median.
Note c - See the Methodology sheet for the logic for choosing the recommended mean.
Note c - A sufficient data set has ≥ 10 failures, ≥ 8% components with failures, and ≥ 0.10 failures/component.
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distibution type (source for mean, source for α factor)
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β parameter is determined from the mean and α. The β parameter is presented to three significant figures to preserve the mean of the distribution

## Train UA
SPAR Basic Event Unavailability Data and Results
Train Unavailability Event | Train Description | Existing SPAR Value | Data Source | Data | [5 empty] | Industry-average Probability Distribution (note a) | [8 empty] | Comments (see Appendix B for details) | [5 empty] | Major change from draft report | Effective Date
|  | Mean |  | MSPI Trains | ROP SSU Planned Outage Hours | ROP SSU Unplanned Outage Hours | ROP SSU Plant Critical Hours | Mean (note a) | Comments | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Error Factor |  | Recommended Improvement | 95th | Median | 95th | Median
AHU-TM | Air Handling Unit Test or Maintenance | 0.0025 | IPEs |  |  |  |  | 0.00248 | Table C-1, CFC-FAN-TM | Beta (IPEs, SCNID) | 0.00248 | 0.5 | 201.1129 | 8.4084 | 0.0025 | 0.5 | 199.5 | 8.4082 |  | Look for more up-to-date data | 0.0095935 | 0.001141 | 0.0095168 | 0.0011318 |  | 2007-02-01
BAC-TM | Bus (ac) Test or Maintenance | 0.0001 | IPEs |  |  |  |  | 0.000215 | Table C-1, ACP-BAC-TM | Beta (IPEs, SCNID) | 0.000215 | 0.5 | 2325.0814 | 8.4408 | 0.0002 | 0.5 | 2499.5 | 8.4411 |  | Look for more up-to-date data | 0.00076823 | 9.101e-05 | 0.00082584 | 9.7838e-05 |  | 2007-02-01
BCH-TM | Battery Charger Test or Maintenance | 0.0022 | IPEs |  |  |  |  | 0.0022 | Table C-1, CDP-BCH-TM | Beta (IPEs, SCNID) | 0.0022 | 0.5 | 226.7727 | 8.4125 | 0.002 | 0.5 | 249.5 | 8.4153 |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0084433 | 0.0010037 |  | 2007-02-01
CHL-TM | Chiller Test or Maintenance | 0.0241 | IPEs |  |  |  |  | 0.0395 | Table C-1, EHV-FAN-TM-TRN | Beta (IPEs/2, SCNID) | 0.01975 | 0.5 | 24.8165 | 8.1595 | 0.02 | 0.5 | 24.5 | 8.1559 | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. | Look for more up-to-date data | 0.076141 | 0.0093357 | 0.075198 | 0.009216 |  | 2007-02-01
CTF-TM | Cooling Tower Fan Test or Maintenance | 0.002 | IPEs |  |  |  |  | 0.00186 | Table C-1, OLW-FAN-TM | Beta (IPEs, SCNID) | 0.00186 | 0.5 | 268.3172 | 8.4174 | 0.002 | 0.5 | 249.5 | 8.4153 |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0071395 | 0.00084819 |  | 2007-02-01
CTG-TM | Combustion Turbine Generator Test or Maintenance | 0.1 | IPEs |  |  |  |  | 0.101 | Table C-1, GTG-TM | Beta (IPEs/2, SCNID) | 0.05 | 0.5 | 9.5 | 7.7165 | 0.05 | 0.5 | 9.5 | 7.7165 | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. | Look for more up-to-date data | 0.18737 | 0.024281 | 0.18737 | 0.024281 |  | 2007-02-01
DDP-TM (AFWS) | Diesel-Driven Pump Test or Maintenance (AFWS) | 0.01 | MSPI | 5 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.0097 | 10.946 | 1117.5076 | 1.5872 | 0.01 | 10 | 990 | 1.6194 |  | Break down SSU data into MDP, TDP, and DDP trains | 0.015668 | 0.0096752 | 0.014939 | 0.0094118 | MSPI data replace ROP SSU data. ROP data did not distinguish AFWS pump types. | 2007-02-01
DDP-TM (SWS) | Diesel-Driven Pump Test or Maintenance (SWS) |  | MSPI | 5 | [5 empty] | Beta (MSPI, MSPI) | 0.0295 | 6.134 | 201.7982 | 1.8206 | 0.03 | 6 | 194 | 1.8316 |  |  | 0.0521 | 0.028445 | 0.050981 | 0.028003 | Not in draft report | 2007-02-01
EDG-TM (EPS) | Emergency Diesel Generator Test or Maintenance (EPS) | 0.031 | MSPI | 219 | 70258.9536 | 16671.853 | 9567549.15 | 0.009086 |  | Beta (MSPI, MSPI) | 0.0134 | 3.586 | 264.0259 | 2.1807 | 0.012 | 4 | 329.3333 | 2.0986 |  |  | 0.023165 | 0.011038 | 0.026621 | 0.012207 | MSPI data replace ROP SSU data. | 2007-02-01
EDG-TM (HPCS) | Emergency Diesel Generator Test or Maintenance (HPCS) |  | MSPI | 8 | [5 empty] | Beta (MSPI, MSPI) | 0.0133 | 5.761 | 427.3969 | 1.866 | 0.012 | 6 | 494 | 1.8451 |  |  | 0.020952 | 0.011355 | 0.023434 | 0.012558 | MSPI data replace ROP SSU data. | 2007-02-01
EOV-TM | Explosive-Operated Valve Test or Maintenance | 0.00055 | IPEs |  |  |  |  | 0.000552 | Table C-1, SLC-EPV-TM | Beta (IPEs, SCNID) | 0.000552 | 0.5 | 905.2971 | 8.436 | 0.0006 | 0.5 | 832.8333 | 8.4354 |  | Look for more up-to-date data | 0.0023043 | 0.00027317 | 0.00212 | 0.0002513 |  | 2007-02-01
FAN-TM | Fan Test or Maintenance | 0.002 | IPEs |  |  |  |  | 0.002 | Table C-1, EHV-FAN-TM | Beta (IPEs, SCNID) | 0.002 | 0.5 | 249.5 | 8.4153 | 0.002 | 0.5 | 249.5 | 8.4153 |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0076764 | 0.00091219 |  | 2007-02-01
FWR-TM | Feedwater Injection Test or Maintenance |  | MSPI | 4 | [5 empty] | Beta (MSPI, MSPI Ave) | 0.016 | 2.5 | 153.75 | 2.5167 | 0.015 | 2.5 | 164.1667 | 2.5184 | Limited data. Average α used. | Look for more up-to-date data | 0.033008 | 0.013106 | 0.035193 | 0.013984 | Not in draft report | 2007-02-01
HDR-TM (ESW) | Piping Header Test or Maintenance (ESW) |  | MSPI | 53 | [5 empty] | Beta (MSPI, MSPI) | 0.00865 | 1 | 114.6069 | 4.2788 | 0.009 | 1 | 110.1111 | 4.2771 | Header may include 1 MDP or 2 or more MDPs in parallel |  | 0.02684 | 0.0062752 | 0.0258 | 0.0060298 | Not in draft report | 2007-02-01
HDR-TM (RHRSW) | Piping Header Test or Maintenance (RHRSW) |  | MSPI | 38 | [5 empty] | Beta (MSPI, MSPI) | 0.00363 | 1.747 | 479.5202 | 3.0228 | 0.004 | 1.5 | 373.5 | 3.291 | Header includes either 1 MDP or 2 MDPs in parallel |  | 0.0104 | 0.0031602 | 0.0089772 | 0.0029698 | Not in draft report | 2007-02-01
HTG-TM | Hydro Turbine Generator Test or Maintenance |  | SSU |  | 2138 | 12 | 240344 | 0.0089455 | Without fault exposure hours. Not enough trains to obtain percentiles. | Beta (SSU, MSPI Ave) | 0.0089744 | 2.5 | 276.0687 | 2.5287 | 0.009 | 2.5 | 275.2778 | 2.5287 | Limited data. Average α used. MSPI data cover mainly the transmission lines (underground and aboveground from the HTGs to the plants) |  | 0.019854 | 0.0078513 | 0.019798 | 0.007829 |  | 2007-02-01
HTX-TM (CCW) | Heat Exchanger Test or Maintenance (CCW) | 0.0025 | MSPI | 73 |  |  |  | 0.00547 |  | Beta (MSPI, MSPI) | 0.00723 | 1 | 137.3126 | 4.2859 | 0.007 | 1 | 141.8571 | 4.2871 | CCW HTX trains may include 1 MDP or 2 MDPs in parallel | Look for more up-to-date data. Might be able to get some HX UA data from ROP SSU UAs for BWR RHR trains (in cases where 2 pumps feed 1 HX). | 0.020897 | 0.0048743 | 0.021581 | 0.0050352 | Not in draft report | 2007-02-01
HTX-TM (RHR-BWR) | Heat Exchanger Test or Maintenance (RHR-BWR) |  | MSPI | 70 | [5 empty] | Beta (MSPI, MSPI) | 0.00762 | 3.759 | 489.5481 | 2.1503 | 0.008 | 4 | 496 | 2.1029 | RHR-BWR HTX trains include 1 MDP or 2 MDPs in parallel |  | 0.015465 | 0.0073539 | 0.014978 | 0.0069654 | MSPI data replace ROP SSU data. | 2007-02-01
HTX-TM (RHR-PWR) | Heat Exchanger Test or Maintenance (RHR-PWR) |  | MSPI | 145 | [5 empty] | Beta (MSPI, MSPI) | 0.00518 | 2.748 | 527.7539 | 2.4336 | 0.005 | 2.5 | 497.5 | 2.5355 | RHR-PWR HTX trains include 1 MDP or 2 MDPs in parallel |  | 0.011048 | 0.0043572 | 0.011128 | 0.0045727 | MSPI data replace ROP SSU data. | 2007-02-01
IC-TM | Isolation Condenser Test or Maintenance | ? | MSPI | 6 | 579 | 43 | 68380 | 0.0090962 |  | Beta (MSPI, MSPI) | 0.00586 | 1.265 | 214.6053 | 3.6471 | 0.006 | 1.2 | 198.8 | 3.7747 |  | Complete the data period (2000 - 2002) to be consistent | 0.016814 | 0.0044543 | 0.016127 | 0.0044218 | MSPI data replace ROP SSU data. | 2007-02-01
MDC-TM | Motor-Driven Compressor Test or Maintenance | 0.00076 | IPEs |  |  |  |  | 0.026 | Table C-1, IAS-MDC-TM | Beta (IPEs/2, SCNID) | 0.013 | 0.5 | 37.9615 | 8.2572 | 0.012 | 0.5 | 41.1667 | 8.2716 | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. | Look for more up-to-date data | 0.045856 | 0.0055438 | 0.049654 | 0.0060135 |  | 2007-02-01
MDP-TM (AFWS) | Motor-Driven Pump Test or Maintenance (AFWS) | 0.0011 | MSPI | 122 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.00395 | 2.387 | 601.9168 | 2.5905 | 0.004 | 2.5 | 622.5 | 2.5373 |  | Break down SSU data into MDP, TDP, and DDP trains | 0.008842 | 0.0034849 | 0.0088543 | 0.0034179 | MSPI data replace ROP SSU data. ROP data did not distinguish AFWS pump types. | 2007-02-01
MDP-TM (CCW) | Motor-Driven Pump Test or Maintenance (CCW) | 0.0111 | MSPI | 133 | [5 empty] | Beta (MSPI, MSPI) | 0.00591 | 1.288 | 216.6477 | 3.605 | 0.006 | 1.2 | 198.8 | 3.7747 |  | Get from MSPI baseline data for all plants if MSPI is implemented | 0.016814 | 0.0044543 | 0.016164 | 0.0044837 | MSPI data replace ROP SSU data. | 2007-02-01
MDP-TM (HPCS) | Motor-Driven Pump Test or Maintenance (HPCS) | 0.05 | MSPI | 8 | 1887 | 109.5 | 294243 | 0.0067852 |  | Beta (MSPI, MSPI) | 0.0131 | 1.537 | 115.7912 | 3.2182 | 0.012 | 1.5 | 123.5 | 3.2669 |  |  | 0.031082 | 0.009514 | 0.033639 | 0.010453 | MSPI data replace ROP SSU data. | 2007-02-01
MDP-TM (HPSI) | Motor-Driven Pump Test or Maintenance (HPSI) | 0.0019 | MSPI | 196 | 33134 | 4640 | 7494000 | 0.0050406 |  | Beta (MSPI, MSPI) | 0.00412 | 2.348 | 567.5549 | 2.6098 | 0.004 | 2.5 | 622.5 | 2.5373 |  |  | 0.008842 | 0.0034849 | 0.0092811 | 0.0035563 | MSPI data replace ROP SSU data. | 2007-02-01
MDP-TM (RHR BWR) | Motor-Driven Pump Test or Maintenance (RHR BWR) | 0.0101 | SSU |  | 22716 | 3812 | 3657028 | 0.007254 | Without fault exposure hours | Beta (SSU, SSU) | 0.0076743 | 5.892 | 761.8614 | 1.8581 | 0.008 | 6 | 744 | 1.8481 |  | Subdivide plants into those with a single pump feeding a heat exchanger and those with two pumps feeding a heat exchanger | 0.013985 | 0.0075669 | 0.013473 | 0.0072511 |  | 2007-02-01
MDP-TM (RHR PWR) | Motor-Driven Pump Test or Maintenance (RHR PWR) | 0.00737 | SSU |  | 34781 | 3759 | 6783002 | 0.0056819 | Without fault exposure hours | Beta (SSU, SSU) | 0.0059847 | 2.8173 | 467.9389 | 2.4071 | 0.006 | 3 | 497 | 2.3459 |  |  | 0.012563 | 0.0053552 | 0.01276 | 0.0053009 |  | 2007-02-01
MDP-TM (ESW) | Motor-Driven Pump Test or Maintenance (ESW) | 0.0271 | MSPI | 223 | [5 empty] | Beta (MSPI, MSPI) | 0.013 | 1 | 75.9231 | 4.2571 | 0.012 | 1 | 82.3333 | 4.2621 |  | Get from MSPI baseline data for all plants if MSPI is implemented | 0.035731 | 0.0083835 | 0.038689 | 0.0090881 | MSPI data replace ROP SSU data. | 2007-02-01
MDP-TM (NSW) | Motor-Driven Pump Test or Maintenance (NSW) |  | MSPI | 6 | [5 empty] | Beta (MSPI, MSPI) | 0.0164 | 6.278 | 376.5269 | 1.8183 | 0.015 | 6 | 394 | 1.8429 |  |  | 0.026167 | 0.014199 | 0.028301 | 0.015565 | Not in draft report | 2007-02-01
MDP-TM (RHRSW) | Motor-Driven Pump Test or Maintenance (RHRSW) |  | MSPI | 8 | [5 empty] | Beta (MSPI, MSPI) | 0.00576 | 1.32 | 227.8467 | 3.55 | 0.006 | 1.2 | 198.8 | 3.7747 | Most RHRSW MDPs are included in header trains with 2 parallel MDPs, rather than reported individually |  | 0.016814 | 0.0044543 | 0.015623 | 0.0044009 | Not in draft report | 2007-02-01
MDP-TM (Other) | Motor-Driven Pump Test or Maintenance (Other) | Various | MSPI | 696 |  |  |  |  | Use results from all MDPs combined | Beta (MSPI, MSPI) | 0.00751 | 1 | 132.1558 | 4.2845 | 0.008 | 1 | 124 | 4.2821 | Results from all MDP data combined |  | 0.02387 | 0.0055743 | 0.022413 | 0.0052312 | Not in draft report | 2007-02-01
PDP-TM | Positive Displacement Pump Test or Maintenance | 0.0032 | IPEs |  |  |  |  | 0.00319 | Table C-1, CVC-PDP-TM | Beta (IPEs, SCNID) | 0.00319 | 0.5 | 156.2398 | 8.3983 | 0.003 | 0.5 | 166.1667 | 8.401 |  | Look for more up-to-date data | 0.01151 | 0.00137 | 0.012238 | 0.0014572 |  | 2007-02-01
SPC-TM | Signal Processing Channel Test or Maintenance |  | SS |  |  |  |  | 0.058 | NUREG/CR-5500, Vol. 2, Table 4 | Beta (SS, SCNID) | 0.058 | 0.5 | 8.1207 | 7.598 | 0.06 | 0.5 | 7.8333 | 7.5683 |  |  | 0.22351 | 0.029532 | 0.21632 | 0.028471 |  | 2007-02-01
TDP-TM (AFWS) | Turbine-Driven Pump Test or Maintenance (AFWS) | 0.008 | MSPI | 69 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.00544 | 2.177 | 398.0068 | 2.701 | 0.005 | 2 | 398 | 2.8157 |  | Break down SSU data into MDP, TDP, and DDP trains | 0.011834 | 0.0042028 | 0.012536 | 0.0046412 | MSPI data replace ROP SSU data. ROP data did not distinguish AFWS pump types. | 2007-02-01
TDP-TM (HPCI) | Turbine-Driven Pump Test or Maintenance (HPCI) | 0.023 | MSPI | 24 | 8946 | 3552 | 1127958 | 0.01108 |  | Beta (MSPI, MSPI) | 0.013 | 3.288 | 249.6351 | 2.2534 | 0.012 | 3 | 247 | 2.3373 |  |  | 0.025067 | 0.010725 | 0.026453 | 0.011739 | Not in draft report | 2007-02-01
TDP-TM (RCIC) | Turbine-Driven Pump Test or Maintenance (RCIC) | 0.011 | MSPI | 30 | 11458 | 3598 | 1181880 | 0.012739 |  | Beta (MSPI, MSPI) | 0.0107 | 4.703 | 434.8297 | 1.9887 | 0.01 | 5 | 495 | 1.9509 |  |  | 0.018249 | 0.0093542 | 0.019822 | 0.009967 | Not in draft report | 2007-02-01
Acronyms - AFWS (auxiliary feedwater system), BWR (boiling water reactor), CCW (component cooling water), EPS (emergency power system), ESW (emergency or essential service water), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), IC (isolation condenser), HTX (heat exchanger), IPE (Individual Plant Examination), MDP (motor-driven pump), MSPI (Mitigating Systems Performance Index), NSW (normal service water), PWR (pressurized water reactor), RCIC (reactor core isolation cooling), RHR (residual heat removal), RHRSW (residual heat removal service water), ROP (Reactor Oversight Process), SCNID (simplified constrained noninformative distribution), SS (system study), SSU (Safety System Unavailability), SWS (service water system)
Note a - For the ROP UAs, the mean is the average of individual train UAs. Each train UA is the total number of planned and unplanned outage hours divided by total number of plant critical hours.
Note b - For the ROP UAs, the percentiles were obtained from the ordered set of train UAs. The error factor is the 95th percentile divided by the median.
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distribution type (source for mean, source for α factor). If the source for the mean indicates IPE/2, these are cases in which the IPE value was divided by 2 to reflect more current performance.
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β factor is determined from the mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution.

## Special Events
SPAR Special Event Data and Results
Special Event Name | System Study Name | Description | Existing SPAR Value |  | Data Source | Data | [6 empty] | Industry-average Probability or Rate Distribution (note a) | [8 empty] | Comments (see Appendix C for details) | [5 empty] | Effective Date
|  |  | Mean | Units |  | Failures | Demands or Hours | MLE | Jeffreys Mean | Error Factor | Data Source | d or h | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Error Factor |  | Recommended Improvement | 95% | Median | 95% | Median
TDP-PRST (RCIC) | IFRS | RCIC TDP probability of restart | 0.26 | D | SS | 6 | 47 | 0.12766 | 0.13542 | ? | System Study (1996 - 2002) | d | Beta (Jeffreys, Jeffreys) | 0.13542 | 6.5 | 41.5 | 1.7163 | 0.15 | 6 | 34 | 1.7403 |  |  | 0.25085 | 0.14415 | 0.22371 | 0.13034 | 2007-02-01
TDP-FRST (RCIC) | LNRS | RCIC TDP restart failure per event | 0.24 | D | SS | 1 | 17 | 0.058824 | 0.083333 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.083333 | 0.5 | 5.5 | 7.2198 | 0.08 | 0.5 | 5.75 | 7.2698 |  |  | 0.29419 | 0.040467 | 0.30575 | 0.042348 | 2007-02-01
TDP-FRFRST (RCIC) | FRFTRS | RCIC failure to recover TDP restart failure | 0.5 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01 |  | Mean | Alpha | Beta | 5% | 50% | 95%
MOV-PMINJ (RCIC) | PMI | RCIC injection valve probability of multiple injections | ? | D | SS | 14 | 28 | 0.5 | 0.5 | ? | System Study (1998 - 2002) | d | Beta (EB/YL/KS, EB/YL/KS) | 0.503 | 4.18 | 4.1301 | 1.5354 | 0.5 | 4 | 4 | 1.5494 |  |  | 0.77468 | 0.5 | 0.77267 | 0.50325 | 2007-02-01 | Beta | 0.0012 | 0.9 | 749.1 | 4.667e-05 | 0.00079635 | 0.0037297
MOV-FTRO (RCIC) | FRO | RCIC injection valve fails to reopen | ? | D | SS | 1 | 38 | 0.026316 | 0.038462 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.038462 | 0.5 | 12.5 | 7.8865 | 0.04 | 0.5 | 12 | 7.8639 |  |  | 0.15073 | 0.019168 | 0.14506 | 0.018393 | 2007-02-01 | Gamma | 0.02 | 6 | 300 | 0.00871 | 0.018901 | 0.035043
MOV-FRFTRO (RCIC) | FRFRO | RCIC failure to recover injection valve failure to reopen | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFRI (RCIC) | LNRC | RCIC failure to transfer back to injection mode (pump recirculation valve) | 0.034 | D | SS | 1 | 197.95 | 0.0050518 | 0.0075777 | ? | System Study (1988 - 2002) | h | Gamma (Jeffreys, SCNID) | 0.0075777 | 0.5 | 65.9833 | 8.4439 | 0.008 | 0.5 | 62 | 8.4439 | Note that this is per hour. Failure occurred 8 min after RCIC initiation. |  | 119.0852 | 14.103 | 126.7361 | 15.0091 | 2007-02-01
SUC-FRFTFR (RCIC) | FRFTRC | RCIC failure to recover transfer failure | 0.17 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (HPCI) | PMI | HPCI injection valve probability of multiple injections | 0.13 | D | SS | 2 | 17 | 0.11765 | 0.13889 | ? | System Study (1995 - 2002) | d | Beta (Jeffreys, SCNID) | 0.13889 | 0.5 | 3.1 | 6.38 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.48738 | 0.076392 | 2007-02-01
MOV-FTRO (HPCI) | FRO | HPCI injection valve fails to reopen | 0.192 | D | SS | 1 | 8 | 0.125 | 0.16667 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.16667 | 0.5 | 2.5 | 5.9592 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.56926 | 0.095526 | 2007-02-01
MOV-FRFTRO (HPCI) | FRFRO | HPCI failure to recover injection valve failure to reopen | 0.833 | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFR (HPCI) | FTRT | HPCI failure to transfer | ? | D | SS | 0 | 1270 | 0 | 0.00039339 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.00039339 | 0.5 | 1270.5 | 8.4383 | 0.0004 | 0.5 | 1249.5 | 8.4382 |  |  | 0.0015363 | 0.00018207 | 0.0015109 | 0.00017906 | 2007-02-01
SUC-FRFTFR (HPCI) | FRFTRT | HPCI failure to recover transfer failure | ? | D | SS | 0 | 0 | #DIV/0! | 0.5 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.5 | 0.5 | 0.5 | 1.9877 | 0.5 | 0.5 | 0.5 | 1.9877 |  |  | 0.99384 | 0.5 | 0.99384 | 0.5 | 2007-02-01
SUC-FTFR (HPCS) | FTRT | HPCS failure to transfer | ? | D | SS | 1 | 478 | 0.0020921 | 0.0031315 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.0031315 | 0.5 | 159.1667 | 8.3991 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.012014 | 0.0014303 | 2007-02-01
SUC-FRFTFR (HPCS) | FRFTRT | HPCS failure to recover transfer failure | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
Acronyms - EB (empirical Bayes), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), KS (Kass-Steffey), MOV (motor-operated valve), RCIC (reactor core isolation cooling), SCNID (simplified constrained noninformative distribution), SUC (suction), SS (updated system study), TDP (turbine-driven pump), YL (year level)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distribution type (source for mean, source for α factor).
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β factor is determined from mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution.

## IEs
SPAR Initiating Event Data and Results
Initiating Event | Description | Existing SPAR Value |  | Data Source | Data | [8 empty] | Industry-average Frequency Distribution (note a) | [8 empty] | Comments (see Appendix D for details) | Recommended Improvement | Comparison with Initiating Event Report on Website | [11 empty] | Additional Comments | Effective Date
|  | Mean | Units |  | Number of Events | Critical Years (rcry) | MLE | Jeffreys Mean (note a) | EB Mean | α Factor | Error Factor (note b) | Data Source | Comments | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Error Factor |  |  | Baseline Period | Events | RCRYs | Mean Frequency (MLE) | Main Reason(s) for Differences | 0.95 | Median | Beta | 95% | Median | 95% | 50%
IE-LLOCA (BWR) | Large Loss-of-Coolant Accident (BWRs) | 3e-05 | CrY | [69] | [9 empty] | Gamma (EE, EE) | 6.78e-06 | 0.47 | 69321.5339 | 9.1372 | 7e-06 | 0.5 | 71428.5714 | 8.4439 |  | Revise based on ongoing NRC studies | FY1997 - FY2002 | 153 | 178.9 | 0.85523 | FY rather than CY | 2.689e-05 | 3.1846e-06 |  |  |  | 2.6624e-05 | 2.9138e-06 |  | 2007-02-01
IE-LLOCA (PWR) | Large Loss-of-Coolant Accident (PWRs) | 5e-06 | CrY | [69] | [9 empty] | Gamma (EE, EE) | 1.33e-06 | 0.42 | 315789.4737 | 10.6625 | 1.2e-06 | 0.4 | 333333.3333 | 11.4556 |  | Revise based on ongoing NRC studies | FY1998 - FY2002 | 212 | 301.7 | 0.70268 |  | 4.9859e-06 | 4.3523e-07 |  |  |  | 5.4332e-06 | 5.0956e-07 |  | 2007-02-01
IE-LOAC | Loss of Vital AC Bus | 0.0238 | CrY | IEDB | 8 | 965.8 | 0.0082833 | 0.008801 |  |  |  | LERs (1992 - 2002) | EB degenerate | Gamma (Jeffreys, Jeffreys) | 0.008801 | 8.5 | 965.8 | 1.6885 | 0.009 | 8 | 888.8889 | 1.7144 | Review of events to remove those not applicable based on SPAR modeling |  | FY1996 - FY2002 | 39 | 208.2 | 0.18732 | FY rather than CY and Jeffreys mean rather than MLE | 0.014792 | 0.0086279 | 0 | #DIV/0! | #DIV/0! | 0.014282 | 0.0084584 | EB failed but indicated little plant variation. No plants had more than 1 event. | 2007-02-01
IE-LOCCW | Total Loss of Component Cooling Water | 0.00097 | CrY | IEDB | 0 | 1282.385 | 0 | 0.0003899 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0003899 | 0.5 | 1282.385 | 8.4439 | 0.0004 | 0.5 | 1250 | 8.4439 | No failures (but some ASP events have been close to complete loss of CCW) | Replace with SPAR initiating event fault tree (plant-specific) | FY1991 - FY2002 | 65 | 704.7 | 0.092238 |  | 0.0015366 | 0.00018197 |  |  |  | 0.0014978 | 0.00017738 | No events | 2007-02-01
IE-LOCHS (BWR) | Total Loss of Condenser Heat Sink (BWRs) | 0.29 | CrY | IEDB | 41 | 208.61 | 0.19654 | 0.19894 | 0.197 | 15.822 | 1.4772 | LERs (1996 - 2002) |  | Gamma (EB/PL/KS, EB/PL/KS) | 0.19654 | 11.08 | 56.3756 | 1.5874 | 0.2 | 12 | 60 | 1.5604 |  |  | FY1993 - FY2002 | 82 | 880.1 | 0.093171 | FY rather than CY and Jeffreys mean rather than MLE | 0.30346 | 0.19447 | 80.3147 | 0.28491 | 0.19287 | 0.30265 | 0.19066 | EB worked. 3 plants had 3, 4, and 5 events. | 2007-02-01
IE-LOCHS (PWR) | Total Loss of Condenser Heat Sink (PWRs) | 0.12 | CrY | IEDB | 38 | 475 | 0.08 | 0.081053 |  |  |  | LERs (1995 - 2002) | EB degenerate | Gamma (Jeffreys, Jeffreys) | 0.081053 | 38.5 | 475 | 1.2902 | 0.08 | 40 | 500 | 1.2842 |  |  | FY1997 - FY2002 | 8 | 534.1 | 0.014978 | SPAR recommended comes from draft LOOP report. LOOP report includes 2003 and uses different baseline periods for each of the five LOOP categories. | 0.10188 | 0.079334 |  |  |  | 0.10367 | 0.080352 | EB failed but indicated little plant variation. No plants had more than 2 events. | 2007-02-01
IE-LODC | Loss of Vital DC Bus | 0.0021 | CrY | IEDB | 1 | 1282.385 | 0.0007798 | 0.0011697 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0011697 | 0.5 | 427.4617 | 8.4439 | 0.0012 | 0.5 | 416.6667 | 8.4439 | Review of events to remove those not applicable based on SPAR modeling | [6 empty] | 0.0046098 | 0.00054592 |  |  |  | 0.0044933 | 0.00053214 | 1 event | 2007-02-01
IE-LOIA (BWR) | Total Loss of Instrument Air (BWRs) | 0.029 | CrY | IEDB | 3 | 343.3 | 0.0087387 | 0.010195 |  |  |  | LERs (1991 - 2002) | EB degenerate | Gamma (Jeffreys, Jeffreys) | 0.010195 | 3.5 | 343.3 | 2.2168 | 0.01 | 3 | 300 | 2.3544 | Review of events to remove those not applicable based on SPAR modeling | [6 empty] | 0.020986 | 0.0089135 |  |  |  | 0.020488 | 0.0092424 | EB failed but indicated little plant variation. Of 3 events, no plant had more than 1. | 2007-02-01
IE-LOIA (PWR) | Total Loss of Instrument Air (PWRs) | 0.0096 | CrY | IEDB | 3 | 356.91 | 0.0084055 | 0.0098064 |  |  |  | LERs (1997 - 2002) |  | Gamma (Jeffreys, SCNID) | 0.0098064 | 0.5 | 50.9871 | 8.4439 | 0.01 | 0.5 | 50 | 8.4439 | Review of events to remove those not applicable based on SPAR modeling | [6 empty] | 0.038415 | 0.0045494 | #DIV/0! | #DIV/0! | #DIV/0! | 0.037671 | 0.0044613 | EB failed. Of 3 events, 2 were at 1 plant. | 2007-02-01
IE-LOMFW | Total Loss of Main Feedwater | 0.085 | CrY | IEDB | 84 | 881.942 | 0.095244 | 0.095811 | 0.0959 | 1.839 | 2.9505 | LERs (1993 - 2002) |  | Gamma (EB/PL/KS, EB/PL/KS) | 0.0959 | 1.326 | 13.8269 | 3.56 | 0.1 | 1.2 | 12 | 3.7983 | [7 empty] | 0.28106 | 0.073995 | 19.194 | 0.23343 | 0.079115 | 0.26044 | 0.073158 | EB worked. Of 84 events, 5 plants had 3, 1 had 4, and 1 had 5. Rest had no more than 2 events. | 2007-02-01
IE-LOOP | Total Loss of Offsite Power | 0.046 | CrY | [68] |  |  | 0.033135 | 0.035897 |  | 1.58 | 3.2053 | LERS (1997 - 2004) | Sum of individual subcategories. Error factor from simulation. | Gamma (Jeffreys, Simulation) | 0.035897 | 1.58 | 44.0152 | 3.2053 | 0.04 | 1.5 | 37.5 | 3.303 |  |  | FY1988 - FY2002 | 38 | 1277 | 0.029757 | Trend plot indicates more events in recent years. SPAR recommended generated using only recent years. | 0.1042 | 0.031546 | 44.0152 | 0.091904 | 0.028672 | 0.091904 | 0.028672 |  | 2007-02-01
| Plant Centered Contribution to LOOP |  | CrY | IEDB | 1 | 724.3 | 0.0013806 | 0.002071 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | [18 empty] | 241.4333 | 0.0079555 | 0.00094216 | #DIV/0! | #DIV/0! |  | 2007-02-01
| Switchyard Centered Contribution to LOOP |  | CrY | IEDB | 7 | 724.3 | 0.0096645 | 0.010355 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | [18 empty] | 48.2867 | 0.039778 | 0.0047108 | #DIV/0! | #DIV/0! |  | 2007-02-01
| Grid Related Contribution to LOOP |  | CrY | IEDB | 13 | 724.3 | 0.017948 | 0.018639 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | [18 empty] | 26.8259 | 0.0716 | 0.0084794 | #DIV/0! | #DIV/0! |  | 2007-02-01
| Weather Related Contribution to LOOP |  | CrY | IEDB | 3 | 724.3 | 0.0041419 | 0.0048323 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | [18 empty] | 103.4714 | 0.018563 | 0.0021984 | #DIV/0! | #DIV/0! |  | 2007-02-01
IE-LOESW | Total Loss of Emergency Service Water | 0.00097 | CrY | IEDB | 0 | 1269.4 | 0 | 0.00039389 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.00039389 | 0.5 | 1269.4 | 8.4439 | 0.0004 | 0.5 | 1250 | 8.4439 | The Harris event in the database involves complete failure of the NSW, not the ESW | Replace with SPAR initiating event fault tree (plant-specific) | FY1988 - FY2002 | 3 | 1277 | 0.0023493 | Jeffreys mean rather than MLE | 0.0015366 | 0.00018197 |  |  |  | 0.0015131 | 0.00017919 | No events | 2007-02-01
IE-MLOCA (BWR) | Medium Loss-of-Coolant Accident (BWRs) | 4e-05 | CrY | [69] | [9 empty] | Gamma (EE, EE) | 0.000104 | 0.61 | 5865.3846 | 6.719 | 0.0001 | 0.6 | 6000 | 6.8388 |  | Revise based on ongoing NRC studies | FY1993 - FY2002 | 6 | 290.1 | 0.020683 | Different baseline periods and Jeffreys mean rather than MLE | 0.00035984 | 5.2617e-05 |  |  |  | 0.00037201 | 5.5366e-05 |  | 2007-02-01
IE-MLOCA (PWR) | Medium Loss-of-Coolant Accident (PWRs) | 4e-05 | CrY | [69] | [9 empty] | Gamma (EE, EE) | 0.00051 | 0.44 | 862.7451 | 9.985 | 0.0005 | 0.4 | 800 | 11.4556 |  | Revise based on ongoing NRC studies | FY1993 - FY2002 | 6 | 290.1 | 0.020683 | Different baseline periods and Jeffreys mean rather than MLE | 0.0020775 | 0.00018135 |  |  |  | 0.0020498 | 0.00020529 |  | 2007-02-01
IE-PLOCCW | Partial Loss of Component Cooling Water | 0.0089 | CrY | IEDB | 1 | 1282.4 | 0.00077979 | 0.0011697 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0011697 | 0.5 | 427.4667 | 8.4439 | 0.0012 | 0.5 | 416.6667 | 8.4439 | Review of events to remove those not applicable based on SPAR modeling |  | FY1988 - FY2002 | 2 | 863.4 | 0.0023164 | Jeffreys mean rather than MLE | 0.0046098 | 0.00054592 |  |  |  | 0.0044933 | 0.00053213 | 1 event | 2007-02-01
IE-PLOESW | Partial Loss of Emergency Service Water | 0.0089 | CrY | IEDB | 2 | 1282.385 | 0.0015596 | 0.0019495 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0019495 | 0.5 | 256.477 | 8.4439 | 0.002 | 0.5 | 250 | 8.4439 | Review of events to remove those not applicable based on SPAR modeling |  | FY1994 - FY2002 | 2 | 263.5 | 0.0075901 | Different baseline periods and Jeffreys mean rather than MLE | 0.0076829 | 0.00090987 |  |  |  | 0.0074889 | 0.0008869 | 2 events, not at same plant | 2007-02-01
IE-SGTR (PWR) | Steam Generator Tube Rupture (PWRs) | 0.007 | CrY | IEDB | 2 | 706.44 | 0.0028311 | 0.0035389 |  |  |  | LERs (1991 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0035389 | 0.5 | 141.288 | 8.4439 | 0.004 | 0.5 | 125 | 8.4439 |  |  | FY1990 - FY2002 | 9 | 758.9 | 0.011859 | Different baseline periods and Jeffreys mean rather than MLE | 0.015366 | 0.0018197 |  |  |  | 0.013594 | 0.00161 | 2 events, not at same plant | 2007-02-01
IE-SLOCA (BWR) | Small Loss-of-Coolant Accident (BWRs) | 0.0005 | CrY | [69] | [9 empty] | Gamma (EE, EE) | 0.0005 | 0.78 | 1560 | 5.2928 | 0.0005 | 0.8 | 1600 | 5.1763 |  |  | FY1988 - FY2002 | 5 | 1277 | 0.0039154 | SPAR recommended does not include very small LOCAs. Jeffreys mean rather than MLE. | 0.001622 | 0.00031334 |  |  |  | 0.0016368 | 0.00030925 |  | 2007-02-01
IE-SLOCA (PWR) | Small Loss-of-Coolant Accident (PWRs) | 0.0005 | CrY | IEDB | 0 | 866.6 | 0 | 0.00057697 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.00057697 | 0.5 | 866.6 | 8.4439 | 0.0006 | 0.5 | 833.3333 | 8.4439 | No failures, but there were events in the early 1980s (RCP seal LOCAs) |  | FY1988 - FY2002 | 5 | 1277 | 0.0039154 | SPAR recommended does not include very small LOCAs. Jeffreys mean rather than MLE. | 0.0023049 | 0.00027296 |  |  |  | 0.0022164 | 0.00026248 | No events | 2007-02-01
IE-SORV (BWR) | Stuck Open Safety/Relief Valve (BWRs) | 0.0463 | CrY | IEDB | 6 | 291.679 | 0.020571 | 0.022285 |  |  |  | LERs (1993 - 2002) | EB degenerate | Gamma (Jeffreys, Jeffreys) | 0.022285 | 6.5 | 291.679 | 1.8122 | 0.02 | 6 | 300 | 1.8541 |  |  | FY1988 - FY2002 | 3 | 863.4 | 0.0034746 | Jeffreys mean rather than MLE | 0.035043 | 0.018901 |  |  |  | 0.038333 | 0.021153 | EB failed but indicated little plant variation. 6 events. No plant had more than 1 event. | 2007-02-01
IE-SORV (PWR) | Stuck Open Safety/Relief Valve (PWRs) | 0.00632 | CrY | IEDB | 2 | 866.578 | 0.0023079 | 0.0028849 |  |  |  | LERs (1988 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0028849 | 0.5 | 173.3156 | 8.4439 | 0.003 | 0.5 | 166.6667 | 8.4439 | [7 empty] | 0.011524 | 0.0013648 |  |  |  | 0.011082 | 0.0013125 | 2 events, not at same plant | 2007-02-01
IE-TRAN (BWR) | General Transient (BWRs) | 1.5 | CrY | IEDB | 149 | 180.165 | 0.82702 | 0.82979 |  |  |  | LERs (1997 - 2002) | EB degenerate | Gamma (Jeffreys, Jeffreys) | 0.82979 | 149.5 | 180.165 | 1.1408 | 0.8 | 150 | 187.5 | 1.1405 | [7 empty] | 0.91039 | 0.79822 |  |  |  | 0.94449 | 0.82795 | EB failed but indicated little plant variation. Expected number is 4.4 per plant. 3 plants had 8 events and 1 had 9. | 2007-02-01
IE-TRAN (PWR) | General Transient (PWRs) | 1.2 | CrY | IEDB | 228 | 304.027 | 0.74993 | 0.75158 | 0.751 | 69.239 | 1.2114 | LERs (1998 - 2002) |  | Gamma (EB/PL/KS, EB/PL/KS) | 0.751 | 17.772 | 23.6644 | 1.4465 | 0.8 | 20 | 25 | 1.4175 |  |  | 0.0018497 | 95% of gamma distribution |  |  |  | 1.1152 | 0.78671 | 92.1248 | 0.90606 | 0.74796 | 1.066 | 0.73696 | EB worked. Expected number is 3.3 per plant. 4 plants had 8 events and 2 had 6. | 2007-02-01
IE-VSLOCA | Very Small Loss-of-Coolant Accident |  | CrY | IEDB | 1 | 965.778 | 0.0010354 | 0.0015532 |  |  |  | LERs (1992 - 2002) | EB degenerate | Gamma (Jeffreys, SCNID) | 0.0015532 | 0.5 | 321.926 | 8.4439 | 0.0015 | 0.5 | 333.3333 | 8.4439 | [7 empty] | 0.0057622 | 0.0006824 |  |  |  | 0.0059664 | 0.00070659 | 1 event | 2007-02-01
Acronyms - ASP (accident sequence precursor), BWR (boiling water reactor), CCW (component cooling water), EB (empirical Bayes), EE (expert elicitation), ESW (emergency service water), IE (initiating event), IEDB (initiating events database), KS (Kass-Steffey), LOCA (loss-of-coolant accident), LOOP (loss of offsite power), NSW (normal service water), PL (plant level), PWR (pressurized water reactor), RCP (reactor coolant pump), SCNID (simplified constrained noninformative distribution), SPAR (standardized plant analysis risk)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distibution type (source for mean, source for α factor)
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β factor is determined from the mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution

## MSPI vs ROP UA Comparison
Comparison of MSPI and ROP SSU Train UA Data
Train Unavailability Event | Train Description | Data Source | Data | [5 empty] | Recommended Probability Distribution | MSPI Data (2002 - 2004) |  |  |  | ROP SSU Data (1998 - 2002) |  |  |  | MSPI Mean/ ROP SSU Mean | Comments (see Appendix B for details) | [5 empty] | Effective Date
|  |  | MSPI Trains | ROP SSU Planned Outage Hours | ROP SSU Unplanned Outage Hours | ROP SSU Plant Critical Hours | Mean (note a) | Comments | Distribution (note a) | Mean | α | β | Error Factor | Mean | α | β | Error Factor |  |  | Recommended Improvement | 95th | Median | 95th | Median
AHU-TM | Air Handling Unit Test or Maintenance | IPEs |  |  |  |  | 0.00248 | Table C-1, CFC-FAN-TM | Beta (IPEs, SCNID) | 0.00248 | 0.5 | 201.1129 | 8.4084 | 0.0025 | 0.5 | 199.5 | 8.4082 |  |  | Look for more up-to-date data | 0.0095935 | 0.001141 | 0.0095168 | 0.0011318 | 2007-02-01
BAC-TM | Bus (ac) Test or Maintenance | IPEs |  |  |  |  | 0.000215 | Table C-1, ACP-BAC-TM | Beta (IPEs, SCNID) | 0.000215 | 0.5 | 2325.0814 | 8.4408 | 0.0002 | 0.5 | 2499.5 | 8.4411 |  |  | Look for more up-to-date data | 0.00076823 | 9.101e-05 | 0.00082584 | 9.7838e-05 | 2007-02-01
BCH-TM | Battery Charger Test or Maintenance | IPEs |  |  |  |  | 0.0022 | Table C-1, CDP-BCH-TM | Beta (IPEs, SCNID) | 0.0022 | 0.5 | 226.7727 | 8.4125 | 0.002 | 0.5 | 249.5 | 8.4153 |  |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0084433 | 0.0010037 | 2007-02-01
CHL-TM | Chiller Test or Maintenance | IPEs |  |  |  |  | 0.0395 | Table C-1, EHV-FAN-TM-TRN | Beta (IPEs/2, SCNID) | 0.01975 | 0.5 | 24.8165 | 8.1595 | 0.02 | 0.5 | 24.5 | 8.1559 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. | Look for more up-to-date data | 0.076141 | 0.0093357 | 0.075198 | 0.009216 | 2007-02-01
CTF-TM | Cooling Tower Fan Test or Maintenance | IPEs |  |  |  |  | 0.00186 | Table C-1, OLW-FAN-TM | Beta (IPEs, SCNID) | 0.00186 | 0.5 | 268.3172 | 8.4174 | 0.002 | 0.5 | 249.5 | 8.4153 |  |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0071395 | 0.00084819 | 2007-02-01
CTG-TM | Combustion Turbine Generator Test or Maintenance | IPEs |  |  |  |  | 0.101 | Table C-1, GTG-TM | Beta (IPEs/2, SCNID) | 0.05 | 0.5 | 9.5 | 7.7165 | 0.05 | 0.5 | 9.5 | 7.7165 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. | Look for more up-to-date data | 0.18737 | 0.024281 | 0.18737 | 0.024281 | 2007-02-01
DDP-TM (AFWS) | Diesel-Driven Pump Test or Maintenance (AFWS) | MSPI | 5 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.0097 | 10.946 | 1117.5076 | 1.5872 | 0.00505 | 3.4 | 669.8673 | 2.2349 | 1.9208 | ROP SSU data do not identify AFWS pump types, so the result is an average of MDPs, TDPs, and DDPs | Break down SSU data into MDP, TDP, and DDP trains | 0.010211 | 0.004569 | 0.014939 | 0.0094118 | 2007-02-01
DDP-TM (SWS) | Diesel-Driven Pump Test or Maintenance (SWS) | MSPI | 5 | [5 empty] | Beta (MSPI, MSPI) | 0.0295 | 6.134 | 201.7982 | 1.8206 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW |  | #NUM! | #NUM! | 0.050981 | 0.028003 | 2007-02-01
EDG-TM (EPS) | Emergency Diesel Generator Test or Maintenance (EPS) | MSPI | 219 | 70258.9536 | 16671.853 | 9567549.15 | 0.009086 |  | Beta (MSPI, MSPI) | 0.0134 | 3.586 | 264.0259 | 2.1807 | 0.00906 | 3.6 | 393.751 | 2.1828 | 1.479 |  |  | 0.018008 | 0.0082501 | 0.026621 | 0.012207 | 2007-02-01
EDG-TM (HPCS) | Emergency Diesel Generator Test or Maintenance (HPCS) | MSPI | 8 | [5 empty] | Beta (MSPI, MSPI) | 0.0133 | 5.761 | 427.3969 | 1.866 | 0.00761 | 3.8 | 495.543 | 2.1419 | 1.7477 |  |  | 0.014915 | 0.0069631 | 0.023434 | 0.012558 | 2007-02-01
EOV-TM | Explosive-Operated Valve Test or Maintenance | IPEs |  |  |  |  | 0.000552 | Table C-1, SLC-EPV-TM | Beta (IPEs, SCNID) | 0.0022 | 0.5 | 226.7727 | 8.4125 | 0.0006 | 0.5 | 832.8333 | 8.4354 |  |  | Look for more up-to-date data | 0.0023043 | 0.00027317 | 0.0084433 | 0.0010037 | 2007-02-01
FAN-TM | Fan Test or Maintenance | IPEs |  |  |  |  | 0.002 | Table C-1, EHV-FAN-TM | Beta (IPEs, SCNID) | 0.002 | 0.5 | 249.5 | 8.4153 | 0.002 | 0.5 | 249.5 | 8.4153 |  |  | Look for more up-to-date data | 0.0076764 | 0.00091219 | 0.0076764 | 0.00091219 | 2007-02-01
FWR-TM | Feedwater Injection Test or Maintenance | MSPI | 4 | [5 empty] | Beta (MSPI, MSPI Ave) | 0.016 | 2.5 | 153.75 | 2.5167 | 0.0091 | 2.5 | 272.2253 | 2.5285 | 1.7582 |  | Look for more up-to-date data | 0.020073 | 0.0079388 | 0.035193 | 0.013984 | 2007-02-01
HDR-TM (ESW) | Piping Header Test or Maintenance (ESW) | MSPI | 51 | [5 empty] | Beta (MSPI, MSPI) | 0.00865 | 1 | 114.6069 | 4.2788 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW |  | #NUM! | #NUM! | 0.0258 | 0.0060298 | 2007-02-01
HDR-TM (RHRSW) | Piping Header Test or Maintenance (RHRSW) | MSPI | 38 | [5 empty] | Beta (MSPI, MSPI) | 0.00363 | 1.747 | 479.5202 | 3.0228 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW |  | #NUM! | #NUM! | 0.0089772 | 0.0029698 | 2007-02-01
HTG-TM | Hydro Turbine Generator Test or Maintenance | SSU |  | 2138 | 12 | 240344 | 0.0089455 | Without fault exposure hours. Not enough trains to obtain percentiles. | Beta (SSU, MSPI Ave) | 0.0089744 | 2.5 | 276.0687 | 2.5287 | 0.009 | 2.5 | 275.2778 | 2.5287 |  | ROP SSU UA data do not cover SWSs or CCW |  | 0.019854 | 0.0078513 | 0.019798 | 0.007829 | 2007-02-01
HTX-TM (CCW) | Heat Exchanger Test or Maintenance (CCW) | MSPI | 73 |  |  |  | 0.00547 |  | Beta (MSPI, MSPI) | 0.00723 | 1 | 137.3126 | 4.2859 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW | Look for more up-to-date data. Might be able to get some HX UA data from ROP SSU UAs for BWR RHR trains (in cases where 2 pumps feed 1 HX). | #NUM! | #NUM! | 0.021581 | 0.0050352 | 2007-02-01
HTX-TM (RHR-BWR) | Heat Exchanger Test or Maintenance (RHR-BWR) | MSPI | 70 | [5 empty] | Beta (MSPI, MSPI) | 0.00762 | 3.759 | 489.5481 | 2.1503 | 0.00771 | 6.2 | 797.9505 | 1.831 | 0.98833 |  |  | 0.013377 | 0.0073057 | 0.014978 | 0.0069654 | 2007-02-01
HTX-TM (RHR-PWR) | Heat Exchanger Test or Maintenance (RHR-PWR) | MSPI | 145 | [5 empty] | Beta (MSPI, MSPI) | 0.00518 | 2.748 | 527.7539 | 2.4336 | 0.00598 | 2.5 | 415.5602 | 2.5339 | 0.86622 |  |  | 0.013208 | 0.0052126 | 0.011128 | 0.0045727 | 2007-02-01
IC-TM | Isolation Condenser Test or Maintenance | MSPI | 6 | 579 | 43 | 68380 | 0.0090962 |  | Beta (MSPI, MSPI) | 0.00586 | 1.265 | 214.6053 | 3.6471 | 0.00748 | 2.5 | 331.7246 | 2.5313 | 0.78342 |  | Complete the data period (2000 - 2002) to be consistent | 0.016511 | 0.0065227 | 0.016127 | 0.0044218 | 2007-02-01
MDC-TM | Motor-Driven Compressor Test or Maintenance | IPEs |  |  |  |  | 0.026 | Table C-1, IAS-MDC-TM | Beta (IPEs/2, SCNID) | 0.013 | 0.5 | 37.9615 | 8.2572 | 0.012 | 0.5 | 41.1667 | 8.2716 |  |  | Look for more up-to-date data | 0.045856 | 0.0055438 | 0.049654 | 0.0060135 | 2007-02-01
MDP-TM (AFWS) | Motor-Driven Pump Test or Maintenance (AFWS) | MSPI | 122 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.00395 | 2.387 | 601.9168 | 2.5905 | 0.00505 | 3.4 | 669.8673 | 2.2349 | 0.78218 | ROP SSU data do not identify AFWS pump types, so the result is an average of MDPs, TDPs, and DDPs | Break down SSU data into MDP, TDP, and DDP trains | 0.010211 | 0.004569 | 0.0088543 | 0.0034179 | 2007-02-01
MDP-TM (CCW) | Motor-Driven Pump Test or Maintenance (CCW) | MSPI | 133 | [5 empty] | Beta (MSPI, MSPI) | 0.00591 | 1.288 | 216.6477 | 3.605 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW | Get from MSPI baseline data for all plants if MSPI is implemented | #NUM! | #NUM! | 0.016164 | 0.0044837 | 2007-02-01
MDP-TM (HPCS) | Motor-Driven Pump Test or Maintenance (HPCS) | MSPI | 8 | 1887 | 109.5 | 294243 | 0.0067852 |  | Beta (MSPI, MSPI) | 0.0131 | 1.537 | 115.7912 | 3.2182 | 0.0072 | 20 | 2757.7778 | 1.4154 | 1.8194 |  |  | 0.010024 | 0.0070821 | 0.033639 | 0.010453 | 2007-02-01
MDP-TM (HPSI) | Motor-Driven Pump Test or Maintenance (HPSI) | MSPI | 196 | 33134 | 4640 | 7494000 | 0.0050406 |  | Beta (MSPI, MSPI) | 0.00412 | 2.348 | 567.5549 | 2.6098 | 0.00497 | 2.2 | 440.4559 | 2.6884 | 0.82897 |  |  | 0.011418 | 0.004247 | 0.0092811 | 0.0035563 | 2007-02-01
MDP-TM (RHR BWR) | Motor-Driven Pump Test or Maintenance (RHR BWR) | SSU |  | 22716 | 3812 | 3657028 | 0.007254 | Without fault exposure hours | Beta (SSU, SSU) | 0.0076743 | 5.892 | 761.8614 | 1.8581 | 0.008 | 6 | 744 | 1.8481 |  |  | Subdivide plants into those with a single pump feeding a heat exchanger and those with two pumps feeding a heat exchanger | 0.013985 | 0.0075669 | 0.013473 | 0.0072511 | 2007-02-01
MDP-TM (RHR PWR) | Motor-Driven Pump Test or Maintenance (RHR PWR) | SSU |  | 34781 | 3759 | 6783002 | 0.0056819 | Without fault exposure hours | Beta (SSU, SSU) | 0.0059847 | 2.8173 | 467.9389 | 2.4071 | 0.006 | 3 | 497 | 2.3459 |  |  |  | 0.012563 | 0.0053552 | 0.01276 | 0.0053009 | 2007-02-01
MDP-TM (ESW) | Motor-Driven Pump Test or Maintenance (ESW) | MSPI | 223 | [5 empty] | Beta (MSPI, MSPI) | 0.013 | 1 | 75.9231 | 4.2571 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW | Get from MSPI baseline data for all plants if MSPI is implemented | #NUM! | #NUM! | 0.038689 | 0.0090881 | 2007-02-01
MDP-TM (NSW) | Motor-Driven Pump Test or Maintenance (NSW) | MSPI | 6 | [5 empty] | Beta (MSPI, MSPI) | 0.0164 | 6.278 | 376.5269 | 1.8183 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW |  | #NUM! | #NUM! | 0.028301 | 0.015565 | 2007-02-01
MDP-TM (RHRSW) | Motor-Driven Pump Test or Maintenance (RHRSW) | MSPI | 8 | [5 empty] | Beta (MSPI, MSPI) | 0.00576 | 1.306 | 225.4301 | 3.5739 | [5 empty] | ROP SSU UA data do not cover SWSs or CCW |  | #NUM! | #NUM! | 0.01568 | 0.0043874 | 2007-02-01
MDP-TM (Other) | Motor-Driven Pump Test or Maintenance (Other) | MSPI | 696 |  |  |  |  | Use results from all MDPs combined | Beta (MSPI, MSPI) | 0.00751 | 1 | 132.1558 | 4.2845 | 0.00506 | 2.7 | 530.8968 | 2.4521 | 1.4842 | ROP SSU result is combination of AFWS, HPCS, and HPSI data |  | 0.010927 | 0.0044564 | 0.022413 | 0.0052312 | 2007-02-01
PDP-TM | Positive Displacement Pump Test or Maintenance | IPEs |  |  |  |  | 0.00319 | Table C-1, CVC-PDP-TM | Beta (IPEs, SCNID) | 0.00319 | 0.5 | 156.2398 | 8.3983 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | Look for more up-to-date data | 0.01151 | 0.00137 | 0.012238 | 0.0014572 | 2007-02-01
SPC-TM | Signal Processing Channel Test or Maintenance | SS |  |  |  |  | 0.058 | NUREG/CR-5500, Vol. 2, Table 4 | Beta (SS, SCNID) | 0.058 | 0.5 | 8.1207 | 7.598 | 0.06 | 0.5 | 7.8333 | 7.5683 |  |  |  | 0.22351 | 0.029532 | 0.21632 | 0.028471 | 2007-02-01
TDP-TM (AFWS) | Turbine-Driven Pump Test or Maintenance (AFWS) | MSPI | 69 | 33379 | 5801 | 7679019 | 0.0051022 |  | Beta (MSPI, MSPI) | 0.00544 | 2.177 | 398.0068 | 2.701 | 0.00505 | 3.4 | 669.8673 | 2.2349 | 1.0772 | ROP SSU data do not identify AFWS pump types, so the result is an average of MDPs, TDPs, and DDPs | Break down SSU data into MDP, TDP, and DDP trains | 0.010211 | 0.004569 | 0.012536 | 0.0046412 | 2007-02-01
TDP-TM (HPCI) | Turbine-Driven Pump Test or Maintenance (HPCI) | MSPI | 24 | 8946 | 3552 | 1127958 | 0.01108 |  | Beta (MSPI, MSPI) | 0.013 | 3.288 | 249.6351 | 2.2534 | 0.0115 | 3.9 | 335.2304 | 2.1179 | 1.1304 |  |  | 0.022352 | 0.010554 | 0.026453 | 0.011739 | 2007-02-01
TDP-TM (RCIC) | Turbine-Driven Pump Test or Maintenance (RCIC) | MSPI | 30 | 11458 | 3598 | 1181880 | 0.012739 |  | Beta (MSPI, MSPI) | 0.0107 | 4.703 | 434.8297 | 1.9887 | 0.0129 | 4.6 | 351.9891 | 2.001 | 0.82946 |  |  | 0.024013 | 0.012001 | 0.019822 | 0.009967 | 2007-02-01
Acronyms - AFWS (auxiliary feedwater system), BWR (boiling water reactor), CCW (component cooling water), DDP (diesel-driven pump), EPS (emergency power system), ESW (emergency or essential service water), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), HPSI (high-pressure safety injection), IC (isolation condenser), MDP (motor-driven pump), MSPI (Mitigating Systems Performance Index), NSW (normal service water), PWR (pressurized water reactor), RCIC (reactor core isolation cooling), RHR (residual heat removal), RHRSW (residual heat removal service water), ROP (Reactor Oversight Process), SSU (Safety System Unavailability), SWS (service water system), TDP (turbine-driven pump), TM (test or maintenance)
Note a - For the ROP UAs, the mean is the average of individual train UAs. Each train UA is the total number of planned and unplanned outage hours divided by total number of plant critical hours.
Note b - For the ROP UAs, the percentiles were obtained from the ordered set of train UAs. The error factor is the 95th percentile divided by the median.
Note a - The format for the distributions is the following: distribution type (source for mean, source for α factor). If the source for the mean indicates IPE/2, these are cases in which the IPE value was divided by 2 to reflect more current performance.
Note b - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note c - The β factor is determined from the mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution.