## Component UR
Summary of SPAR Component Unreliability Data and Results
2010 Paramater Estimation Update
Group | Component Failure Mode | Description | Data Source | Data | [6 empty] | Industry-average Failure Probability or Rate Distribution (note a) | [5 empty] | Comments (see Appendix A for details) |  |  |  | Effective Date | p-value | Significance of p-value
|  |  |  | Failures | Demands or Hours (Column Hidden) | Demands or Hours | d or h | Components | MLE | Jeffreys Mean | Distribution (note b) | Analysis Type | Mean | α | β | Error Factor |  |  | 95% | Median
Valves | AOV ELS | Air-Operated Valve (AOV) External Leak Small | EPIX | 64 | 1171601352 h | 1171601352 | h | 10283 | 5.4626e-08 | 5.5053e-08 | Gamma | JNID/IL | 5.51e-08 | 64.5 | 1171601352 | 1.2123 |  |  | 6.6792e-08 | 5.4769e-08 | 2012-02-01 | 0.1814
| AOV ELL | Air-Operated Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 3.857e-09 | 0.3 | 77780658.5429 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.7644e-08 | 9.4022e-10 | 2007-02-01
| AOV FC | Air-Operated Valve (AOV) Loss of Function / Fail to Control | EPIX | 266 | 1171601352 h | 1171601352 | h | 10283 | 2.2704e-07 | 2.2747e-07 | Gamma | EB/PL/KS | 2.486e-07 | 1.421 | 5719000 | 2.6521 |  |  | 6.5912e-07 | 1.9323e-07 | 2007-02-01 | 0.032 | Significant
| AOV FTO/C | Air-Operated Valve (AOV) Fail to Open/Close | EPIX | 146 | 173117 | 173117 | d | 2207 | 0.00084336 | 0.00084625 | Beta | EB/PL/KS | 0.000951 | 1.112 | 1168 | 2.8843 |  |  | 0.0027437 | 0.00068635 | 2012-02-01 | 0.0011 | High
| AOV ILS | Air-Operated Valve (AOV) Internal Leak Small | EPIX | 113 | 1171601352 h | 1171601352 | h | 10283 | 9.6449e-08 | 9.6876e-08 | Gamma | JNID/IL | 9.69e-08 | 113.5 | 1171601352 | 1.1558 |  |  | 1.123e-07 | 9.6592e-08 | 2012-02-01 | 0.083
| AOV ILL | Air-Operated Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 1.938e-09 | 0.3 | 154798761.6099 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 8.8654e-09 | 4.7243e-10 | 2007-02-01
| AOV SOP | Air-Operated Valve (AOV) Spurious Operation | EPIX | 140 | 1171601352 h | 1171601352 | h | 10283 | 1.1949e-07 | 1.1992e-07 | Gamma | EB/PL/KS | 1.305e-07 | 0.6801 | 5211000 | 3.4398 |  |  | 4.4888e-07 | 7.4643e-08 | 2012-02-01 | 0.0005 | Extreme
| CKV ELS | Check Valve (CKV) External Leak Small | EPIX | 10 | 1004642562 h | 1004642562 | h | 8820 | 9.9538e-09 | 1.0451e-08 | Gamma | JNID/IL | 1.05e-08 | 10.5 | 1004642562 | 1.5524 |  |  | 1.626e-08 | 1.0122e-08 | 2012-02-01 | 0.133
| CKV ELL | Check Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 7.35e-10 | 0.3 | 408163265.3061 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 3.3623e-09 | 1.7917e-10 | 2007-02-01
| CKV FTC | Check Valve (CKV) Fail to Close | EPIX | 8 | 46841 | 46841 | d | 599 | 0.00017079 | 0.00018146 | Beta | EB/PL/KS | 0.0002382 | 0.8062 | 3384 | 3.2343 |  |  | 0.00077042 | 0.00014988 | 2012-02-01 | 0.9605
| CKV FTO | Check Valve (CKV) Fail to Open | EPIX | 0 | 46841 | 46841 | d | 599 | 0 | 1.0674e-05 | Beta | JNID/IL | 1.07e-05 | 0.5 | 46841.43 | 3.8318 |  |  | 4.1004e-05 | 4.8561e-06 | 2012-02-01 | 0.0163 | Significant
| CKV ILS | Check Valve (CKV) Internal Leak Small | EPIX | 204 | 1004642562 h | 1004642562 | h | 8820 | 2.0306e-07 | 2.0355e-07 | Gamma | EB/PL/KS | 3.076e-07 | 0.5709 | 1856000 | 3.6638 |  |  | 1.1268e-06 | 1.5603e-07 | 2012-02-01 | 0.0008 | Extreme
| CKV ILL | Check Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 6.152e-09 | 0.3 | 48764629.3888 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 2.8142e-08 | 1.4997e-09 | 2007-02-01
| CKV SC | Check Valve (CKV) Spurious Closing | EPIX | 5 | 1004642562 h | 1004642562 | h | 8820 | 4.9769e-09 | 5.4746e-09 | Gamma | JNID/IL | 5.47e-09 | 5.5 | 1004642562 | 1.7898 |  |  | 9.7921e-09 | 5.1466e-09 | 2012-02-01 | 0.3358
| CKV SO | Check Valve (CKV) Spurious Opening | EPIX | 3 | 1004642562 h | 1004642562 | h | 8820 | 2.9861e-09 | 3.4838e-09 | Gamma | JNID/IL | 3.48e-09 | 3.5 | 1004642562 | 2.0115 |  |  | 7.0011e-09 | 3.1582e-09 | 2012-02-01 | 0.0321 | Significant
| EOV FTOC | Explosive-Operated Valve (EOV) Fail to Open/Close | EPIX | 1 | 583 | 583 | d | 60 | 0.0017153 | 0.0025729 | Beta | JNID/IL | 0.00257 | 1.5 | 582.7 | 2.5992 |  | 2005-10-04 | 0.0066803 | 0.0020273 | 2012-02-01 | 0.1882
| HOV ELS | Hydraulic-Operated Valve (HOV) External Leak Small | EPIX | 19 | 87527799 h | 87527799 | h | 771 | 2.1707e-07 | 2.2279e-07 | Gamma | JNID/IL | 2.23e-07 | 19.5 | 87527799 | 1.3991 |  |  | 3.1174e-07 | 2.1899e-07 | 2012-02-01 | 0.8869
| HOV ELL | Hydraulic-Operated Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 1.561e-08 | 0.3 | 19218449.7117 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 7.1408e-08 | 3.8053e-09 | 2007-02-01
| HOV FC | Hydraulic-Operated Valve (HOV) Loss of Function / Fail to Control | EPIX | 42 | 87527799 h | 87527799 | h | 771 | 4.7985e-07 | 4.8556e-07 | Gamma | JNID/IL | 4.86e-07 | 42.5 | 87527799 | 1.2634 |  |  | 6.1421e-07 | 4.8176e-07 | 2007-02-01 | 0.207
| HOV FTO/C | Hydraulic-Operated Valve (HOV) Fail to Open/Close | EPIX | 24 | 20476 | 20476 | d | 428 | 0.0011721 | 0.0011965 | Beta | JNID/IL | 0.0012 | 24.5 | 20452.9 | 1.35 |  |  | 0.0016195 | 0.0011802 | 2012-02-01 | 0.465
| HOV ILS | Hydraulic-Operated Valve (HOV) Internal Leak Small | EPIX | 2 | 87527799 h | 87527799 | h | 771 | 2.285e-08 | 2.8562e-08 | Gamma | JNID/IL | 2.86e-08 | 2.5 | 87527799 | 2.2098 |  |  | 6.324e-08 | 2.4858e-08 | 2012-02-01 | 0.0698
| HOV ILL | Hydraulic-Operated Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 5.72e-10 | 0.3 | 524475524.4755 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 2.6166e-09 | 1.3944e-10 | 2007-02-01
| HOV SOP | Hydraulic-Operated Valve (HOV) Spurious Operation | EPIX | 17 | 87527799 h | 87527799 | h | 771 | 1.9422e-07 | 1.9994e-07 | Gamma | JNID/IL | 2e-07 | 17.5 | 87527799 | 1.42 |  |  | 2.8449e-07 | 1.9614e-07 | 2012-02-01 | 0.9956
| MOV ELS | Motor-Operated Valve (MOV) External Leak Small | EPIX | 51 | 1571522275 h | 1571522275 | h | 13807 | 3.2453e-08 | 3.2771e-08 | Gamma | EB/PL/KS | 3.277e-08 | 0.4755 | 14510000 | 3.9121 |  |  | 1.2815e-07 | 1.424e-08 | 2012-02-01 | 0.032 | Significant
| MOV ELL | Motor-Operated Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 2.2939e-09 | 0.3 | 130781638.258 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.0493e-08 | 5.5919e-10 | 2007-02-01
| MOV FC | Motor-Operated Valve (MOV) Loss of Function / Fail to Control | EPIX | 105 | 1571522275 h | 1571522275 | h | 13807 | 6.6814e-08 | 6.7132e-08 | Gamma | EB/PL/KS | 6.616e-08 | 1.458 | 22050000 | 2.63 |  |  | 1.7389e-07 | 5.1771e-08 | 2007-02-01 | 0.0019 | High
| MOV FTO/C | Motor-Operated Valve (MOV) Fail to Open/Close | EPIX | 532 | 602223 | 602223 | d | 7445 | 0.00088339 | 0.00088422 | Beta | EB/PL/KS | 0.0009631 | 2.046 | 2123 | 2.3539 |  |  | 0.0022664 | 0.00081155 | 2012-02-01 | 0.0388 | Significant
| MOV ILS | Motor-Operated Valve (MOV) Internal Leak Small | EPIX | 145 | 1571522275 h | 1571522275 | h | 13807 | 9.2267e-08 | 9.2585e-08 | Gamma | EB/PL/KS | 1.01e-07 | 0.6545 | 6477000 | 3.4891 |  |  | 3.5239e-07 | 5.6408e-08 | 2012-02-01 | 0.0015 | High
| MOV ILL | Motor-Operated Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 2.02e-09 | 0.3 | 148514851.4851 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 9.2405e-09 | 4.9242e-10 | 2007-02-01
| MOV SOP | Motor-Operated Valve (MOV) Spurious Operation | EPIX | 52 | 1571522275 h | 1571522275 | h | 13807 | 3.3089e-08 | 3.3407e-08 | Gamma | EB/PL/KS | 3.386e-08 | 0.5703 | 16840000 | 3.6651 |  |  | 1.2411e-07 | 1.7165e-08 | 2012-02-01 | 0.2764
| MSV ELS | Main Steam Isolation Valve (MSV) External Leak Small | EPIX | 7 | 55836292 h | 55836292 | h | 490 | 1.2537e-07 | 1.3432e-07 | Gamma | JNID/IL | 1.34e-07 | 7.5 | 55836292 | 1.6716 | [5 empty] | 0.9517
| MSV FTOC | Main Steam Isolation Valve (MSV) Fail to Open/Close | EPIX | 23 | 30182 | 30182 | d | 401 | 0.00076204 | 0.00077858 | Beta | JNID/IL | 0.000779 | 23.5 | 30159.26 | 1.3607 | [5 empty] | 0.8793
| MSV ILS | Main Steam Isolation Valve (MSV) Internal Leak Small | EPIX | 84 | 55836292 h | 55836292 | h | 490 | 1.5044e-06 | 1.5134e-06 | Gamma | JNID/IL | 1.51e-06 | 84.5 | 55836292 | 1.1854 | [5 empty] | 0.0042 | High
| MSV SOP | Main Steam Isolation Valve (MSV) Spurious Operation | EPIX | 21 | 55836292 h | 55836292 | h | 490 | 3.761e-07 | 3.8505e-07 | Gamma | JNID/IL | 3.85e-07 | 21.5 | 55836292 | 1.3792 | [5 empty] | 0.0536
| SOV ELS | Solenoid-Operated Valve (SOV) External Leak Small | EPIX | 4 | 131304380 h | 131304380 | h | 1153 | 3.0464e-08 | 3.4272e-08 | Gamma | JNID/IL | 3.43e-08 | 4.5 | 131304380 | 1.8776 | 1 to 50 gpm. 1997 - 2004 data. |  | 6.4427e-08 | 3.1769e-08 | 2012-02-01 | 0.2299
| SOV ELL | Solenoid-Operated Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 2.401e-09 | 0.3 | 124947938.359 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.0983e-08 | 5.8529e-10 | 2007-02-01
| SOV FC | Solenoid-Operated Valve (SOV) Loss of Function / Fail to Control | WSRC |  | 131304380 h | 131304380 | h |  | 0 | 3e-06 | Gamma(WSRC, LL) |  | 3e-06 | 0.3 | 100000 | 18.7656 |  |  | 1.3724e-05 | 7.3131e-07 | 2007-02-01 | 0.0555
| SOV FTO/C | Solenoid-Operated Valve (SOV) Fail to Open/Close | EPIX | 30 | 25650 | 25650 | d | 775 | 0.0011696 | 0.001189 | Beta | JNID/IL | 0.00119 | 30.5 | 25620.77 | 1.3109 |  |  | 0.0015636 | 0.0011761 | 2012-02-01 | 0.9492
| SOV ILS | Solenoid-Operated Valve (SOV) Internal Leak Small | EPIX | 23 | 131304380 h | 131304380 | h | 1153 | 1.7517e-07 | 1.7897e-07 | Gamma | JNID/IL | 1.79e-07 | 23.5 | 131304380 | 1.3631 | 1 to 50 gpm. 1997 - 2004 data. |  | 2.4371e-07 | 1.7644e-07 | 2012-02-01 | 0.2732
| SOV ILL | Solenoid-Operated Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 3.58e-09 | 0.3 | 83798882.6816 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 1.6377e-08 | 8.727e-10 | 2007-02-01
| SOV SOP | Solenoid-Operated Valve (SOV) Spurious Operation | EPIX | 4 | 131304380 h | 131304380 | h | 1153 | 3.0464e-08 | 3.4272e-08 | Gamma | JNID/IL | 3.43e-08 | 4.5 | 131304380 | 1.8776 |  |  | 6.4427e-08 | 3.1769e-08 | 2012-02-01 | 0.0521
| TBV FC | Turbine Bypass Valve (TBV) Loss of Function / Fail to Control | EPIX | 18 | 17548608 h | 17548608 | h | 154 | 1.0257e-06 | 1.0542e-06 | Gamma | JNID/IL | 1.05e-06 | 18.5 | 17548608 | 1.419 | [5 empty] | 0.2863
| TBV FTC | Turbine Bypass Valve (TBV) Fail to Close | EPIX | 0 | 2023 | 2023 | d | 77 | 0 | 0.00024704 | Beta | JNID/IL | 0.000247 | 0.5 | 2023.82 | 3.8421
| TBV FTO | Turbine Bypass Valve (TBV) Fail to Open | EPIX | 8 | 2023 | 2023 | d | 77 | 0.0039545 | 0.0041996 | Beta | JNID/IL | 0.0042 | 8.5 | 2015.82 | 1.6214 | [5 empty] | 0.0067 | High
| VBV FTC | Vacuum Breaker Valve (VBV) Fail to Close | EPIX | 6 | 20108 | 20108 | d | 167 | 0.00029839 | 0.00032324 | Beta | EB/PL/KS | 0.0002971 | 0.7141 | 2402 | 3.3793 |  |  | 0.0010042 | 0.00017508 | 2012-02-01 | 0.1685
| VBV FTO | Vacuum Breaker Valve (VBV) Fail to Open | EPIX | 4 | 20108 | 20108 | d | 167 | 0.00019893 | 0.00022378 | Beta | JNID/IL | 0.000224 | 4.5 | 20104.9 | 1.8795 |  |  | 0.00042064 | 0.00020744 | 2012-02-01 | 0.3177
| VBV ILS | Vacuum Breaker Valve (VBV) Internal Leak Small | EPIX | 15 | 37300280 h | 37300280 | h | 336 | 4.0214e-07 | 4.1555e-07 | Gamma | JNID/IL | 4.16e-07 | 15.5 | 37300280 | 1.4495 | [5 empty] | 0.3652
| XVM ELS | Manual Valve (XVM) External Leak Small | EPIX | 26 | 100961448 h | 100961448 | h | 886 | 2.5752e-07 | 2.6248e-07 | Gamma | JNID/IL | 2.62e-07 | 26.5 | 100961448 | 1.3435 |  |  | 3.5159e-07 | 2.5918e-07 | 2012-02-01 | 0.4039
| XVM ELL | Manual Valve External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 1.834e-08 | 0.3 | 16357688.1134 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 8.3896e-08 | 4.4708e-09 | 2007-02-01
| XVM FTO/C | Manual Valve (XVM) Fail to Open/Close | EPIX | 0 | 2605 | 2605 | d | 76 | 0 | 0.00019186 | Beta | JNID/IL | 0.000192 | 0.5 | 2605.71 | 3.8385 |  |  | 0.00073692 | 8.7301e-05 | 2012-02-01 | 0.0105 | Significant
| XVM ILS | Manual Valve (XVM) Internal Leak Small | EPIX | 13 | 100961448 h | 100961448 | h | 886 | 1.2876e-07 | 1.3371e-07 | Gamma | JNID/IL | 1.34e-07 | 13.5 | 100961448 | 1.4851 |  |  | 1.9866e-07 | 1.3043e-07 | 2012-02-01 | 0.193
| XVM ILL | Manual Valve Internal Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ILS*0.02, LL) |  | 2.68e-09 | 0.3 | 111940298.5075 | 18.7656 | > 50 gpm. Small leak times 0.02 |  | 1.226e-08 | 6.533e-10 | 2007-02-01
| XVM SOP | Manual Valve (XVM) Spurious Operation | EPIX | 8 | 100961448 h | 100961448 | h | 886 | 7.9238e-08 | 8.4191e-08 | Gamma | JNID/IL | 8.42e-08 | 8.5 | 100961448 | 1.6271 |  |  | 1.3662e-07 | 8.0913e-08 | 2012-02-01 | 0.08
Pumps | EDP AFW FTR>1H | Engine-Driven Pump (EDP) Standby Fail to Run greater than 1 hour | EPIX | 0 | 231 h | 231 | h | 5 | 0 | 0.0021645 | Gamma | JNID/IL | 0.00216 | 0.5 | 231.06 | 3.8472 |  |  | 0.0082871 | 0.00098504 | 2012-02-01 | 0.1676
| EDP AFW FTR≤1H | Engine-Driven Pump (EDP) Standby Fail to Run less than or equal to 1 hour | EPIX | 4 | 584 h | 584 | h | 5 | 0.0068493 | 0.0077055 | Gamma | JNID/IL | 0.0077 | 4.5 | 580.01 | 1.8701 |  |  | 0.014436 | 0.0071447 | 2012-02-01 | 0.4305
| EDP AFW FTS | Engine-Driven Pump (EDP) Fail to Start | EPIX | 6 | 1132 | 1132 | d | 5 | 0.0053004 | 0.005737 | Beta | EB/PL/KS | 0.004878 | 0.633 | 129.1 | 3.5219 |  |  | 0.017181 | 0.0026777 | 2012-02-01 | 0.2431
| EDP ELS | Engine-Driven Pump (EDP) External Leak Small | EPIX | 7 | 6267335 h | 6267335 | h | 55 | 1.1169e-06 | 1.1967e-06 | Gamma | JNID/IL | 1.2e-06 | 7.5 | 6267335 | 1.6583 |  |  | 1.9941e-06 | 1.1439e-06 | 2012-02-01 | 0.8067
| EDP ELL | Diesel-Driven Pump External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 8.4e-08 | 0.3 | 3571428.5714 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 3.8426e-07 | 2.0477e-08 | 2007-02-01
| EDP FTR>1H | Engine-Driven Pump (EDP) Standby Fail to Run greater than 1 hour | EPIX | 9 | 4182 h | 4182 | h | 36 | 0.0021521 | 0.0022716 | Gamma | JNID/IL | 0.00227 | 9.5 | 4182.08 | 1.5859 | No data. FTR≤1H times 0.06 | 2005-10-04 | 0.0036039 | 0.0021924 | 2012-02-01 | 0.9277
| EDP FTR≤1H | Engine-Driven Pump (EDP) Standby Fail to Run less than or equal to 1 hour | EPIX | 8 | 7698 h | 7698 | h | 36 | 0.0010392 | 0.0011042 | Gamma | EB/PL/KS | 0.001255 | 0.5542 | 441.1 | 3.7004 |  |  | 0.004652 | 0.00062287 | 2012-02-01 | 0.3826
| EDP FTS | Engine-Driven Pump (EDP) Fail to Start | EPIX | 44 | 13647 | 13647 | d | 41 | 0.0032242 | 0.0032606 | Beta | EB/PL/KS | 0.005094 | 0.7316 | 142.9 | 3.3412 |  |  | 0.01702 | 0.0030556 | 2012-02-01 | 0.0224 | Significant
| MDP ELS | Motor-Driven Pump (MDP) External Leak Small | EPIX | 93 | 258455367 h | 258455367 | h | 2271 | 3.5983e-07 | 3.6176e-07 | Gamma | EB/PL/KS | 3.423e-07 | 0.7311 | 2136000 | 3.3509 |  |  | 1.1469e-06 | 2.0433e-07 | 2012-02-01 | 0.9295
| MDP ELL | Motor-Driven Pump External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 2.3961e-08 | 0.3 | 12520345.5615 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.0961e-07 | 5.841e-09 | 2007-02-01
| MDP FTR | Motor-Driven Pump (MDP) Fail to Run | EPIX | 149 | 45853637 h | 45853637 | h | 704 | 3.2495e-06 | 3.2604e-06 | Gamma | EB/PL/KS | 3.528e-06 | 2.292 | 649600 | 2.2732 |  |  | 8.0209e-06 | 3.0306e-06 | 2012-02-01 | 0.033 | Significant
| MDP FTS | Motor-Driven Pump (MDP) Fail to Start | EPIX | 150 | 114473 | 114473 | d | 706 | 0.0013104 | 0.0013147 | Beta | EB/PL/KS | 0.001362 | 3.282 | 2406 | 2.0448 |  |  | 0.0027855 | 0.001227 | 2012-02-01 | 0.006 | High
| MDP SBY FTR>1H | Motor-Driven Pump (MDP) Standby Fail to Run greater than 1 hour | EPIX | 110 | 14219837 h | 14219837 | h | 1341 | 7.7357e-06 | 7.7708e-06 | Gamma | EB/PL/KS | 1.041e-05 | 0.781 | 75010 | 3.2728 |  |  | 3.4069e-05 | 6.4441e-06 | 2012-02-01 | 0.7459
| MDP SBY FTR≤1H | Motor-Driven Pump (MDP) Standby Fail to Run less than or equal to 1 hour | EPIX | 38 | 326023 h | 326023 | h | 1341 | 0.00011656 | 0.00011809 | Gamma | EB/PL/KS | 0.000123 | 1.82 | 14790 | 2.4447 |  |  | 0.00030081 | 0.0001014 | 2012-02-01 | 0.111
| MDP SBY FTS | Motor-Driven Pump (MDP) Fail to Start | EPIX | 315 | 363935 | 363935 | d | 1341 | 0.00086554 | 0.00086691 | Beta | EB/PL/KS | 0.0009474 | 1.948 | 2054 | 2.3908 |  |  | 0.0022653 | 0.00079147 | 2012-02-01 | 0.0575
| PDP ELS | Positive Displacement Pump (PDP) External Leak Small | EPIX | 14 | 19599696 h | 19599696 | h | 172 | 7.143e-07 | 7.3981e-07 | Gamma | JNID/IL | 7.4e-07 | 14.5 | 19599696 | 1.473 |  |  | 1.0857e-06 | 7.2287e-07 | 2012-02-01 | 0.9933
| PDP ELL | Positive Displacement Pump External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 5.18e-08 | 0.3 | 5791505.7915 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 2.3696e-07 | 1.2627e-08 | 2007-02-01
| PDP FTR | Positive Displacement Pump (PDP) Fail to Run | EPIX | 48 | 2216149 h | 2216149 | h | 59 | 2.1659e-05 | 2.1885e-05 | Gamma | EB/PL/KS | 2.302e-05 | 1.152 | 50060 | 2.8501 |  |  | 6.56e-05 | 1.68e-05 | 2012-02-01 | 0.5991
| PDP FTS | Positive Displacement Pump (PDP) Fail to Start | EPIX | 62 | 25438 | 25438 | d | 62 | 0.0024373 | 0.0024569 | Beta | EB/PL/KS | 0.003149 | 1.02 | 322.9 | 2.9705 |  |  | 0.0093529 | 0.0022041 | 2012-02-01 | 0.1585
| PDP SBY FTR>1H | Positive Displacement Pump (PDP) Standby Fail to Run greater than 1 hour | EPIX | 2 | 1175 h | 1175 | h | 74 | 0.0017021 | 0.0021277 | Gamma | JNID/IL | 0.00213 | 2.5 | 1174.91 | 2.2113 | No data. FTR≤1H times 0.06 | 2005-10-04 | 0.0047112 | 0.0018518 | 2012-02-01 | 0.256
| PDP SBY FTR≤1H | Positive Displacement Pump (PDP) Standby Fail to Run less than or equal to 1 hour | EPIX | 2 | 3527 h | 3527 | h | 74 | 0.00056705 | 0.00070882 | Gamma | JNID/IL | 0.000709 | 2.5 | 3525.21 | 2.2144 |  |  | 0.0015702 | 0.00061719 | 2012-02-01 | 0.2498
| PDP SBY FTS | Positive Displacement Pump (PDP) Fail to Start | EPIX | 62 | 25438 | 25438 | d | 62 | 0.0024373 | 0.0024569 | Beta | JNID/IL | 0.00179 | 14.5 | 8065.93 | 1.4693 |  |  | 0.0026324 | 0.0017535 | 2012-02-01 | 0.5041
| PMP FTR | Pump Volute Fail to Run | EPIX | 9 | 74199 | 74199 | h | 180 | 0.0001213 | 0.00012803 | Gamma (EB/PL/KS, EB/PL/KS) |  | 0.000135 | 1.389 | 10288.8889 | 3.4587 |  |  | 0.00036088 | 0.00010434 | 2007-02-01
| PMP FTS | Pump Volute Fail to Start | EPIX | 4 | 16776 | 16776 | d | 180 | 0.00023844 | 0.00026822 | Beta (Jeffreys, SCNID) |  | 0.00026822 | 0.5 | 1863.6111 | 8.4401 |  |  | 0.0010303 | 0.00012207 | 2007-02-01
| TDP ELS | Turbine-Driven Pump (TDP) External Leak Small | EPIX | 14 | 20036597 h | 20036597 | h | 178 | 6.9872e-07 | 7.2368e-07 | Gamma | JNID/IL | 7.24e-07 | 14.5 | 20036597 | 1.4641 |  |  | 1.062e-06 | 7.0711e-07 | 2012-02-01 | 0.6163
| TDP ELL | Turbine-Driven Pump External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 5.068e-08 | 0.3 | 5919494.8698 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 2.3184e-07 | 1.2354e-08 | 2007-02-01
| TDP FTR | Turbine-Driven Pump (TDP) Fail to Run | EPIX | 39 | 4276404 h | 4276404 | h | 42 | 9.1198e-06 | 9.2367e-06 | Gamma | EB/PL/KS | 9.338e-06 | 1.792 | 191900 | 2.4566 |  |  | 2.2942e-05 | 7.6703e-06 | 2012-02-01 | 0.4143
| TDP FTS | Turbine-Driven Pump (TDP) Fail to Start | EPIX | 8 | 957 | 957 | d | 42 | 0.0083595 | 0.0088727 | Beta | EB/PL/KS | 0.008932 | 0.8767 | 97.28 | 3.1247 |  |  | 0.027912 | 0.0058911 | 2012-02-01 | 0.0731
| TDP SBY FTR>1H | Turbine-Driven Pump (TDP) Standby Fail to Run greater than 1 hour | EPIX | 12 | 8028 h | 8028 | h | 133 | 0.0014948 | 0.0015571 | Gamma | JNID/IL | 0.00156 | 12.5 | 8027.74 | 1.5064 |  | 2005-10-04 | 0.0023451 | 0.0015158 | 2012-02-01 | 0.0316 | Significant
| TDP SBY FTR≤1H | Turbine-Driven Pump (TDP) Standby Fail to Run less than or equal to 1 hour | EPIX | 54 | 13062 h | 13062 | h | 133 | 0.0041341 | 0.0041724 | Gamma | EB/PL/KS | 0.004426 | 0.9618 | 216.4 | 3.0298 |  |  | 0.0135 | 0.0030325 | 2012-02-01 | 0.8117
| TDP SBY FTS | Turbine-Driven Pump (TDP) Fail to Start | EPIX | 117 | 19760 | 19760 | d | 133 | 0.0059211 | 0.0059461 | Beta | EB/PL/KS | 0.006493 | 0.9421 | 144.1 | 3.0494 |  |  | 0.019809 | 0.0044132 | 2012-02-01 | 0.264
Generators | CTG FTLR | Combustion Turbine Generator (CTG) Fail to Load/Run | EPIX | 2 | 156296 | 156296 | d | 3 | 1.2796e-05 | 1.5995e-05 | Beta | JNID/IL | 1.6e-05 | 2.5 | 156294.897 | 2.2125 |  |  | 3.5415e-05 | 1.3921e-05 | 2012-02-01
| CTG FTR | Combustion Turbine Generator (CTG) Fail to Run | EPIX | 3 | 473 h | 473 | h | 3 | 0.0063425 | 0.0073996 | Gamma | JNID/IL | 0.0074 | 3.5 | 473.2 | 2.0135 | 1998 - 3Q2004 data used. Data limited so EDG FTR used |  | 0.014864 | 0.0067052 | 2012-02-01 | 0.1643
| CTG FTS | Combustion Turbine Generator (CTG) Fail to Start | EPIX | 10 | 672 | 672 | d | 3 | 0.014881 | 0.015602 | Beta | JNID/IL | 0.0156 | 10.5 | 662.86 | 1.5513 |  |  | 0.024172 | 0.015116 | 2012-02-01 | 0.042 | Significant
| EDG FTLR | Emergency Diesel Generator (EDG) Fail to Load/Run | EPIX | 182 | 49383 | 49383 | d | 224 | 0.0036855 | 0.0036955 | Beta | EB/PL/KS | 0.003779 | 2.774 | 731.1 | 2.1437 |  |  | 0.0081027 | 0.0033397 | 2012-02-01 | 0.1375
| EDG FTR | Emergency Diesel Generator (EDG) Fail to Run | EPIX | 113 | 106820 h | 106820 | h | 224 | 0.0010579 | 0.0010625 | Gamma | EB/PL/KS | 0.001096 | 4.487 | 4093 | 1.8814 |  |  | 0.0020594 | 0.001015 | 2012-02-01 | 0.0067 | High
| EDG FTS | Emergency Diesel Generator (EDG) Fail to Start | EPIX | 161 | 56695 | 56695 | d | 224 | 0.0028398 | 0.0028486 | Beta | EB/PL/KS | 0.002891 | 8.111 | 2798 | 1.6375 |  |  | 0.0047332 | 0.0027733 | 2012-02-01 | 0.9042
| EDG-SBO FTLR | EDG-Station Blackout Fail to Load/Run | EPIX | 4 | 4 | 443.74 | d | 4 |  |  | Beta |  | 0.0101 | 4.5 | 440.24 | 2.028 |  |  | 0.019216 | 0.0094753 |  | 0.228
| EDG-SBO FTR | EDG-Station Blackout Fail to Run | EPIX | 1 | 1 | 1155.3 | h | 4 |  |  | Gamma |  | 0.0013 | 1.5 | 1155.3 | 3.303 |  |  | 0.0033821 | 0.001024 |  | 0.2217
| EDG-SBO FTS | EDG-Station Blackout Fail to Start | EPIX | 14 | 14 | 372.13 | d | 4 |  |  | Beta |  | 0.04319 | 1.094 | 24.23 | 4.048 |  |  | 0.13105 | 0.032374 |  | 0.7745
| HTG FTLR | Hydro Turbine Generator (HTG) Fail to Load/Run | EPIX | 6 | 3087 | 3087 | d | 2 | 0.0019436 | 0.0021049 | Beta | JNID/IL | 0.0021 | 6.5 | 3081.47 | 1.7238 |  |  | 0.0036285 | 0.0020023 | 2012-02-01 | 0.6468
| HTG FTR>1H | Hydro Turbine Generator (HTG) Fail to Run | EPIX | 1 | 7449 h | 7449 | h | 2 | 0.00013425 | 0.00020137 | Gamma | JNID/IL | 0.000201 | 1.5 | 7448.95 | 2.6119 |  |  | 0.00052455 | 0.00015881 | 2012-02-01 | 0.7065
| HTG FTS | Hydro Turbine Generator (HTG) Fail to Start | EPIX | 7 | 5141 | 5141 | d | 2 | 0.0013616 | 0.0014586 | Beta | JNID/IL | 0.00146 | 7.5 | 5134.96 | 1.6644 |  |  | 0.0024294 | 0.0013943 | 2012-02-01 | 0.0217 | Significant
Relief Valves | PORV ELS | Power-Operated Relief Valve (PORV) External Leak Small | EPIX | 5 | 46264512 h | 46264512 | h | 406 | 1.0807e-07 | 1.1888e-07 | Gamma | JNID/IL | 1.19e-07 | 5.5 | 46264512 | 1.7899 |  |  | 2.1264e-07 | 1.1176e-07 |  | 0.335
| PORV FC | Power-Operated Relief Valve (PORV) Loss of Function / Fail to Control | EPIX | 12 | 46264512 h | 46264512 | h | 406 | 2.5938e-07 | 2.7019e-07 | Gamma | JNID/IL | 2.7e-07 | 12.5 | 46264512 | 1.5074 |  |  | 4.0693e-07 | 2.6302e-07 |  | 0.4909
| PORV ILS | Power-Operated Relief Valve (PORV) Internal Leak Small | EPIX | 23 | 46264512 h | 46264512 | h | 406 | 4.9714e-07 | 5.0795e-07 | Gamma | JNID/IL | 5.08e-07 | 23.5 | 46264512 | 1.3622 |  |  | 6.9169e-07 | 5.0076e-07 |  | 0.0265 | Significant
| PORV MSS FTC | Power-Operated Relief Valve (PORV) Fail to Close | EPIX | 14 | 8363 | 8363 | d | 126 | 0.001674 | 0.0017336 | Beta | JNID/IL | 0.00173 | 14.5 | 8349.36 | 1.4682 |  |  | 0.0025432 | 0.0016941 | 2012-02-01 | 0.3868
| PORV MSS FTO | Power-Operated Relief Valve (PORV) Fail to Open | EPIX | 41 | 8363 | 8363 | d | 126 | 0.0049025 | 0.0049617 | Beta | EB/PL/KS | 0.005564 | 2.123 | 379.4 | 2.3221 |  |  | 0.012922 | 0.0047276 | 2012-02-01 | 0.9159
| PORV PPR FTC | Power-Operated Relief Valve (PORV) Fail to Close | EPIX | 4 | 4657 | 4657 | d | 120 | 0.00085892 | 0.00096608 | Beta | JNID/IL | 0.000966 | 4.5 | 4653.08 | 1.8841 |  |  | 0.0018157 | 0.00089575 | 2012-02-01 | 0.6777
| PORV PPR FTO | Power-Operated Relief Valve (PORV) Fail to Open | EPIX | 16 | 4657 | 4657 | d | 120 | 0.0034357 | 0.0035423 | Beta | JNID/IL | 0.00354 | 16.5 | 4641.08 | 1.4379 |  |  | 0.0050851 | 0.0034718 | 2012-02-01 | 0.1599
| PORV SOP | Power-Operated Relief Valve (PORV) Spurious Operation | EPIX | 21 | 46264512 h | 46264512 | h | 406 | 4.5391e-07 | 4.6472e-07 | Gamma | JNID/IL | 4.65e-07 | 21.5 | 46264512 | 1.3785 |  |  | 6.4092e-07 | 4.5753e-07 | 2012-02-01 | 0.5041
| RVL ELS | Low-Capacity Relief Valve (RVL) External Leak Small | WSRC |  | 7520832 h | 7520832 | h |  | 0 | 6.6482e-08 | Gamma | JNID/IL | 6.6482e-08 | 0.3 | 4512499.2 | 2.0108 |  |  | 3.0412e-07 | 1.6206e-08 |  | 0.8756
| RVL FTC | Low-Capacity Relief Valve (RVL) Fail to Close | WSRC |  | 185 | 185 | d |  | 0 | 0.0026882 | Beta | JNID/IL | 0.0026882 | 0.3 | 111.6 | 1.7703 |  |  | 0.01226 | 0.00065714 |  | 0.8961
| RVL FTO | Low-Capacity Relief Valve (RVL) Fail to Open | WSRC |  | 185 | 185 | d |  | 0 | 0.0026882 | Beta | JNID/IL | 0.0026882 | 0.3 | 111.6 | 2.5931 |  |  | 0.01226 | 0.00065714 |  | 0.5521
| RVL ILS | Low-Capacity Relief Valve (RVL) Internal Leak Small | WSRC |  | 7520832 h | 7520832 | h |  | 0 | 6.6482e-08 | Gamma | JNID/IL | 6.6482e-08 | 0.3 | 4512499.2 | 1.4515 |  |  | 3.0412e-07 | 1.6206e-08 |  | 0.0948
| RVL SO | Low-Capacity Relief Valve (RVL) Spurious Opening | WSRC |  | 7520832 h | 7520832 | h |  | 0 | 6.6482e-08 | Gamma | JNID/IL | 6.6482e-08 | 0.3 | 4512499.2 | 2.6131 |  |  | 3.0412e-07 | 1.6206e-08 |  | 0.7912
| SRV ELS | Safety Relief Valve (SRV) External Leak Small | EPIX | 1 | 62541477 h | 62541477 | h | 577 | 1.5989e-08 | 2.3984e-08 | Gamma | JNID/IL | 2.4e-08 | 1.5 | 62541477 | 2.6042 | [5 empty] | 0.5681
| SRV FTC | Safety Relief Valve (SRV) Fail to Close | EPIX | 6 | 7396 | 7396 | d | 409 | 0.00081125 | 0.00087873 | Beta | EB/PL/KS | 0.0008558 | 0.922 | 1076 | 3.0825 |  |  | 0.0026386 | 0.00057409 | 2012-02-01 | 0.7933
| SRV FTCL | Safety Relief Valve Fail to Close (Passing Liquid) | WSRC |  |  |  | h |  |  | 0.1 | Beta (WSRC, SCNID) |  | 0.1 | 0.5 | 4.5 | 6.9689 | Average of 95th percentiles of FTC data entries |  | 0.36249 | 0.052015 | 2007-02-01
| SRV FTO | Safety Relief Valve (SRV) Fail to Open | EPIX | 20 | 7396 | 7396 | d | 409 | 0.0027042 | 0.0027714 | Beta | JNID/IL | 0.00277 | 20.5 | 7376.39 | 1.3899 |  |  | 0.0038473 | 0.0027267 | 2012-02-01 | 0.4818
| SRV SOP | Safety Relief Valve (SRV) Spurious Operation | EPIX | 12 | 62541477 h | 62541477 | h | 577 | 1.9187e-07 | 1.9987e-07 | Gamma | EB/PL/KS | 2.431e-07 | 0.4426 | 1821000 | 4.0111 |  |  | 9.7486e-07 | 9.8429e-08 | 2012-02-01 | 0.0489 | Significant
| SVV ELS | Safety Valve (SVV) External Leak Small | EPIX | 4 | 161355977 h | 161355977 | h | 1416 | 2.479e-08 | 2.7889e-08 | Gamma | JNID/IL | 2.79e-08 | 4.5 | 161355977 | 1.8781 |  |  |  |  | 2012-02-01 | 1
| SVV FTC | Safety Valve (SVV) Fail to Close | EPIX | 3 | 17320 | 17320 | d | 950 | 0.00017321 | 0.00020207 | Beta | JNID/IL | 0.000202 | 3.5 | 17317.83 | 2.0099 |  |  | 0.00040603 | 0.00018319 | 2012-02-01 | 0.058
| SVV FTCL | Safety Valve Fail to Close (Passing Liquid) | EPIX |  |  |  | h |  |  | 0.1 | Beta (WSRC, SCNID) |  | 0.1 | 0.5 | 4.5 | 6.9689 | Average of 95th percentiles of FTC data entries |  | 0.36249 | 0.052015 | 2007-02-01
| SVV FTO | Safety Valve (SVV) Fail to Open | EPIX | 7 | 17320 | 17320 | d | 950 | 0.00040416 | 0.000433 | Beta | EB/PL/KS | 0.0004234 | 1.034 | 2441 | 2.9594 |  |  | 0.0012533 | 0.00029741 | 2012-02-01 | 0.5204
| SVV ILS | Safety Valve (SVV) Internal Leak Small | EPIX | 14 | 161355977 h | 161355977 | h | 1416 | 8.6765e-08 | 8.9863e-08 | Gamma | JNID/IL | 8.99e-08 | 14.5 | 161355977 | 1.4683 |  |  |  |  | 2012-02-01 | 0.3224
| SVV MSS FTC | Safety Valve (SVV) Fail to Close | EPIX | 2 | 14809 | 14809 | d | 760 | 0.00013505 | 0.0001688 | Beta | JNID/IL | 0.000169 | 2.5 | 14807.04 | 2.213 |  |  |  |  | 2012-02-01 | 0.0259 | Significant
| SVV MSS FTO | Safety Valve (SVV) Fail to Open | EPIX | 6 | 14809 | 14809 | d | 760 | 0.00040516 | 0.00043889 | Beta | EB/PL/KS | 0.0004505 | 0.5044 | 1119 | 3.8291 |  |  |  |  | 2012-02-01 | 0.3848
| SVV MSS SOP | Safety Valve (SVV) Spurious Operation | EPIX | 9 | 136514441 h | 136514441 | h | 1198 | 6.5927e-08 | 6.959e-08 | Gamma | JNID/IL | 6.96e-08 | 9.5 | 136514441 | 1.5805 |  |  |  |  | 2012-02-01 | 0.0535
| SVV RCS FTC | Safety Valve (SVV) Fail to Close | EPIX | 1 | 2048 | 2048 | d | 147 | 0.00048828 | 0.00073206 | Beta | JNID/IL | 0.000732 | 1.5 | 2047.76 | 2.6093 |  |  |  |  | 2012-02-01 | 0.9981
| SVV RCS FTO | Safety Valve (SVV) Fail to Open | EPIX | 1 | 2048 | 2048 | d | 147 | 0.00048828 | 0.00073206 | Beta | JNID/IL | 0.000732 | 1.5 | 2047.76 | 2.6093 |  |  |  |  | 2012-02-01 | 0.6
| SVV RCS SOP | Safety Valve (SVV) Spurious Operation | EPIX | 9 | 136514441 h | 136514441 | h | 1198 | 6.5927e-08 | 6.959e-08 | Gamma | JNID/IL | 6.96e-08 | 9.5 | 136514441 | 1.5805 |  |  | 1.104e-07 | 6.7164e-08 | 2012-02-01 | 0.7754
Electrical Equipment | ABT FC | Automatic Bus Transfer Switch (ABT) Loss of Function / Fail to Control | EPIX | 0 | 311 | 311 | h | 23 | 0 | 0.0016077 | Gamma | JNID/IL | 0.0016 | 0.5 | 311.63 | 3.8438 |  |  | 0.0061494 | 0.00073025 | 2012-02-01 | 0.3083
| ABT SOP | Automatic Bus Transfer Switch (ABT) Spurious Operation | EPIX | 0 | 3646454 h | 3646454 | h | 32 | 0 | 1.3712e-07 | Gamma | JNID/IL | 1.37e-07 | 0.5 | 3646454 | 3.8467 |  |  | 5.2674e-07 | 6.2381e-08 | 2012-02-01 | 0.9934
| BAT FTOP | Battery (BAT) Fail to Operate | EPIX | 33 | 57203716 h | 57203716 | h | 502 | 5.7689e-07 | 5.8563e-07 | Gamma | EB/PL/KS | 5.861e-07 | 1.883 | 3213000 | 2.4177 |  |  | 1.417e-06 | 4.8621e-07 | 2012-02-01 | 0.8175
| BCH FTOP | Battery Charger (BCH) Fail to Operate | EPIX | 233 | 95947373 h | 95947373 | h | 842 | 2.4284e-06 | 2.4336e-06 | Gamma | EB/PL/KS | 2.708e-06 | 1.281 | 472800 | 2.7485 |  |  | 7.4454e-06 | 2.046e-06 | 2012-02-01 | 0.0098 | High
| BUS AC FTOP | Bus (BUS) Fail to Operate | EPIX | 101 | 146884096 h | 146884096 | h | 1289 | 6.8762e-07 | 6.9102e-07 | Gamma | EB/PL/KS | 1.388e-06 | 0.7031 | 506500 | 3.3984 |  |  | 4.7174e-06 | 8.1008e-07 | 2012-02-01 | 0.594
| BUS DC FTOP | Bus (BUS) Fail to Operate | EPIX | 1 | 6381312 h | 6381312 | h | 56 | 1.5671e-07 |  | Gamma | JNID/IL | 2.35e-07 | 1.5 | 6381312 | 2.6043 |  |  | 6.1231e-07 | 1.8538e-07 | 2012-02-01 | 0.4301
| CRB FTO/C | Circuit Breaker (CRB) Fail to Open/Close | EPIX | 179 | 126213 | 126213 | d | 4494 | 0.0014182 | 0.0014222 | Beta | EB/PL/KS | 0.002392 | 0.9548 | 398.3 | 3.041 |  |  | 0.0073 | 0.0016306 | 2012-02-01 | 0.0122 | Significant
| CRB SOP | Circuit Breaker (CRB) Spurious Operation | EPIX | 4 | 91161573 h | 91161573 | h | 800 | 4.3878e-08 | 4.9363e-08 | Gamma | EB/PL/KS | 2.113e-07 | 1.156 | 5470000 | 2.8471 |  |  | 6.0172e-07 | 1.5446e-07 | 2012-02-01 | 0.0791
| CRBDC FTOC | Circuit Breaker (CRB) Fail to Open/Close | EPIX | 7 | 13080 | 13080 | d | 667 | 0.00053517 | 0.00057335 | Beta | JNID/IL | 0.000573 | 7.5 | 13073.74 | 1.6667 |  |  | 0.00095595 | 0.00054838 | 2012-02-01 | 0.6389
| CRBDC SOP | Circuit Breaker (CRB) Spurious Operation | EPIX | 4 | 91161573 h | 91161573 | h | 800 | 4.3878e-08 | 4.9363e-08 | Gamma | JNID/IL | 4.94e-08 | 4.5 | 91161573 | 1.8785 |  |  | 9.2797e-08 | 4.5758e-08 | 2012-02-01 | 1
| CRBHV FTOC | Circuit Breaker (CRB) Fail to Open/Close | EPIX | 39 | 7964 | 7964 | d | 257 | 0.004897 | 0.0049592 | Beta | EB/PL/KS | 0.006662 | 1.09 | 162.5 | 2.897 |  |  | 0.019494 | 0.0048033 | 2012-02-01 | 0.4811
| CRBHV SOP | Circuit Breaker (CRB) Spurious Operation | EPIX | 4 | 91161573 h | 91161573 | h | 800 | 4.3878e-08 | 4.9363e-08 | Gamma | EB/PL/KS | 8.077e-07 | 1.37 | 1696000 | 2.6854 |  |  | 2.1695e-06 | 6.2195e-07 | 2012-02-01 | 0.0182 | Significant
| CRBMV FTOC | Circuit Breaker (CRB) Fail to Open/Close | EPIX | 59 | 43068 | 43068 | d | 1087 | 0.0013699 | 0.0013815 | Beta | EB/PL/KS | 0.002703 | 0.5562 | 205.2 | 3.6937 |  |  | 0.010023 | 0.0013476 | 2012-02-01 | 0.1995
| CRBMV SOP | Circuit Breaker (CRB) Spurious Operation | EPIX | 4 | 91161573 h | 91161573 | h | 800 | 4.3878e-08 | 4.9363e-08 | Gamma | JNID/IL | 1.04e-07 | 14.5 | 139818814 | 1.4615 |  |  | 1.5219e-07 | 1.0133e-07 | 2012-02-01 | 0.0543
| INV FTOP | Inverter (INV) Fail to Operate | EPIX | 95 | 25981056 h | 25981056 | h | 228 | 3.6565e-06 | 3.6758e-06 | Gamma | EB/PL/KS | 5.6e-06 | 1.184 | 211400 | 2.8232 |  |  | 1.5815e-05 | 4.1262e-06 | 2012-02-01 | 0.4357
| MCC FTOP | Motor Control Center (MCC) Fail to Operate | EPIX | 6 | 24727584 h | 24727584 | h | 217 | 2.4264e-07 | 2.6286e-07 | Gamma | EB/PL/KS | 2.612e-07 | 0.8438 | 3230000 | 3.183 | [5 empty] | 0.9485
| SEQ FTOP | Sequencer Fail to Operate | EPIX | 2 | 750 | 750 | h | 225 | 0.0026667 | 0.0033333 | Beta (Jeffreys, SCNID) |  | 0.0033333 | 0.5 | 149.5 | 8.3962 |  |  | 0.012787 | 0.0015229 | 2007-02-01
| TFM FTOP | Transformer (TFM) Fail to Operate | EPIX | 267 | 599615105 h | 599615105 | h | 5262 | 4.4529e-07 | 4.4612e-07 | Gamma | EB/PL/KS | 9.437e-07 | 0.9572 | 1014000 | 3.0423 |  |  | 2.8721e-06 | 6.4278e-07 | 2012-02-01 | 0.1035
Strainers | FLT ELS | Filter (FLT) External Leak Small | EPIX | 3 | 24955463 h | 24955463 | h | 219 | 1.2021e-07 | 1.4025e-07 | Gamma | JNID/IL | 1.4e-07 | 3.5 | 24955463 | 2.0143 | [5 empty] | 0.5138
| FLT PG | Filter (FLT) Plugged | EPIX | 3 | 11281248 h | 11281248 | h | 99 | 2.6593e-07 | 3.1025e-07 | Gamma | JNID/IL | 3.1e-07 | 3.5 | 11281248 | 2.0097 | [5 empty] | 0.5138
| FLTSC BYP | Self-Cleaning Strainer (FLTSC) Bypass | EPIX | 1 | 19143936 h | 19143936 | h | 168 | 5.2236e-08 | 7.8354e-08 | Gamma | JNID/IL | 7.84e-08 | 1.5 | 19143936 | 2.602 | [5 empty] | 0.4301
| FLTSC ELS | Self-Cleaning Strainer (FLTSC) External Leak Small | EPIX | 16 | 19143936 h | 19143936 | h | 168 | 8.3577e-07 | 8.6189e-07 | Gamma | JNID/IL | 8.62e-07 | 16.5 | 19143936 | 1.4385 | [5 empty] | 0.04 | Significant
| FLTSC FTOP | Self-Cleaning Strainer (FLTSC) Fail to Operate | EPIX | 76 | 19143936 h | 19143936 | h | 168 | 3.9699e-06 | 3.996e-06 | Gamma | JNID/IL | 4e-06 | 76.5 | 19143936 | 1.195 | [5 empty] | 0.9973
| FLTSC PG | Self-Cleaning Strainer (FLTSC) Plugged | EPIX | 44 | 19143936 h | 19143936 | h | 168 | 2.2984e-06 | 2.3245e-06 | Gamma | JNID/IL | 2.32e-06 | 44.5 | 19143936 | 1.2629 | [5 empty] | 0.4567
| SMP PG | Sump Strainer (SMP) Plugged | EPIX | 5 | 10825440 h | 10825440 | h | 95 | 4.6187e-07 | 5.0806e-07 | Gamma | JNID/IL | 5.08e-07 | 5.5 | 10825440 | 1.7894 |  |  | 9.0875e-07 | 4.7762e-07 | 2012-02-01 | 0.3452
| TRK PG | Trash Rack (TRK) Plugged | EPIX | 4 | 1139520 h | 1139520 | h | 10 | 3.5102e-06 | 3.949e-06 | Gamma | JNID/IL | 3.95e-06 | 4.5 | 1139520 | 1.8785 |  |  |  |  | 2012-02-01 | 0.7525
| TSA PG | Traveling Screen Assembly (TSA) Plugged | EPIX | 64 | 23929916 h | 23929916 | h | 210 | 2.6745e-06 | 2.6954e-06 | Gamma | EB/PL/KS | 3.073e-06 | 0.5221 | 169900 | 3.7813 | For SWSs with potential for environmental insults |  | 1.1624e-05 | 1.4513e-06 | 2012-02-01 | 0.8667
Reactor Protection | BIS FTOP | Bistable Fail to Operate | RPS SSs | 55 |  | 102094 | d |  | 0.00053872 | 0.00054361 | Beta (Jeffreys, SCNID) |  | 0.00054361 | 0.5 | 919.2748 | 8.4439 |  |  | 0.0020894 | 0.00024744 | 2007-02-01
| MSW FTO/C | Manual Switch Fail to Open or Close | RPS SSs | 2 | 19789 | 19789 | d |  | 0.00010107 | 0.00012633 | Beta (Jeffreys, SCNID) |  | 0.00012633 | 0.5 | 3957.5 | 8.4422 |  |  | 0.00048525 | 5.748e-05 | 2007-02-01
| PLDT FTOP | Process Logic (Delta Temperature) Fail to Operate | RPS SSs | 24.3 | 4887 | 4887 | h |  | 0.0049724 | 0.0050747 | Beta (Jeffreys, SCNID) |  | 0.0050747 | 0.5 | 98.0282 | 8.3713 |  |  | 0.019452 | 0.0023237 | 2007-02-01
| PLF FTOP | Process Logic (Flow) Fail to Operate | RPS SSs | No data |  |  | h |  |  |  | Beta (PLL, SCNID) |  | 0.00062551 | 0.5 | 798.8421 | 8.435 | No data, so PLL FTOP used |  | 0.0024023 | 0.0002848 | 2007-02-01
| PLL FTOP | Process Logic (Level) Fail to Operate | RPS SSs | 3.3 | 6075 | 6075 | h |  | 0.00054321 | 0.00062551 | Beta (Jeffreys, SCNID) |  | 0.00062551 | 0.5 | 798.8421 | 8.435 |  |  | 0.0024023 | 0.0002848 | 2007-02-01
| PLP FTOP | Process Logic (Pressure) Fail to Operate | RPS SSs | 5.6 | 38115 | 38115 | h |  | 0.00014692 | 0.00016004 | Beta (Jeffreys, SCNID) |  | 0.00016004 | 0.5 | 3123.6803 | 8.4416 |  |  | 0.00061475 | 7.2824e-05 | 2007-02-01
| RLY FTOP | Relay Fail to Operate | RPS SSs | 23.7 |  | 974417 | h |  | 2.4322e-05 | 2.4835e-05 | Beta (Jeffreys, SCNID) |  | 2.4835e-05 | 0.5 | 20132.0826 | 8.4436 |  |  | 9.5403e-05 | 1.1299e-05 | 2007-02-01
| RTB (BME) FTO/C | RPS Breaker (Mechanical) Fail to Open or Close | RPS SSs | 1 | 97359 | 97359 | d |  | 1.0271e-05 | 1.5407e-05 | Beta (Jeffreys, SCNID) |  | 1.5407e-05 | 0.5 | 32452.8333 | 8.4437 |  |  | 5.9184e-05 | 7.0092e-06 | 2007-02-01
| RTB (BSN) FTOP | RPS Breaker (Shunt Trip) Fail to Operate | RPS SSs | 14 | 44104 | 44104 | h |  | 0.00031743 | 0.00032877 | Beta (Jeffreys, SCNID) |  | 0.00032877 | 0.5 | 1520.3276 | 8.4392 |  |  | 0.0012628 | 0.00014963 | 2007-02-01
| RTB (BUV) FTOP | RPS Breaker (Undervoltage Trip) Fail to Operate | RPS SSs | 23.1 | 57199 | 57199 | h |  | 0.00040385 | 0.00041259 | Beta (Jeffreys, SCNID) |  | 0.00041259 | 0.5 | 1211.3432 | 8.4381 |  |  | 0.0015847 | 0.0001878 | 2007-02-01
| RTB FTO/C | RPS Breaker (Combined) Fail to Open or Close | RPS SSs |  |  |  | d |  |  |  | Beta (Jeffreys, SCNID) |  | 1.5542e-05 | 0.5 | 32169.5929 | 8.4437 | RTB combined failure probability is BME + BSN*BUV |  | 5.9705e-05 | 7.0709e-06 | 2007-02-01
| STF FTOP | Sensor/Transmitter (Flow) Fail to Operate | RPS SSs |  |  |  | h |  |  |  | Beta (STL, SCNID) |  | 0.00081469 | 0.5 | 613.2273 | 8.4439 | Level sensor/transmitter results used. Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  |  |  | 2007-02-01
|  | Sensor/Transmitter (Flow) Fail to Operate | RPS SSs |  |  |  | h |  |  |  | Gamma (STL, SCNID) |  | 1.0171e-07 | 0.5 | 4915984 | 8.4439 |  |  |  |  | 2007-02-01
| STL FTOP | Sensor/Transmitter (Level) Fail to Operate | RPS SSs | 5 | 6750 | 6750 | d |  | 0.00074074 | 0.00081469 | Beta (Jeffreys, SCNID) |  | 0.00081469 | 0.5 | 613.2273 | 8.4439 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.0031322 | 0.00037094 | 2007-02-01
|  | Sensor/Transmitter (Level) Fail to Operate | RPS SSs | 0.5 | 9831968 | 9831968 | h |  | 5.0855e-08 | 1.0171e-07 | Gamma (Jeffreys, SCNID) |  | 1.0171e-07 | 0.5 | 4915984 | 8.4439 |  |  | 3.9071e-07 | 4.6271e-08 | 2007-02-01
| STP FTOP | Sensor/Transmitter (Pressure) Fail to Operate | RPS SSs | 2.3 | 23960 | 23960 | d |  | 9.5993e-05 | 0.00011686 | Beta (Jeffreys, SCNID) |  | 0.00011686 | 0.5 | 4278.25 | 8.4439 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.00044895 | 5.3169e-05 | 2007-02-01
|  | Sensor/Transmitter (Pressure) Fail to Operate | RPS SSs | 35.2 | 43430451 | 43430451 | h |  | 8.1049e-07 | 8.22e-07 | Gamma (Jeffreys, SCNID) |  | 8.22e-07 | 0.5 | 608269.6218 | 8.4439 |  |  | 3.1577e-06 | 3.7396e-07 | 2007-02-01
| STT FTOP | Sensor/Transmitter (Temperature) Fail to Operate | RPS SSs | 17.1 | 40759 | 40759 | d |  | 0.00041954 | 0.0004318 | Beta (Jeffreys, SCNID) |  | 0.0004318 | 0.5 | 1157.4545 | 8.4439 | Both the beta distribution and the gamma distribution must be used (added). For the RPS, the time-related failures are typically annunciated (or noticed) in the control room, so the detection time and repair time are short (assumed to be 12 hours in the studies). |  | 0.0016594 | 0.00019652 | 2007-02-01
|  | Sensor/Transmitter (Temperature) Fail to Operate | RPS SSs | 29 | 35107399 | 35107399 | h |  | 8.2604e-07 | 8.4028e-07 | Gamma (Jeffreys, SCNID) |  | 8.4028e-07 | 0.5 | 595040.661 | 8.4439 |  |  | 3.2279e-06 | 3.8227e-07 | 2007-02-01
Control Rods | CRD FTOP | Control Rod Drive Fail to Operate | EPIX | 13 | 136286592 h | 136286592 | h |  | 9.5387e-08 | 9.9056e-08 | Gamma | JNID/IL | 9.91e-08 | 13.5 | 136286592 | 1.4834 |  |  | 1.4717e-07 | 9.6621e-08 | 2012-02-01 | 0.021 | Significant
| CRD SOP | Control Rod Drive (CRD) Spurious Operation | EPIX | 26 | 136286592 h | 136286592 | h | 1196 | 1.9077e-07 | 1.9444e-07 | Gamma | JNID/IL | 1.94e-07 | 26.5 | 136286592 | 1.3402 |  |  | 2.6046e-07 | 1.92e-07 | 2012-02-01 | 0.8287
| HCU FTI | Hydraulic Control Unit (HCU) Fail to Insert | EPIX | 2 | 269552 | 269552 | d | 370 | 7.4197e-06 | 9.2746e-06 | Beta | JNID/IL | 9.27e-06 | 2.5 | 269550.9 | 2.2114 | [5 empty] | 0.1156
| HCU FTOP | Hydraulic Control Unit (HCU) Fail to Operate | EPIX | 22 | 747292641 h | 747292641 | h | 6558 | 2.944e-08 | 3.0109e-08 | Gamma | EB/PL/KS | 3.275e-08 | 0.6325 | 19310000 | 3.5298 | [5 empty] | 0.0028 | High
| HCU SOP | Hydraulic Control Unit (HCU) Spurious Operation | EPIX | 14 | 747292641 h | 747292641 | h | 6558 | 1.8734e-08 | 1.9403e-08 | Gamma | JNID/IL | 1.94e-08 | 14.5 | 747292641 | 1.4691 | [5 empty] | 0.4679
| ROD FTOP | Control Rod (ROD) Fail to Operate | EPIX | 28 | 95605727 h | 95605727 | h | 839 | 2.9287e-07 | 2.981e-07 | Gamma | JNID/IL | 2.98e-07 | 28.5 | 95605727 | 1.3289 |  |  | 3.955e-07 | 2.9462e-07 |  | 0.6208
| ROD SOP | Control Rod (ROD) Spurious Operation | EPIX | 18 | 95605727 h | 95605727 | h | 839 | 1.8827e-07 | 1.935e-07 | Gamma | JNID/IL | 1.94e-07 | 18.5 | 95605727 | 1.4072 |  |  | 2.7296e-07 | 1.9003e-07 |  | 0.0764
Heating & Ventilation | AHU FTR | Air Handling Unit (AHU) Fail to Run | EPIX | 52 | 12998080 h | 12998080 | h | 142 | 4.0006e-06 | 4.0391e-06 | Gamma | EB/PL/KS | 5.612e-06 | 0.774 | 137900 | 3.2823 |  |  | 1.8425e-05 | 3.4573e-06 | 2012-02-01 | 0.602
| AHU FTS | Air Handling Unit (AHU) Fail to Start | EPIX | 44 | 12566 | 12566 | d | 142 | 0.0035015 | 0.0035413 | Beta | EB/PL/KS | 0.00386 | 0.4609 | 118.9 | 3.9482 |  |  | 0.015245 | 0.0016371 | 2012-02-01 | 0.5945
| AHU SBY FTR>1H | Air Handling Unit (Standby) Fail to Run After First Hour of Operation | EPIX | 0 | 131445 | 131445 | h | 175 | 0 | 3.8039e-06 | Gamma |  | 3.8039e-06 | 0.5 | 131445 | 8.4439 |  |  | 1.4612e-05 | 1.7305e-06 | 2012-02-01 | 0.0718
| AHU SBY FTR≤1H | Air Handling Unit (Standby) Fail to Run During First Hour of Operation | EPIX | 4 | 6965 | 6965 | h | 56 | 0.0005743 | 0.00064609 | Gamma |  | 0.00228 | 0.3 | 131.5789 | 18.7656 |  |  | 0.01043 | 0.0005558 | 2012-02-01
| AHU SBY FTS | Air Handling Unit (Standby) Fail to Start | EPIX | 10 | 22251 | 22251 | d | 231 | 0.00044942 | 0.00047187 | Beta |  | 0.000829 | 0.36 | 433.8981 | 13.5006 |  |  | 0.00357 | 0.00026443 | 2012-02-01 | 0.2248
| AOD FTO/C | Air Damper (DMP) Fail to Open/Close | EPIX | 10 | 28725 | 28725 | d | 126 | 0.00034813 | 0.00036552 | Beta | JNID/IL | 0.000366 | 10.5 | 28715.91 | 1.5546 |  |  | 0.0005686 | 0.00035399 | 2012-02-01 | 0.4666
| AOD SOP | Air Damper (DMP) Spurious Operation | EPIX | 1 | 20625312 h | 20625312 | h | 181 | 4.8484e-08 | 7.2726e-08 | Gamma | JNID/IL | 7.27e-08 | 1.5 | 20625312 | 2.5997 |  |  | 1.8945e-07 | 5.7356e-08 | 2012-02-01 | 0.7912
| CHL FTR | Chiller (CHL) Fail to Run | EPIX | 180 | 5913615 h | 5913615 | h | 131 | 3.0438e-05 | 3.0523e-05 | Gamma | JNID/IL | 3.05e-05 | 180.5 | 5913615.28 | 1.1279 |  |  | 3.4353e-05 | 3.0466e-05 | 2012-02-01 | 0.0022 | High
| CHL FTS | Chiller (CHL) Fail to Start | EPIX | 84 | 19071 | 19071 | d | 135 | 0.0044046 | 0.0044306 | Beta | EB/PL/KS | 0.01301 | 0.5813 | 44.08 | 3.6188 |  |  | 0.04708 | 0.0067896 | 2012-02-01 | 0.096
| FAN FTR | Fan (FAN) Fail to Run | EPIX | 59 | 12619800 h | 12619800 | h | 219 | 4.6752e-06 | 4.7148e-06 | Gamma | EB/PL/KS | 5.875e-06 | 0.5298 | 90190 | 3.7617 |  |  | 2.2104e-05 | 2.8084e-06 | 2012-02-01 | 0.074
| FAN FTS | Fan (FAN) Fail to Start | EPIX | 42 | 59920 | 59920 | d | 219 | 0.00070093 | 0.00070927 | Beta | JNID/IL | 0.000709 | 42.5 | 59878.55 | 1.2652 |  |  | 0.00089712 | 0.00070372 | 2012-02-01 | 0.7806
| FAN SBY FTR>1H | Fan (FAN) Standby Fail to Run greater than 1 hour | EPIX | 4 | 99174 h | 99174 | h | 127 | 4.0333e-05 | 4.5375e-05 | Gamma | JNID/IL | 4.54e-05 | 4.5 | 99173.94 | 1.8789 |  |  | 8.53e-05 | 4.2062e-05 | 2012-02-01 | 0.8464
| FAN SBY FTR≤1H | Fan (FAN) Standby Fail to Run less than or equal to 1 hour | EPIX | 33 | 31278 h | 31278 | h | 127 | 0.0010551 | 0.001071 | Gamma | JNID/IL | 0.00107 | 33.5 | 31245.42 | 1.2991 |  |  | 0.0013939 | 0.0010615 | 2012-02-01 | 0.4629
| FAN SBY FTS | Fan (FAN) Fail to Start | EPIX | 34 | 40959 | 40959 | d | 127 | 0.0008301 | 0.00084229 | Beta | JNID/IL | 0.000842 | 34.5 | 40925.9 | 1.2945 |  |  | 0.0010911 | 0.00083417 | 2012-02-01 | 0.0168 | Significant
| HOD FTO/C | Air Damper (DMP) Fail to Open/Close | EPIX | 20 | 35320 | 35320 | d | 95 | 0.00056625 | 0.00058039 | Beta | JNID/IL | 0.00058 | 20.5 | 35300.54 | 1.3897 |  |  | 0.00080599 | 0.00057099 | 2012-02-01 | 0.6715
| HOD ILS | Air Damper (DMP) Internal Leak Small | EPIX | 0 | 13902144 h | 13902144 | h | 122 | 0 | 3.5966e-08 | Gamma | JNID/IL | 3.6e-08 | 0.5 | 13902144 | 3.8333 | [5 empty] | 1
| HOD SOP | Air Damper (DMP) Spurious Operation | EPIX | 8 | 13902144 h | 13902144 | h | 122 | 5.7545e-07 | 6.1142e-07 | Gamma | JNID/IL | 6.11e-07 | 8.5 | 13902144 | 1.6236 |  |  | 9.9219e-07 | 5.8761e-07 | 2012-02-01 | 0.2517
| MOD FTO/C | Air Damper (DMP) Fail to Open/Close | EPIX | 7 | 28537 | 28537 | d | 64 | 0.0002453 | 0.00026281 | Beta | EB/PL/KS | 0.000233 | 1.546 | 6634 | 2.5785 |  |  | 0.00060076 | 0.00018515 | 2012-02-01 | 0.3878
| MOD ILS | Air Damper (DMP) Internal Leak Small | EPIX | 1 | 10825440 h | 10825440 | h | 95 | 9.2375e-08 | 1.3856e-07 | Gamma | JNID/IL | 1.39e-07 | 1.5 | 10825440 | 2.5971 | [5 empty] | 1
| MOD SOP | Air Damper (DMP) Spurious Operation | EPIX | 0 | 10825440 h | 10825440 | h | 95 | 0 | 4.6187e-08 | Gamma | JNID/IL | 4.62e-08 | 0.5 | 10825440 | 3.8312 |  |  | 1.7743e-07 | 2.1012e-08 | 2012-02-01 | 1
Miscellaneous Equipment | ACC ELS | Accumulator (ACC) External Leak Small | EPIX | 8 | 76505917 h | 76505917 | h | 675 | 1.0457e-07 | 1.111e-07 | Gamma | JNID/IL | 1.11e-07 | 8.5 | 76505917 | 1.6216 |  |  | 1.8029e-07 | 1.0678e-07 | 2012-02-01 | 0.768
| ACC ELL | Air Accumulator External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 7.77e-09 | 0.3 | 38610038.61 | 18.7656 | Small leak times 0.07 |  | 3.5544e-08 | 1.8941e-09 | 2007-02-01
| ADU FTOP | Air Dryer Unit Fail to Operate | WSRC |  |  |  | h |  |  | 5e-06 | Gamma (WSRC, LL) |  | 5e-06 | 0.3 | 60000 | 18.7653 |  |  | 2.2872e-05 | 1.2189e-06 | 2007-02-01
| CTF FTR | Cooling Tower Fan (CTF) Fail to Run | EPIX | 2 | 1086740 h | 1086740 | h | 20 | 1.8404e-06 | 2.3005e-06 | Gamma | JNID/IL | 2.3e-06 | 2.5 | 1086739.676 | 2.213 |  |  | 5.0934e-06 | 2.0021e-06 | 2012-02-01 | 0.0732
| CTF FTS | Cooling Tower Fan (CTF) Fail to Start | EPIX | 1 | 1941 | 1941 | d | 20 | 0.0005152 | 0.0007724 | Beta | JNID/IL | 0.000773 | 1.5 | 1940.14 | 2.6003 |  |  | 0.0020117 | 0.00060948 | 2012-02-01 | 0.7918
| CTF SBY FTR>1H | Cooling Tower Fan (CTF) Standby Fail to Run greater than 1 hour | EPIX | 9 | 334665 h | 334665 | h | 46 | 2.6893e-05 | 2.8387e-05 | Gamma | JNID/IL | 2.84e-05 | 9.5 | 334664.801 | 1.5845 |  |  | 4.5035e-05 | 2.7397e-05 | 2012-02-01 | 0.1108
| CTF SBY FTR≤1H | Cooling Tower Fan (CTF) Standby Fail to Run less than or equal to 1 hour | EPIX | 9 | 334665 h | 334665 | h | 46 | 2.6893e-05 | 2.8387e-05 | Gamma | JNID/IL | 2.84e-05 | 9.5 | 334664.801 | 1.5845 |  |  | 4.5035e-05 | 2.7397e-05 | 2012-02-01 | 0.1106
| CTF SBY FTS | Cooling Tower Fan (CTF) Fail to Start | EPIX | 18 | 23885 | 23885 | d | 46 | 0.00075361 | 0.00077451 | Beta | EB/PL/KS | 0.003544 | 0.578 | 162.5 | 3.6428 |  |  | 0.012905 | 0.0018218 | 2012-02-01 | 0.017 | Significant
| EDC FTR | Engine-driven Air Compressor (EDC) Fail to Run | EPIX | 15 | 5687 h | 5687 | h | 5 | 0.0026376 | 0.0027255 | Gamma | EB/PL/KS | 0.003777 | 0.6332 | 167.6 | 3.5293 |  |  | 0.013259 | 0.0020636 | 2012-02-01 | 0.2853
| EDC FTS | Engine-driven Air Compressor (EDC) Fail to Start | EPIX | 2 | 1019 | 1019 | d | 5 | 0.0019627 | 0.002451 | Beta | JNID/IL | 0.00245 | 2.5 | 1017.03 | 2.2122 |  |  | 0.0054238 | 0.0021354 | 2012-02-01 | 0.9058
| HTX CCW/RHR LOHT | Heat Exchanger (HTX) Loss of Heat Transfer | EPIX | 16 | 31564654 h | 31564654 | h | 277 | 5.069e-07 | 5.2274e-07 | Gamma | JNID/IL | 5.23e-07 | 16.5 | 31564654 | 1.4359 | Data limited to CCW and RHR systems |  | 7.5084e-07 | 5.1222e-07 | 2012-02-01
| HTX SHELL ELS | Heat Exchanger (HTX) External Leak Small | EPIX | 60 | 222547790 h | 222547790 | h | 1953 | 2.6961e-07 | 2.7185e-07 | Gamma | EB/PL/KS | 3.343e-07 | 0.6159 | 1842000 | 3.5657 |  |  | 1.1919e-06 | 1.792e-07 | 2012-02-01
| HTX SHELL ELL | Heat Exchanger Shell External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 2.3401e-08 | 0.3 | 12819964.9588 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.0705e-07 | 5.7045e-09 | 2007-02-01
| HTX TUBE ELL | Heat Exchanger (HTX) Loss of Heat Transfer | EPIX | 82 | 222547790 h | 222547790 | h | 1953 | 3.6846e-07 | 3.7071e-07 | Gamma | EB/PL/KS | 4.565e-07 | 0.5341 | 1170000 | 3.7525 | > 50 gpm. Small leak times 0.15. |  | 1.7128e-06 | 2.197e-07 | 2012-02-01
| HTX TUBE ELS | Heat Exchanger (HTX) Internal Leak Small | EPIX | 78 | 222547790 h | 222547790 | h | 1953 | 3.5049e-07 | 3.5273e-07 | Gamma | EB/PL/KS | 3.79e-07 | 0.4295 | 1133000 | 4.0528 |  |  | 1.5366e-06 | 1.4878e-07 | 2012-02-01
| MDC FTR | Air Compressor (CMP) Fail to Run | EPIX | 389 | 5540316 h | 5540316 | h | 128 | 7.0213e-05 | 7.0303e-05 | Gamma | EB/PL/KS | 8.497e-05 | 2.003 | 23570 | 2.3702 |  |  | 0.00020147 | 7.1333e-05 | 2012-02-01 | 0.0061 | High
| MDC FTS | Air Compressor (CMP) Fail to Start | EPIX | 152 | 24466 | 24466 | d | 128 | 0.0062127 | 0.0062329 | Beta | EB/PL/KS | 0.01709 | 0.5864 | 33.72 | 3.5986 |  |  | 0.061508 | 0.0090138 | 2012-02-01 | 0.0097 | High
| MDC SBY FTR>1H |  | EPIX | 17.9 |  | 10999 | h | 28 | 0.0016274 | 0.0016729 | Gamma (EB/PL/KS, EB/PL/KS) |  | 0.00262 | 1.696 | 647.3282 | 3.0743 |  |  | 0.0065282 | 0.0021235 | 2007-02-01
| MDC SBY FTR≤1H |  | EPIX | 3 |  | 939 | h | 5 | 0.0031949 | 0.0037274 | Gamma (EB/PL/KS, LL) |  | 0.00314 | 0.3 | 95.5414 | 18.6381 |  |  | 0.014313 | 0.00076795 | 2007-02-01
| MDC SBY FTS |  | EPIX | 15 |  | 2150 | d | 33 | 0.0069767 | 0.007206 | Beta (EB/PL/KS, EB/PL/KS) |  | 0.00713 | 0.476 | 66.2842 | 8.876 |  |  | 0.02779 | 0.003131 | 2007-02-01
| ORF PG | Orifice Plug | WSRC |  |  |  | h |  |  | 1e-06 | Gamma(WSRC, LL) |  | 1e-06 | 0.3 | 300000 | 18.7656 |  |  | 4.5745e-06 | 2.4377e-07 | 2007-02-01
| PIPE OTHER ELS | Piping Non-Service Water System External Leak Small | EPIX | 3.5 | 15830000000 | 15830000000 | h |  | 2.211e-10 | 2.5268e-10 | Gamma (Jeffreys, SCNID) |  | 2.5268e-10 | 0.5 | 1978750000 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. Leakage rate is per hour per foot. |  | 9.7068e-10 | 1.1496e-10 | 2007-02-01
| PIPE OTHER ELL | Piping Non-Service Water System External Leak Large | EPIX |  |  |  | h-ft |  |  |  | Gamma (ELS*0.1, LL) |  | 2.5268e-11 | 0.3 | 11872500000 | 18.7656 | > 50 gpm. Small leak times 0.1. Leakage rate is per hour per foot. |  | 1.1559e-10 | 6.1597e-12 | 2007-02-01
| PIPE SWS ELS | Piping Service Water System External Leak Small | EPIX | 8.5 | 13060000000 | 13060000000 | h |  | 6.5084e-10 | 6.8913e-10 | Gamma (Jeffreys, SCNID) |  | 6.8913e-10 | 0.5 | 725555555.5556 | 8.4439 | 1 to 50 gpm. 1997 - 2004 data. Leakage rate is per hour per foot. |  | 2.6473e-09 | 3.1351e-10 | 2007-02-01
| PIPE SWS ELL | Piping Service Water System External Leak Large | EPIX |  |  |  | h-ft |  |  |  | Gamma (ELS*0.2, LL) |  | 1.3783e-10 | 0.3 | 2176666666.6667 | 18.7656 | > 50 gpm. Small leak times 0.2. Leakage rate is per hour per foot. |  | 6.3048e-10 | 3.3598e-11 | 2007-02-01
| TNK PRES ELS | Tank (TNK) External Leak Small | EPIX | 6 | 19941600 h | 19941600 | h | 175 | 3.0088e-07 | 3.2595e-07 | Gamma | JNID/IL | 3.26e-07 | 6.5 | 19941600 | 1.7209 |  |  | 5.6069e-07 | 3.094e-07 | 2012-02-01
| TNK PRES ELL | Tank Unpressurized External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 2.282e-08 | 0.3 | 13146362.8396 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 1.0439e-07 | 5.5628e-09 | 2007-02-01
| TNK UNPR ELS | Tank (TNK) External Leak Small | EPIX | 6 | 24955440 h | 24955440 | h | 219 | 2.4043e-07 | 2.6046e-07 | Gamma | JNID/IL | 2.6e-07 | 6.5 | 24955440 | 1.7231 |  |  | 4.4804e-07 | 2.4724e-07 | 2012-02-01
| TNK UNPR ELL | Tank Unpressurized External Leak Large | EPIX |  |  |  | h |  |  |  | Gamma (ELS*0.07, LL) |  | 1.82e-08 | 0.3 | 16483516.4835 | 18.7656 | > 50 gpm. Small leak times 0.07. |  | 8.3256e-08 | 4.4366e-09 | 2007-02-01
Acronyms - BWR (boiling water reactor), EB/PL/KS (empirical Bayes/plant level/Kass Steffey), EPIX (Equipment Performance and Information Exchange), JNID/IL (Jeffreys noninformative distribution/industry level), LL (lower limit), PLL (process logic level), PWR (pressurized water reactor), SCNID (simplified constrained noninformative distribution), SS (system study), SWS (service water system), WSRC (Westinghouse Savannah River Company)
Note a - The Jeffreys mean is obtained from a Bayesian update of the Jeffreys noninformative prior. For demand-related events, the mean is (n + 0.5)/(D + 1), where n is the number of failures and D is the number of demands. For time-related failures, the mean is (n + 0.5)/T, where T is the number of hours.
Note b - The error factor is from an empirical Bayes analysis at the plant level, with Kass-Steffey adjustment. The error factor is the 95th percentile divided by the median.
Note b - The format for the distributions is the following: distibution type (source for mean, source for α factor)

## IEs
|  |  | SPAR Initiating Event Data and Results |  |  |  |  | Hidden Columns
2010 Paramater Estimation Update
|  |  | Initiating Event | Description | Data Source | Data | [10 empty] | Industry-average Frequency Distribution (note a) |  |  |  |  | Comments (see Appendix D for details) | Baseline Period | Effective Date
[6 empty] | Number of Events | Critical Years (rcry) | MLE | Jeffreys Mean (note a) | EB Mean | α Factor | Error Factor (note b) | Data Source | Comments | Median | 0.95 | Distribution (note b) | Mean | α | β | Error Factor
PRIMARY / SECONDARY INVENTORY CONTROL and/or HEAT REMOVAL | High Energy Line Breaks
|  |  | IE-FWLB (BWR) | Feedwater Line Break (BWR) | IEDB | 0 | 672.874 | 0 | [8 empty] | Gamma | 0.000743 | 0.5 | 672.874 | 8.432 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-FWLB (PWR) | Feedwater Line Break (PWR) | IEDB | 2 | 1362.787 | 0.0014676 | [8 empty] | Gamma | 0.00183 | 2.5 | 1362.787 | 2.5375 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-SLBIC (PWR) | Steamline Break Inside Containment (PWR) | IEDB | 0 | 1362.787 | 0 | [8 empty] | Gamma | 0.000367 | 0.5 | 1362.787 | 8.4431 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-SLBOC (BWR) | Steamline Break Outside Containment (BWR) | IEDB | 2 | 672.874 | 0.0029723 | [8 empty] | Gamma | 0.00372 | 2.5 | 672.874 | 2.548 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-SLBOC (PWR) | Steamline Break Outside Containment (PWR) | IEDB | 10 | 1362.787 | 0.0073379 | [8 empty] | Gamma | 0.0077 | 10.5 | 1362.787 | 1.6086 |  | 1988 - 2010 | 2012-02-01
| Steam Generator Tube Rupture | [22 empty] | 2012-02-01
|  |  | IE-SGTR (PWR) | Steam Generator Tube Rupture (PWR) | IEDB | 2 | 1805.624 | 0.0011077 | 0.0013846 |  |  |  | LERs (1991 - 2002) | EB degenerate |  |  | Gamma | 0.00138 | 2.5 | 1805.624 | 2.5372 |  | 1991 - 2010 | 2012-02-01
| Loss of Coolant Accidents | [22 empty] | 2012-02-01
|  |  | IE-LLOCA (BWR) | Large Loss-of-Coolant Accident (BWR) | NUREG-1829 | [11 empty] | Gamma (EE, EE) | 6.78e-06 | 0.47 | 69321.5339 | 9.1372 |  |  | 2012-02-01
|  |  | IE-LLOCA (PWR) | Large Loss-of-Coolant Accident (PWR) | NUREG-1829 | [11 empty] | Gamma (EE, EE) | 1.33e-06 | 0.42 | 315789.4737 | 10.6625 |  |  | 2012-02-01
|  |  | IE-MLOCA (BWR) | Medium Loss-of-Coolant Accident (BWR) | NUREG-1829 | [11 empty] | Gamma (EE, EE) | 0.000104 | 0.61 | 5865.3846 | 6.719 |  |  | 2012-02-01
|  |  | IE-MLOCA (PWR) | Medium Loss-of-Coolant Accident (PWR) | NUREG-1829 | [11 empty] | Gamma (EE, EE) | 0.00051 | 0.44 | 862.7451 | 9.985 |  |  | 2012-02-01
|  |  | IE-SLOCA (BWR) | Small Loss-of-Coolant Accident (BWR) | IEDB | 0 | 672.874 | 0 | [8 empty] | Gamma | 0.0005 | 0.78 | 1560 | 8.432 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-SLOCA (PWR) | Small Loss-of-Coolant Accident (PWR) | IEDB | 0 | 1362.787 | 0 | 0.0003669 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.000367 | 0.5 | 1362.787 | 5.3 | No failures, but there were events in the early 1980s (RCP seal LOCAs) | 1988 - 2010 | 2012-02-01
|  |  | IE-VSLOCA (BWR) | Very Small Loss-of-Coolant Accident (BWR) | IEDB | 2 | 574.048 | 0.003484 | [8 empty] | Gamma | 0.00436 | 2.5 | 574.048 | 2.5435 |  | 1992 - 2010 | 2012-02-01
|  |  | IE-VSLOCA (PWR) | Very Small Loss-of-Coolant Accident (PWR) | IEDB | 0 | 1148.306 | 0 | 0.00043542 |  |  |  | LERs (1992 - 2002) | EB degenerate |  |  | Gamma | 0.000435 | 0.5 | 1148.306 | 8.4343 |  | 1992 - 2010 | 2012-02-01
|  |  | IE-SORV1 (BWR) | Stuck Open Safety/Relief Valve-1 (BWR) | IEDB | 9 | 548.825 | 0.016399 | 0.01731 |  |  |  | LERs (1993 - 2002) | EB degenerate |  |  | Gamma | 0.01634 | 0.9117 | 55.79 | 4.6413 |  | 1993 - 2010 | 2012-02-01
|  |  | IE-SORV1 (PWR) | Stuck Open Safety/Relief Valve-1 (PWR) | IEDB | 2 | 1362.787 | 0.0014676 | 0.0018345 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.00183 | 2.5 | 1362.787 | 2.5375 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-SORV2 (BWR) | Stuck Open Safety/Relief Valves-2 (BWR) | IEDB | 0 | 548.825 | 0 | [8 empty] | Gamma | 0.000911 | 0.5 | 548.825 | 8.4541 |  | 1993 - 2010 | 2012-02-01
|  |  | IE-SORV2 (PWR) | Stuck Open Safety/Relief Valves-2 (PWR) | IEDB | 0 | 1362.787 | 0 | [8 empty] | Gamma | 0.000367 | 0.5 | 1362.787 | 8.4431 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-ISLOCA (BWR) | Interfacing System LOCA (BWR) | IEDB | 0 | 672.874 | 0 | [8 empty] | Gamma | 0.000743 | 0.5 | 672.874 | 8.432 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-ISLOCA (PWR) | Interfacing System LOCA (PWR) | IEDB | 0 | 1362.787 | 0 | [8 empty] | Gamma | 0.000367 | 0.5 | 1362.787 | 8.4431 |  | 1988 - 2010 | 2012-02-01
TRANSIENTS | Loss of Feedwater | [22 empty] | 2012-02-01
|  |  | IE-LOMFW | Loss of Main Feedwater | IEDB | 113 | 1638.768 | 0.068954 | 0.069259 | 0.0959 | 1.839 | 2.9505 | LERs (1993 - 2002) |  |  |  | Gamma | 0.06892 | 2.22 | 32.21 | 2.6864 |  | 1993 - 2010 | 2012-02-01
| General Transients | [22 empty] | 2012-02-01
|  |  | IE-TRANS (BWR) | General Transient (BWR) | IEDB | 332 | 437.264 | 0.75927 | 0.76041 |  |  |  | LERs (1997 - 2002) | EB degenerate |  |  | Gamma | 0.7624 | 21.03 | 27.59 | 1.4061 |  | 1997 - 2010 | 2012-02-01
|  |  | IE-TRANS (PWR) | General Transient (PWR) | IEDB | 553 | 803.884 | 0.68791 | 0.68853 | 0.751 | 69.239 | 1.2114 | LERs (1998 - 2002) |  |  |  | Gamma | 0.6897 | 8.185 | 11.87 | 1.7042 |  | 1998 - 2010 | 2012-02-01
| Loss of Condenser Heat Sink | [22 empty] | 2012-02-01
|  |  | IE-LOCHS (BWR) | Loss of Condenser Heat Sink (BWR) | IEDB | 65 | 465.633 | 0.13959 | 0.14067 | 0.197 | 15.822 | 1.4772 | LERs (1996 - 2002) |  |  |  | Gamma | 0.1393 | 2.903 | 20.85 | 2.3867 |  | 1996 - 2010 | 2012-02-01
|  |  | IE-LOCHS (PWR) | Loss of Condenser Heat Sink (PWR) | IEDB | 57 | 974.689 | 0.05848 | 0.058993 |  |  |  | LERs (1995 - 2002) | EB degenerate |  |  | Gamma | 0.05862 | 3.741 | 63.83 | 2.163 |  | 1995 - 2010 | 2012-02-01
HEAT SINK | Loss of Support Systems | [22 empty] | 2012-02-01
|  | Loss of Cooling Water | [21 empty] | 2012-02-01
|  |  | IE-LOSWS | Loss of Service Water System | IEDB | 0 | 2035.66 | 0 | 0.00024562 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.000246 | 0.5 | 2035.66 | 8.4286 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-PLOSWS | Partial Loss of Service Water System | IEDB | 3 | 2035.66 | 0.0014737 | 0.0017193 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.00172 | 3.5 | 2035.66 | 2.2179 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-LOCCW | Loss of Component Cooling Water | IEDB | 0 | 2035.66 | 0 | 0.00024562 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.000246 | 0.5 | 2035.66 | 8.4286 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-PLOCCW | Partial Loss of Component Cooling Water | IEDB | 4 | 2035.66 | 0.001965 | 0.0022106 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.00221 | 4.5 | 2035.66 | 2.0293 |  | 1988 - 2010 | 2012-02-01
LOIA |  | Loss of Instrument Air | [21 empty] | 2012-02-01
|  |  | IE-LOIA (BWR) | Loss of Instrument Air (BWR) | IEDB | 4 | 600.403 | 0.0066622 | 0.007495 |  |  |  | LERs (1991 - 2002) | EB degenerate |  |  | Gamma | 0.00749 | 4.5 | 600.403 | 2.0288 |  | 1991 - 2010 | 2012-02-01
|  |  | IE-LOIA (PWR) | Loss of Instrument Air (PWR) | IEDB | 7 | 856.757 | 0.0081703 | 0.0087539 |  |  |  | LERs (1997 - 2002) |  |  |  | Gamma | 0.008224 | 0.3834 | 46.62 | 12.225 |  | 1997 - 2010 | 2012-02-01
ELECTRICAL POWER |  | Loss of Electrical Bus | [21 empty] | 2012-02-01
|  |  | IE-LOAC | Loss of AC Bus | IEDB | 11 | 1722.354 | 0.0063866 | 0.0066769 |  |  |  | LERs (1992 - 2002) | EB degenerate |  |  | Gamma | 0.00668 | 11.5 | 1722.354 | 1.5741 |  | 1992 - 2010 | 2012-02-01
|  |  | IE-LOAC 4160V | Loss of 4160V AC Bus | IEDB | 7 | 1722.354 | 0.0040642 | [8 empty] | Gamma | 0.00435 | 7.5 | 1722.354 | 1.7452 |  | 1992 - 2010 | 2012-02-01
|  |  | IE-LOAC LOWV | Loss of Low Voltage AC Bus | IEDB | 4 | 1722.354 | 0.0023224 | [8 empty] | Gamma | 0.00261 | 4.5 | 1722.354 | 2.0289 |  | 1992 - 2010 | 2012-02-01
|  |  | IE-LOAC-Calc | [13 empty] | Gamma | 0.00334 | 0.3 | 89.8204 | 18.7656 | Adjusted for initiation by 2-busses |  | 2012-02-01
|  |  | IE-LODC | Loss of DC Bus | IEDB | 1 | 2035.66 | 0.00049124 | 0.00073686 |  |  |  | LERs (1988 - 2002) | EB degenerate |  |  | Gamma | 0.000737 | 1.5 | 2035.66 | 3.3046 |  | 1988 - 2010 | 2012-02-01
|  |  | IE-LODC-Calc | [13 empty] | Gamma | 0.0003685 | 0.3 | 814.1113 | 18.7656 | Adjusted for initiation by 2-busses |  | 2012-02-01
| Loss of Offsite Power | [22 empty] | 2012-02-01
|  | Critical Operation | [21 empty] | 2012-02-01
|  |  | IE-LOOP | Loss of Offsite Power | IEDB | 37 | 1421.4 | 0.026031 | 0.19896 |  | 1.58 | 3.2053 | LERS (1997 - 2004) |  | 0.0211 | 0.0623 | Gamma | 0.061423 | 1.58 | 25.7232 | 2.9526 |  |  | 2012-02-01
|  |  | IE-LOOPGR | Grid Related Contribution to LOOP | IEDB | 14 | 1294 | 0.010819 | 0.011206 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | 0.00437 | 0.0509 | Gamma | 0.0122 | 0.4 | 32.4 | 11.6476 |  | 1997–2010 | 2012-02-01
|  |  | IE-LOOPPC | Plant Centered Contribution to LOOP | IEDB | 2 | 1294 | 0.0015456 | 0.001932 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | 0.00168 | 0.00428 | Gamma | 0.00193 | 2.5 | 1294 | 2.5476 |  | 1997–2010 | 2012-02-01
|  |  | IE-LOOPSC | Switchyard Centered Contribution to LOOP | IEDB | 13 | 1294 | 0.010046 | 0.010433 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | 0.0102 | 0.0155 | Gamma | 0.0104 | 13.5 | 1294 | 1.5196 |  | 1997–2010 | 2012-02-01
|  |  | IE-LOOPWR | Weather Related Contribution to LOOP | IEDB | 8 | 2171.4 | 0.0036843 | 0.0039145 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | 0.00376 | 0.00635 | Gamma | 0.00391 | 8.5 | 2171.4 | 1.6888 |  | 1986–2010 | 2012-02-01
|  | Shutdown Operation | [21 empty] | 2012-02-01
|  |  | IE-SD-LOOP | Loss of Offsite Power | IEDB | 54 | 316.6 | [7 empty] | 0.149 | 0.328 | Gamma | 0.169 | 4.21 | 24.91 | 2.2013 |  |  | 2012-02-01
|  |  | IE-SD-LOOPGR | Grid Related Contribution to LOOP | IEDB | 5 | 435.9 | 0.011471 | 0.012618 | [5 empty] | 0.0119 | 0.0226 | Gamma | 0.0126 | 5.5 | 435.9 | 1.8992 |  | 1986–2010 | 2012-02-01
|  |  | IE-SD-LOOPPC | Plant Centered Contribution to LOOP | IEDB | 23 | 435.9 | 0.052764 | 0.053911 | [5 empty] | 0.0354 | 0.156 | Gamma | 0.0516 | 0.97 | 18.8 | 4.4068 |  | 1986–2010 | 2012-02-01
|  |  | IE-SD-LOOPSC | Switchyard Centered Contribution to LOOP | IEDB | 10 | 156.5 | 0.063898 | 0.067093 | [5 empty] | 0.065 | 0.104 | Gamma | 0.0671 | 10.5 | 156.5 | 1.6 |  | 1997–2010 | 2012-02-01
|  |  | IE-SD-LOOPWR | Weather Related Contribution to LOOP | IEDB | 16 | 435.9 | 0.036706 | 0.037853 |  | 0.5 | 8.4439 | LERS (1997 - 2004) | From LOOP NUREG | 0.0205 | 0.147 | Gamma | 0.0402 | 0.57 | 14.2 | 7.1707 |  | 1986–2010 | 2012-02-01
Acronyms - BWR (boiling water reactor), EB (empirical Bayes), EE (expert elicitation), IE (initiating event), IEDB (initiating events database - http://nrcoe.inl.gov), PWR (pressurized water reactor)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distibution type (source for mean, source for α factor)

## Special Events
SPAR Special Event Data and Results
2010 Paramater Estimation Update
Special Event Name | System Study Name | Description | Existing SPAR Value |  | Data Source | Data | [6 empty] | Industry-average Probability or Rate Distribution (note a) | [8 empty] | Comments (see Appendix C for details) | [5 empty] | Effective Date
|  |  | Mean | Units |  | Failures | Demands or Hours | MLE | Jeffreys Mean | Error Factor | Data Source | d or h | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Error Factor |  | Recommended Improvement | 95% | Median | 95% | Median
TDP-PRST (RCIC) | IFRS | RCIC TDP probability of restart | 0.26 | D | SS | 6 | 47 | 0.12766 | 0.13542 | ? | System Study (1996 - 2002) | d | Beta (Jeffreys, Jeffreys) | 0.13542 | 6.5 | 41.5 | 1.7163 | 0.15 | 6 | 34 | 1.7403 |  |  | 0.25085 | 0.14415 | 0.22371 | 0.13034 | 2007-02-01
TDP-FRST (RCIC) | LNRS | RCIC TDP restart failure per event | 0.24 | D | SS | 1 | 17 | 0.058824 | 0.083333 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.083333 | 0.5 | 5.5 | 7.2198 | 0.08 | 0.5 | 5.75 | 7.2698 |  |  | 0.29419 | 0.040467 | 0.30575 | 0.042348 | 2007-02-01
TDP-FRFRST (RCIC) | FRFTRS | RCIC failure to recover TDP restart failure | 0.5 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01 |  | Mean | Alpha | Beta | 5% | 50% | 95%
MOV-PMINJ (RCIC) | PMI | RCIC injection valve probability of multiple injections | ? | D | SS | 14 | 28 | 0.5 | 0.5 | ? | System Study (1998 - 2002) | d | Beta (EB/YL/KS, EB/YL/KS) | 0.503 | 4.18 | 4.1301 | 1.5354 | 0.5 | 4 | 4 | 1.5494 |  |  | 0.77468 | 0.5 | 0.77267 | 0.50325 | 2007-02-01 | Beta | 0.0012 | 0.9 | 749.1 | 4.667e-05 | 0.00079635 | 0.0037297
MOV-FTRO (RCIC) | FRO | RCIC injection valve fails to reopen | ? | D | SS | 1 | 38 | 0.026316 | 0.038462 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.038462 | 0.5 | 12.5 | 7.8865 | 0.04 | 0.5 | 12 | 7.8639 |  |  | 0.15073 | 0.019168 | 0.14506 | 0.018393 | 2007-02-01 | Gamma | 0.02 | 6 | 300 | 0.00871 | 0.018901 | 0.035043
MOV-FRFTRO (RCIC) | FRFRO | RCIC failure to recover injection valve failure to reopen | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFRI (RCIC) | LNRC | RCIC failure to transfer back to injection mode (pump recirculation valve) | 0.034 | D | SS | 1 | 197.95 | 0.0050518 | 0.0075777 | ? | System Study (1988 - 2002) | h | Gamma (Jeffreys, SCNID) | 0.0075777 | 0.5 | 65.9833 | 8.4439 | 0.008 | 0.5 | 62 | 8.4439 | Note that this is per hour. Failure occurred 8 min after RCIC initiation. |  | 119.0852 | 14.103 | 126.7361 | 15.0091 | 2007-02-01
SUC-FRFTFR (RCIC) | FRFTRC | RCIC failure to recover transfer failure | 0.17 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (HPCI) | PMI | HPCI injection valve probability of multiple injections | 0.13 | D | SS | 2 | 17 | 0.11765 | 0.13889 | ? | System Study (1995 - 2002) | d | Beta (Jeffreys, SCNID) | 0.13889 | 0.5 | 3.1 | 6.38 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.48738 | 0.076392 | 2007-02-01
MOV-FTRO (HPCI) | FRO | HPCI injection valve fails to reopen | 0.192 | D | SS | 1 | 8 | 0.125 | 0.16667 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.16667 | 0.5 | 2.5 | 5.9592 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.56926 | 0.095526 | 2007-02-01
MOV-FRFTRO (HPCI) | FRFRO | HPCI failure to recover injection valve failure to reopen | 0.833 | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFR (HPCI) | FTRT | HPCI failure to transfer | ? | D | SS | 0 | 1270 | 0 | 0.00039339 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.00039339 | 0.5 | 1270.5 | 8.4383 | 0.0004 | 0.5 | 1249.5 | 8.4382 |  |  | 0.0015363 | 0.00018207 | 0.0015109 | 0.00017906 | 2007-02-01
SUC-FRFTFR (HPCI) | FRFTRT | HPCI failure to recover transfer failure | ? | D | SS | 0 | 0 | #DIV/0! | 0.5 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.5 | 0.5 | 0.5 | 1.9877 | 0.5 | 0.5 | 0.5 | 1.9877 |  |  | 0.99384 | 0.5 | 0.99384 | 0.5 | 2007-02-01
SUC-FTFR (HPCS) | FTRT | HPCS failure to transfer | ? | D | SS | 1 | 478 | 0.0020921 | 0.0031315 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.0031315 | 0.5 | 159.1667 | 8.3991 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.012014 | 0.0014303 | 2007-02-01
SUC-FRFTFR (HPCS) | FRFTRT | HPCS failure to recover transfer failure | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
Acronyms - EB (empirical Bayes), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), KS (Kass-Steffey), MOV (motor-operated valve), RCIC (reactor core isolation cooling), SCNID (simplified constrained noninformative distribution), SUC (suction), SS (updated system study), TDP (turbine-driven pump), YL (year level)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distribution type (source for mean, source for α factor).
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β factor is determined from mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution.

## Train UA
SPAR Basic Event Unavailability Data and Results
2010 Paramater Estimation Update
Train Unavailability Event | Train Description | Data Source | Industry-average Probability Distribution (note a) |  |  |  |  | Effective Date
|  |  | Distribution | Mean | α | β | Error Factor
ZT-DGN-TM | Diesel Generator Test And Maintenance | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.014354 | 3.7092 | 254.6928 | 2.1529 | 2012-02-01
ZT-EDP-TM | Engine Driven Pump Test And Maintenance | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.00719 | 44.2199 | 6105.9731 | 1.2679 | 2012-02-01
ZT-EDP-TM(FWS) | EDP-TM(FWS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.031809 | 13.742 | 418.2729 | 1.5055 | 2012-02-01
ZT-HTX-CCW-TM | Heat Exchanger Test Or Maintenance (CCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0085409 | 1 | 116.0837 | 4.2794 | 2012-02-01
ZT-HTX-TRAIN-BWR-RHR-TM | Heat Exchanger And Pump Train Test Or Maintenance (RHR-BWR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.002355 | 2.0025 | 848.295 | 2.8197 | 2012-02-01
ZT-MDP-TM(SDC) | Motor Driven Pump Test And Maintenance (SDC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.002355 | 2.0025 | 848.295 | 2.8197 | 2012-02-01
ZT-HTX-TRAIN-PWR-RHR-TM | Heat Exchanger And Pump Train Test Or Maintenance (RHR-BWR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.00012 | 2.9383 | 24482.9188 | 2.3743 | 2012-02-01
ZT-MDP-TM(AFW) | Motor Driven Pump Test And Maintenance (AFW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.003976 | 4.0344 | 1010.6676 | 2.1009 | 2012-02-01
ZT-MDP-TM(BCW) | Motor Driven Pump Test And Maintenance (BCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CCS) | Motor Driven Pump Test And Maintenance (CCS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CDS) | Motor Driven Pump Test And Maintenance (CDS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CHW) | Motor Driven Pump Test And Maintenance (CHW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CMS) | Motor Driven Pump Test And Maintenance (CMS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CPC) | Motor Driven Pump Test And Maintenance (CPC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CRD) | Motor Driven Pump Test And Maintenance (CRD) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CSR) | Motor Driven Pump Test And Maintenance (CSR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CSS) | Motor Driven Pump Test And Maintenance (CSS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(CTS) | Motor Driven Pump Test And Maintenance (CTS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(DWP) | Motor Driven Pump Test And Maintenance (DWP) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(EPS) | Motor Driven Pump Test And Maintenance (EPS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(FWS) | Motor Driven Pump Test And Maintenance (FWS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(LCS) | Motor Driven Pump Test And Maintenance (LCS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(LPI) | Motor Driven Pump Test And Maintenance (LPI) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(MFW) | Motor Driven Pump Test And Maintenance (MFW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(QSS) | Motor Driven Pump Test And Maintenance (QSS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(RSS) | Motor Driven Pump Test And Maintenance (RSS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(SFW) | Motor Driven Pump Test And Maintenance (SFW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(SSM) | Motor Driven Pump Test And Maintenance (SSM) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0071243 | 1.1545 | 160.8942 | 3.8696 | 2012-02-01
ZT-MDP-TM(ACW) | Motor Driven Pump Test And Maintenance (ACW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(CCW) | Motor Driven Pump Test And Maintenance (CCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(DHC) | Motor Driven Pump Test And Maintenance (DHC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(ECW) | Motor Driven Pump Test And Maintenance (ECW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(EHV) | Motor Driven Pump Test And Maintenance (EHV) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(ESR) | Motor Driven Pump Test And Maintenance (ESR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(NSC) | Motor Driven Pump Test And Maintenance (NSC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(RBC) | Motor Driven Pump Test And Maintenance (RBC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(SAC) | Motor Driven Pump Test And Maintenance (SAC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(TBC) | Motor Driven Pump Test And Maintenance (TBC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0047901 | 1.1814 | 245.4562 | 3.8191 | 2012-02-01
ZT-MDP-TM(CWS) | Motor Driven Pump Test And Maintenance (CWS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(ESP) | Motor Driven Pump Test And Maintenance (ESP) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(ESW) | Motor Driven Pump Test And Maintenance (ESW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(EWS) | Motor-Driven Pump Test or Maintenance (ESW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(ICW) | Motor Driven Pump Test And Maintenance (ICW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(MCW) | Motor Driven Pump Test And Maintenance (MCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(NSR) | Motor Driven Pump Test And Maintenance (NSR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(RCW) | Motor Driven Pump Test And Maintenance (RCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(RWS) | Motor Driven Pump Test And Maintenance (RWS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(SCW) | Motor Driven Pump Test And Maintenance (SCW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(SRW) | Motor Driven Pump Test And Maintenance (SRW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(SSF) | Motor Driven Pump Test And Maintenance (SSF) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(SWS) | Motor Driven Pump Test And Maintenance (SWS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.013236 | 1 | 74.5515 | 4.256 | 2012-02-01
ZT-MDP-TM(HPCS) | Motor Driven Pump Test And Maintenance (HPCS) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0068188 | 11.8225 | 1721.9975 | 1.5624 | 2012-02-01
ZT-MDP-TM(CVC) | Motor Driven Pump Test And Maintenance (CVC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0038792 | 3.1323 | 804.3392 | 2.3087 | 2012-02-01
ZT-MDP-TM(HPSI) | Motor Driven Pump Test And Maintenance (HPSI) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0038792 | 3.1323 | 804.3392 | 2.3087 | 2012-02-01
ZT-MDP-TM(DHR) | Motor Driven Pump Test And Maintenance (DHR) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0053655 | 3.2742 | 606.9501 | 2.267 | 2012-02-01
ZT-TDP-TM(AFW) | Turbine Driven Pump Test Or Maintenance (AFW) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.0053945 | 3.1993 | 589.8714 | 2.2875 | 2012-02-01
ZT-TDP-TM(HPCI) | Turbine Driven Pump Test Or Maintenance (HPCI) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.011333 | 12.8379 | 1120.002 | 1.5341 | 2012-02-01
ZT-TDP-TM(RCIC) | Turbine Driven Pump Test Or Maintenance (RCIC) | 2010 Update to the Parameter Estimation Component Unavailability Data Sheets; Section 1, Table 1-1 | Beta | 0.010952 | 6.7411 | 608.7719 | 1.7865 | 2012-02-01
ZT-ACX-TM | Air Handling Unit Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.0025 | 0.5 | 199.5 | 8.4082 | 2012-02-01
ZT-BAC-TM | Bus (AC) Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.0002 | 0.5 | 2499.5 | 8.4411 | 2012-02-01
ZT-BAT-TM | Battery Test or Maintenance | Letter: Generic Test and Maintenance Unavailability Values, JCN W6467 - MBS-02-99 | Lognormal | 0.00272 | 8.4 | 0 | 8.4 | 2012-02-01
ZT-BCH-TM | Battery Charger Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.002 | 0.5 | 249.5 | 8.4153 | 2012-02-01
ZT-CCP-TM | RPS CH-A IN T&M | RPS Study NUREGs; NUREG/CR-5500, Vol 2,3,10, and 11 | Beta | 0.005 | 0.5 | 47.76 | 8.2952 | 2012-02-01
ZT-CHL-TM | Chiller Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.02 | 0.5 | 24.5 | 8.1559 | 2012-02-01
ZT-CTF-TM | Cooling Tower Fan Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.002 | 0.5 | 249.5 | 8.4153 | 2012-02-01
ZT-CTG-TM | Combustion Turbine Generator Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.05 | 0.5 | 9.5 | 7.7165 | 2012-02-01
ZT-DDC-TM | Diesel Driven Compressor Fails Due To T&M | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.013 | 0.5 | 41.1667 | 8.2716 | 2012-02-01
ZT-EDC-TM | Engine-Driven Compressor Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.012 | 0.5 | 41.1667 | 8.2716 | 2012-02-01
ZT-EPV-TM | Explosive-Operated (SQUIBB) Valve Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.0006 | 0.5 | 832.8333 | 8.4354 | 2012-02-01
ZT-FAN-TM | Fan Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.002 | 0.5 | 249.5 | 8.4153 | 2012-02-01
ZT-HTX-TM | Heat Exchanger in Test or Maintenance | SPAR (IPEs) | Beta | 0.0025 | 0.5 | 119.7 | 8.3844 | 2012-02-01
ZT-MDC-TM | Motor-Driven Compressor Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.012 | 0.5 | 41.1667 | 8.2716 | 2012-02-01
ZT-MDP-TM(SLC) | Positive Displacement Pump Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.003 | 0.5 | 166.1667 | 8.401 | 2012-02-01
ZT-PDP-TM | Positive Displacement Pump Test or Maintenance | NUREG/CR-6928 Appendix B, Section B.4 | Beta | 0.003 | 0.5 | 166.1667 | 8.401 | 2012-02-01
ZT-TFM-TM | Startup Transformer Test or Maintenance | Letter: Generic Test and Maintenance Unavailability Values, JCN W6467 - MBS-02-99 | Lognormal | 0.00175 | 8.4 | 0 | 8.4 | 2012-02-01
Acronyms - AFWS (auxiliary feedwater system), BWR (boiling water reactor), CCW (component cooling water), EPS (emergency power system), ESW (emergency or essential service water), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), IC (isolation condenser), HTX (heat exchanger), IPE (Individual Plant Examination), MDP (motor-driven pump), MSPI (Mitigating Systems Performance Index), NSW (normal service water), PWR (pressurized water reactor), RCIC (reactor core isolation cooling), RHR (residual heat removal), RHRSW (residual heat removal service water), ROP (Reactor Oversight Process), SCNID (simplified constrained noninformative distribution), SS (system study), SSU (Safety System Unavailability), SWS (service water system)