## Component Reliability
Summary of SPAR Component Unreliability Data and Results
2015 Paramater Estimation Update
2016-12-21 12:00
Grouping | Component Type | Component Failure Mode | Description | Data Source | Data |  |  |  | Industry-average Failure Probability or Rate Distribution (note a) | [8 empty] | Date Range | Comments (see Appendix A for details) | Effective Date
[5 empty] | Failures | Demands or Hours | d or h | Components | Distribution | Analysis Type | 5th | Median | Mean | 95th | α | β | Error Factor (note b)
Valves | Air-Operated Valve (AOV) | AOV-FTO | Air Operated Valve Fails To Open | EPIX/RADS | 78 | 201146.5 | d | 1767 | Beta | EB/PL/KS | 1.04e-05 | 0.000244 | 0.000391 | 0.00127 | 0.793 | 2030 | 5.2135 | 1998--2015 |  | 2016-12-20
|  | AOV-FTC | Air Operated Valve Fails To Close | EPIX/RADS | 53 | 201146.5 | d | 1767 | Beta | EB/PL/KS | 2.24e-06 | 0.000178 | 0.000363 | 0.00135 | 0.547 | 1510 | 7.5773 | 1998--2015 |  | 2016-12-20
|  | AOV-FTOC | Air Operated Valve Fails To Open | EPIX/RADS | 134 | 201146.5 | d | 1767 | Beta | EB/PL/KS | 4.49e-05 | 0.000549 | 0.000778 | 0.00229 | 1.05 | 1350 | 4.1654 | 1998--2015 |  | 2016-12-20
|  | AOV-FC | Air Operated Valve Fails To Control | EPIX/RADS | 279 | 1347257000 | h | 8784 | Gamma | EB/PL/KS | 2.41e-08 | 1.77e-07 | 2.28e-07 | 6.08e-07 | 1.41 | 6170000 | 3.4272 | 1998--2015 |  | 2016-12-20
|  | AOV-SOP | Air Operated Valve Transfers Positions | EPIX/RADS | 132 | 1347257000 | h | 8784 | Gamma | EB/PL/KS | 7.28e-09 | 7.61e-08 | 1.05e-07 | 2.99e-07 | 1.14 | 10900000 | 3.933 | 1998--2015 |  | 2016-12-20
|  | AOV-ILS | Air-Operated Valve Internal Leakage (Small) | EPIX/RADS | 104 | 1347257000 | h | 8784 | Gamma | JNID/IL | 6.57e-08 | 7.75e-08 | 7.76e-08 | 9.07e-08 | 105 | 1350000000 | 1.1695 | 1998--2015 |  | 2016-12-20
|  | AOV-ILL | Air-Operated Valve Internal Leakage (Rupture) | EPIX/RADS | 104 | 1347257000 | h | 8784 | Gamma | JNID/IL | 1.66e-13 | 3.78e-10 | 1.55e-09 | 7.1e-09 | 0.3 | 193299000 | 18.7656 | 1998--2015 | AOV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | AOV-ELS | Air-Operated Valve External Leakage (Small) | EPIX/RADS | 60 | 1347257000 | h | 8784 | Gamma | JNID/IL | 3.58e-08 | 4.46e-08 | 4.49e-08 | 5.47e-08 | 60.5 | 1350000000 | 1.2272 | 1998--2015 |  | 2016-12-20
|  | AOV-ELL | Air-Operated Valve External Leakage (Rupture) | EPIX/RADS | 60 | 1347257000 | h | 8784 | Gamma | JNID/IL | 3.36e-13 | 7.66e-10 | 3.14e-09 | 1.44e-08 | 0.3 | 95450200 | 18.7656 | 1998--2015 | AOV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | CCW-AOV-OC | CCW AOV Spuriously Transfers | EPIX/RADS | 25 | 178863300 | h | 1161 | Gamma | JNID/IL | 9.94e-08 | 1.41e-07 | 1.43e-07 | 1.92e-07 | 25.5 | 179000000 | 1.3642 | 1998--2015 |  | 2016-12-20
|  | IAS-AOV-OC | Instrument Air System AOV Spuriously Transfers | EPIX/RADS | 0 | 7056096 | h | 45 | Gamma | JNID/IL | 2.78e-10 | 3.22e-08 | 7.09e-08 | 2.72e-07 | 0.5 | 7060000 | 8.4439 | 1998--2015 |  | 2016-12-20
| Motor-Operated Valve (MOV) | MOV-FTO | Motor Operated Valve Fail To Open | EPIX/RADS | 293 | 740890.2 | d | 6902 | Beta | EB/PL/KS | 0.000117 | 0.000376 | 0.000421 | 0.000876 | 3.08 | 7320 | 2.329 | 1998--2015 |  | 2016-12-20
|  | MOV-FTC | Motor Operated Valve Fail To Close | EPIX/RADS | 234 | 740890.2 | d | 6902 | Beta | EB/PL/KS | 5.25e-05 | 0.000276 | 0.000335 | 0.000817 | 1.82 | 5440 | 2.9658 | 1998--2015 |  | 2016-12-20
|  | MOV-FTOC | Motor Operated Valve Fails to Open/Close | EPIX/RADS | 558 | 740890.2 | d | 6902 | Beta | EB/PL/KS | 0.0002 | 0.00072 | 0.000822 | 0.00178 | 2.66 | 3240 | 2.4746 | 1998--2015 |  | 2016-12-20
|  | MOV-FC | Motor Operated Feed Control Valve Fails To Operate | EPIX/RADS | 119 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 7.49e-09 | 4.69e-08 | 5.9e-08 | 1.5e-07 | 1.58 | 26900000 | 3.2053 | 1998--2015 |  | 2016-12-20
|  | MOV-SOP | Motor Operated Valve Fails To Remain Open | EPIX/RADS | 63 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 2.9e-10 | 1.69e-08 | 3.24e-08 | 1.17e-07 | 0.593 | 18300000 | 6.926 | 1998--2015 |  | 2016-12-20
|  | MOV-ILS | Motor Operated Valve Internal Leakage (Small) | EPIX/RADS | 141 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 1.66e-09 | 4.58e-08 | 7.58e-08 | 2.52e-07 | 0.747 | 9860000 | 5.5029 | 1998--2015 |  | 2016-12-20
|  | MOV-ILL | Motor Operated Valve Internal Leakage (Rupture) | EPIX/RADS | 141 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 1.62e-13 | 3.7e-10 | 1.52e-09 | 6.93e-09 | 0.3 | 197889000 | 18.7656 | 1998--2015 | MOV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | MOV-ELS | Motor Operated Valve External Leakage (Small) | EPIX/RADS | 51 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 9.56e-11 | 1.21e-08 | 2.71e-08 | 1.05e-07 | 0.49 | 18100000 | 8.6605 | 1998--2015 |  | 2016-12-20
|  | MOV-ELL | Motor Operated Valve External Leakage (Rupture) | EPIX/RADS | 51 | 1983522000 | h | 13001 | Gamma | EB/PL/KS | 2.03e-13 | 4.62e-10 | 1.9e-09 | 8.68e-09 | 0.3 | 158144000 | 18.7656 | 1998--2015 | MOV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | MOV-FTO-BFV | Butterfly Valve Fail To Open | EPIX/RADS | 27 | 109521.5 | d | 961 | Beta | JNID/IL | 0.000179 | 0.000249 | 0.000251 | 0.000336 | 27.5 | 109000 | 1.3492 | 1998--2015 |  | 2016-12-20
|  | MOV-FTC-BFV | Butterfly Valve Fail To Close | EPIX/RADS | 34 | 109521.5 | d | 961 | Beta | EB/PL/KS | 2.3e-05 | 0.000245 | 0.000338 | 0.000968 | 1.13 | 3350 | 3.9557 | 1998--2015 |  | 2016-12-20
|  | MOV-FTOC-BFV | Butterfly Valve Fail To Open/Close | EPIX/RADS | 65 | 109521.5 | d | 961 | Beta | EB/PL/KS | 3.84e-05 | 0.000498 | 0.000714 | 0.00212 | 1.02 | 1430 | 4.2552 | 1998--2015 |  | 2016-12-20
|  | CCW-BFV-OC | CCW Butterfly Valve Spuriously Transfers | EPIX/RADS | 6 | 106466800 | h | 708 | Gamma | JNID/IL | 2.78e-08 | 5.82e-08 | 6.11e-08 | 1.05e-07 | 6.5 | 106000000 | 1.8122 | 1998--2015 |  | 2016-12-20
|  | CCW-MOV-OC | CCW MOV Spuriously Transfers | EPIX/RADS | 6 | 223471400 | h | 1443 | Gamma | JNID/IL | 1.32e-08 | 2.77e-08 | 2.91e-08 | 5.01e-08 | 6.5 | 223000000 | 1.8122 | 1998--2015 |  | 2016-12-20
|  | SWS-MOV-OC | Standby Service Water Motor Operated Valve Spuriously Transfers | EPIX/RADS | 3 | 73067170 | h | 495 | Gamma | JNID/IL | 1.48e-08 | 4.34e-08 | 4.79e-08 | 9.62e-08 | 3.5 | 73100000 | 2.2168 | 1998--2015 |  | 2016-12-20
| Hydraulic-Operated Valve (HOV) | HOV-FTOC | Hydraulic Operated Valve Fails To Open | EPIX/RADS | 26 | 19862.5 | d | 230 | Beta | JNID/IL | 0.00094 | 0.00132 | 0.00133 | 0.00179 | 26.5 | 19800 | 1.3562 | 1998--2015 |  | 2016-12-20
|  | HOV-FC | Hydraulic Valve Fail To Control | EPIX/RADS | 42 | 93083360 | h | 601 | Gamma | JNID/IL | 3.48e-07 | 4.53e-07 | 4.57e-07 | 5.77e-07 | 42.5 | 93100000 | 1.2749 | 1998--2015 |  | 2016-12-20
|  | HOV-SOP | Hydraulic valve spurios operation | EPIX/RADS | 17 | 93083360 | h | 601 | Gamma | JNID/IL | 1.21e-07 | 1.84e-07 | 1.88e-07 | 2.67e-07 | 17.5 | 93100000 | 1.4504 | 1998--2015 |  | 2016-12-20
|  | HOV-ILS | Hydraulic Operated Valve Internal Leakage (Small) | EPIX/RADS | 4 | 93083360 | h | 601 | Gamma | JNID/IL | 1.79e-08 | 4.48e-08 | 4.83e-08 | 9.09e-08 | 4.5 | 93100000 | 2.028 | 1998--2015 |  | 2016-12-20
|  | HOV-ILL | Hydraulic Operated Valve Internal Leakage (Rupture) | EPIX/RADS | 4 | 93083360 | h | 601 | Gamma | JNID/IL | 1.03e-13 | 2.35e-10 | 9.66e-10 | 4.42e-09 | 0.3 | 310559000 | 18.7656 | 1998--2015 | HOV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | HOV-ELS | Hydraulic Operated Valve External Leakage (Small) | EPIX/RADS | 12 | 93083360 | h | 601 | Gamma | JNID/IL | 7.85e-08 | 1.31e-07 | 1.34e-07 | 2.02e-07 | 12.5 | 93100000 | 1.5472 | 1998--2015 |  | 2016-12-20
|  | HOV-ELL | Hydraulic Operated Valve External Leakage (Rupture) | EPIX/RADS | 12 | 93083360 | h | 601 | Gamma | JNID/IL | 1e-12 | 2.29e-09 | 9.38e-09 | 4.29e-08 | 0.3 | 31982900 | 18.7656 | 1998--2015 | HOV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Solenoid-Operated Valve (SOV) | SOV-FTOC | Solenoid Operated Valve Fails To Open | EPIX/RADS | 23 | 33316.7 | d | 759 | Beta | JNID/IL | 0.000484 | 0.000695 | 0.000705 | 0.00096 | 23.5 | 33300 | 1.3811 | 1998--2015 |  | 2016-12-20
|  | SOV-FC | Solenoid Operated Valve Fails To Control | EPIX/RADS | 58 | 143582100 | h | 1161 | Gamma | JNID/IL | 3.23e-07 | 4.04e-07 | 4.07e-07 | 4.97e-07 | 58.5 | 144000000 | 1.2313 | 1998--2015 |  | 2016-12-20
|  | SOV-SOP | Solenoid-Operated Valve Spuriously Open or Close | EPIX/RADS | 9 | 143582100 | h | 1161 | Gamma | JNID/IL | 3.51e-08 | 6.37e-08 | 6.62e-08 | 1.05e-07 | 9.5 | 144000000 | 1.6438 | 1998--2015 |  | 2016-12-20
|  | SOV-ILS | Solenoid Operated Valve Internal Leakage (Small) | EPIX/RADS | 20 | 143582100 | h | 1161 | Gamma | JNID/IL | 9.49e-08 | 1.4e-07 | 1.43e-07 | 1.98e-07 | 20.5 | 144000000 | 1.4117 | 1998--2015 |  | 2016-12-20
|  | SOV-ILL | Solenoid Operated Valve Internal Leakage (Rupture) | EPIX/RADS | 20 | 143582100 | h | 1161 | Gamma | JNID/IL | 3.06e-13 | 6.97e-10 | 2.86e-09 | 1.31e-08 | 0.3 | 104895000 | 18.7656 | 1998--2015 | SOV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | SOV-ELS | Solenoid Operated Valve External Leakage (Small) | EPIX/RADS | 3 | 143582100 | h | 1161 | Gamma | JNID/IL | 7.53e-09 | 2.2e-08 | 2.44e-08 | 4.88e-08 | 3.5 | 144000000 | 2.2168 | 1998--2015 |  | 2016-12-20
|  | SOV-ELL | Solenoid Operated Valve External Leakage (Rupture) | EPIX/RADS | 3 | 143582100 | h | 1161 | Gamma | JNID/IL | 1.83e-13 | 4.16e-10 | 1.71e-09 | 7.81e-09 | 0.3 | 175644000 | 18.7656 | 1998--2015 | SOV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Explosive-Operated Valve (EOV) | EOV-FTO | Explosive Valve Fails To Open | EPIX/RADS | 3 | 713.1 | d | 57 | Beta | JNID/IL | 0.00152 | 0.00444 | 0.0049 | 0.00983 | 3.5 | 711 | 2.2108 | 1998--2015 |  | 2016-12-20
| Vacuum Breaker Valve (VBV) | VBV-FTO | Vacuum Breaker Valve Fail to Open | EPIX/RADS | 2 | 27842.4 | d | 167 | Beta | JNID/IL | 2.06e-05 | 7.83e-05 | 8.98e-05 | 0.000199 | 2.5 | 27800 | 2.5439 | 1998--2015 |  | 2016-12-20
|  | VBV-FTC | Vacuum breaker fails to close | EPIX/RADS | 6 | 27842.4 | d | 167 | Beta | EB/PL/KS | 4.03e-06 | 0.000127 | 0.000215 | 0.000725 | 0.715 | 3330 | 5.7296 | 1998--2015 |  | 2016-12-20
|  | VBV-FTOC | Vacuum Breaker Valve Fails to Open/Close | EPIX/RADS | 8 | 27842.4 | d | 167 | Beta | EB/PL/KS | 5.55e-06 | 0.000194 | 0.000337 | 0.00115 | 0.69 | 2050 | 5.9268 | 1998--2015 |  | 2016-12-20
|  | VBV-SOP | Vacuum Breaker Fails Open | EPIX/RADS | 1 | 52796540 | h | 342 | Gamma | JNID/IL | 3.33e-09 | 2.24e-08 | 2.84e-08 | 7.4e-08 | 1.5 | 52800000 | 3.303 | 1998--2015 |  | 2016-12-20
|  | VBV-ILS | Vacuum Breaker Valve Internal Leakage (Small) | EPIX/RADS | 15 | 52796540 | h | 342 | Gamma | JNID/IL | 1.83e-07 | 2.87e-07 | 2.94e-07 | 4.26e-07 | 15.5 | 52800000 | 1.4829 | 1998--2015 |  | 2016-12-20
|  | VBV-ILL | Vacuum Breaker Valve Internal Leakage (Rupture) | EPIX/RADS | 15 | 52796540 | h | 342 | Gamma | JNID/IL | 6.29e-13 | 1.43e-09 | 5.88e-09 | 2.69e-08 | 0.3 | 51020400 | 18.7656 | 1998--2015 | VBV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
| Turbine Bypass Valve (TBV) | TBV-FTO | Turbine Bypass Valve Fail to Open | EPIX/RADS | 8 | 2725.4 | d | 73 | Beta | JNID/IL | 0.00159 | 0.00299 | 0.00312 | 0.00505 | 8.5 | 2720 | 1.6868 | 1998--2015 |  | 2016-12-20
|  | TBV-FTC | Turbine Bypass Valve Fails to Close | EPIX/RADS | 0 | 2725.4 | d | 73 | Beta | JNID/IL | 7.2e-07 | 8.33e-05 | 0.000183 | 0.000703 | 0.5 | 2730 | 8.4413 | 1998--2015 |  | 2016-12-20
|  | TBV-FTOC | Turbine Bypass Valve Fail to Open/Close | EPIX/RADS | 8 | 2725.4 | d | 73 | Beta | JNID/IL | 0.00159 | 0.00299 | 0.00312 | 0.00505 | 8.5 | 2720 | 1.6868 | 1998--2015 |  | 2016-12-20
|  | TBV-FC | Turbine Bypass Valve Fails To Control | EPIX/RADS | 14 | 23964260 | h | 156 | Gamma | JNID/IL | 3.69e-07 | 5.9e-07 | 6.05e-07 | 8.87e-07 | 14.5 | 24000000 | 1.5019 | 1998--2015 |  | 2016-12-20
| Main Steam Isolation Valve (MSV) | MSV-FTOC | Main Steam Isolation Valve Fails to Open/Close | EPIX/RADS | 34 | 38629.4 | d | 419 | Beta | JNID/IL | 0.000659 | 0.000884 | 0.000893 | 0.00116 | 34.5 | 38600 | 1.308 | 1998--2015 |  | 2016-12-20
|  | MSV-SOP | Main Steam Isolation Fails To Remain Open | EPIX/RADS | 25 | 79241950 | h | 513 | Gamma | EB/PL/KS | 1.44e-09 | 1.45e-07 | 3.1e-07 | 1.18e-06 | 0.516 | 1660000 | 8.1238 | 1998--2015 |  | 2016-12-20
|  | MSV-ILS | Main Steam Isolation Internal Leakage (Small) | EPIX/RADS | 63 | 79241950 | h | 513 | Gamma | JNID/IL | 6.44e-07 | 7.98e-07 | 8.01e-07 | 9.74e-07 | 63.5 | 79200000 | 1.2214 | 1998--2015 |  | 2016-12-20
|  | MSV-ILL | Main Steam Isolation Internal Leakage (Rupture) | EPIX/RADS | 63 | 79241950 | h | 513 | Gamma | JNID/IL | 1.71e-12 | 3.91e-09 | 1.6e-08 | 7.33e-08 | 0.3 | 18726600 | 18.7656 | 1998--2015 | MSV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | MSV-ELS | Main Steam Isolation External Leakage (Small) | EPIX/RADS | 2 | 79241950 | h | 513 | Gamma | JNID/IL | 7.23e-09 | 2.75e-08 | 3.15e-08 | 6.99e-08 | 2.5 | 79200000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | MSV-ELL | Main Steam Isolation External Leakage (Rupture) | EPIX/RADS | 2 | 79241950 | h | 513 | Gamma | JNID/IL | 2.36e-13 | 5.38e-10 | 2.21e-09 | 1.01e-08 | 0.3 | 136054000 | 18.7656 | 1998--2015 | MSV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Check Valve (CKV) | CKV-FTO | Check Valve Fails To Open Fails To Open | EPIX/RADS | 0 | 54125.9 | d | 496 | Beta | JNID/IL | 3.63e-08 | 4.2e-06 | 9.24e-06 | 3.55e-05 | 0.5 | 54100 | 8.4438 | 1998--2015 |  | 2016-12-20
|  | CKV-FTC | Check Valve Fails To Close | EPIX/RADS | 8 | 54125.9 | d | 496 | Beta | JNID/IL | 8.01e-05 | 0.000151 | 0.000157 | 0.000255 | 8.5 | 54100 | 1.6884 | 1998--2015 |  | 2016-12-20
|  | CKV-SO | Check Valve Fails to Remain Open | EPIX/RADS | 2 | 977258600 | h | 6331 | Gamma | JNID/IL | 5.86e-10 | 2.23e-09 | 2.56e-09 | 5.67e-09 | 2.5 | 977000000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | CKV-SC | Check Valve Fails to Remain Open (Spurious Close) | EPIX/RADS | 5 | 977258600 | h | 6331 | Gamma | JNID/IL | 2.34e-09 | 5.29e-09 | 5.63e-09 | 1.01e-08 | 5.5 | 977000000 | 1.9026 | 1998--2015 |  | 2016-12-20
|  | CKV-ILS | Check Valve Internal Leakage (Small) | EPIX/RADS | 143 | 977258600 | h | 6331 | Gamma | EB/PL/KS | 1.14e-09 | 1e-07 | 2.08e-07 | 7.8e-07 | 0.534 | 2570000 | 7.7976 | 1998--2015 |  | 2016-12-20
|  | CKV-ILL | Check Valve Internal Leakage (Rupture) | EPIX/RADS | 143 | 977258600 | h | 6331 | Gamma | EB/PL/KS | 4.45e-13 | 1.01e-09 | 4.16e-09 | 1.9e-08 | 0.3 | 72115400 | 18.7656 | 1998--2015 | CKV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | CKV-ELS | Check Valve External Leakage (Small) | EPIX/RADS | 7 | 977258600 | h | 6331 | Gamma | JNID/IL | 3.72e-09 | 7.34e-09 | 7.67e-09 | 1.28e-08 | 7.5 | 977000000 | 1.7432 | 1998--2015 |  | 2016-12-20
|  | CKV-ELL | Check Valve External Leakage (Rupture) | EPIX/RADS | 7 | 977258600 | h | 6331 | Gamma | JNID/IL | 5.75e-14 | 1.31e-10 | 5.37e-10 | 2.46e-09 | 0.3 | 558763000 | 18.7656 | 1998--2015 | CKV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Manual Valve (XVM) | XVM-FTOC | Manual Valve Fails To Open | EPIX/RADS | 1 | 3270.1 | d | 66 | Beta | JNID/IL | 5.38e-05 | 0.000362 | 0.000459 | 0.00119 | 1.5 | 3270 | 3.3016 | 1998--2015 |  | 2016-12-20
|  | XVM-SOP | Manual Valve Spurious Transfer | EPIX/RADS | 6 | 128295300 | h | 866 | Gamma | JNID/IL | 2.3e-08 | 4.82e-08 | 5.07e-08 | 8.74e-08 | 6.5 | 128000000 | 1.8122 | 1998--2015 |  | 2016-12-20
|  | XVM-ILS | Manual Valve Internal Leakage (Small) | EPIX/RADS | 7 | 128295300 | h | 866 | Gamma | EB/PL/KS | 9.97e-10 | 3.89e-08 | 6.88e-08 | 2.38e-07 | 0.667 | 9700000 | 6.1301 | 1998--2015 |  | 2016-12-20
|  | XVM-ILL | Manual Valve Internal Leakage (Rupture) | EPIX/RADS | 7 | 128295300 | h | 866 | Gamma | EB/PL/KS | 1.47e-13 | 3.35e-10 | 1.38e-09 | 6.29e-09 | 0.3 | 218023000 | 18.7656 | 1998--2015 | XVM leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | XVM-ELS | Manual Valve External Leakage (Small) | EPIX/RADS | 14 | 128295300 | h | 866 | Gamma | JNID/IL | 6.92e-08 | 1.11e-07 | 1.13e-07 | 1.66e-07 | 14.5 | 128000000 | 1.5019 | 1998--2015 |  | 2016-12-20
|  | XVM-ELL | Manual Valve External Leakage (Rupture) | EPIX/RADS | 14 | 128295300 | h | 866 | Gamma | JNID/IL | 8.47e-13 | 1.93e-09 | 7.91e-09 | 3.62e-08 | 0.3 | 37926700 | 18.7656 | 1998--2015 | XVM leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | SWS-XVM-OC | Standby Service Water Manual Valve Spuriously Transfers | EPIX/RADS | 2 | 18346180 | h | 121 | Gamma | JNID/IL | 3.13e-08 | 1.19e-07 | 1.36e-07 | 3.02e-07 | 2.5 | 18300000 | 2.5441 | 1998--2015 |  | 2016-12-20
| Flow Control Valve (FCV) | FCV-FTOC | Flow Control Valve Fails To Open/Close | EPIX/RADS | 5 | 12487.7 | d | 96 | Beta | JNID/IL | 0.000183 | 0.000413 | 0.00044 | 0.000787 | 5.5 | 12500 | 1.9023 | 1998--2015 |  | 2016-12-20
|  | FCV-FC | Flow Control Valve Fails To Control | EPIX/RADS | 16 | 88861090 | h | 574 | Gamma | JNID/IL | 1.17e-07 | 1.82e-07 | 1.86e-07 | 2.67e-07 | 16.5 | 88900000 | 1.4659 | 1998--2015 |  | 2016-12-20
|  | FCV-SO | Flow Control Valve Transfers Positions | EPIX/RADS | 10 | 88861090 | h | 574 | Gamma | JNID/IL | 6.52e-08 | 1.14e-07 | 1.18e-07 | 1.84e-07 | 10.5 | 88900000 | 1.6064 | 1998--2015 |  | 2016-12-20
|  | FRV-FO | Feedwater Regulating Valve Fail To Operate | EPIX/RADS | 72 | 33730380 | h | 216 | Gamma | EB/PL/KS | 3.08e-07 | 1.72e-06 | 2.1e-06 | 5.23e-06 | 1.73 | 822000 | 3.048 | 1998--2015 |  | 2016-12-20
Pumps | Motor-Driven Pump (MDP) | MDP-SBY-FTS | Motor Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 351 | 482205.5 | d | 1311 | Beta | EB/PL/KS | 0.000159 | 0.000678 | 0.000794 | 0.00183 | 2.21 | 2780 | 2.6908 | 1998--2015 |  | 2016-12-20
|  | MDP-SBY-FTR<1H | Motor Driven Pump Fails To Run, Early Term | EPIX/RADS | 48 | 437647.2 | h | 1311 | Gamma | EB/PL/KS | 3.94e-06 | 7.86e-05 | 0.000122 | 0.000389 | 0.844 | 6910 | 4.9446 | 1998--2015 |  | 2016-12-20
|  | MDP-SBY-FTR>1H | Motor Driven Pump Fails To Run, Late Term | EPIX/RADS | 143 | 20062180 | h | 1311 | Gamma | EB/PL/KS | 1.35e-07 | 6.28e-06 | 1.15e-05 | 4.07e-05 | 0.632 | 54900 | 6.4741 | 1998--2015 |  | 2016-12-20
|  | MDP-ELS | Motor Driven Pump External Leakage (Small) | EPIX/RADS | 105 | 347850600 | h | 2344 | Gamma | EB/PL/KS | 9.46e-09 | 1.87e-07 | 2.91e-07 | 9.22e-07 | 0.847 | 2920000 | 4.9299 | 1998--2015 |  | 2016-12-20
|  | MDP-ELL | Motor Driven Pump External Leakage (Rupture) | EPIX/RADS | 105 | 347850600 | h | 2344 | Gamma | EB/PL/KS | 2.18e-12 | 4.97e-09 | 2.04e-08 | 9.32e-08 | 0.3 | 14727500 | 18.7656 | 1998--2015 | MDP leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | MDP-NR-FTS | Motor-driven pump Fail to Start, Normally Running | EPIX/RADS | 147 | 138318.9 | d | 670 | Beta | EB/PL/KS | 0.000261 | 0.000952 | 0.00108 | 0.00237 | 2.62 | 2410 | 2.4904 | 1998--2015 |  | 2016-12-20
|  | MDP-NR-FTR | Motor-driven pump Fail to Run, Normally Running | EPIX/RADS | 225 | 59582350 | h | 664 | Gamma | EB/PL/KS | 1.15e-06 | 3.43e-06 | 3.79e-06 | 7.68e-06 | 3.42 | 901000 | 2.2362 | 1998--2015 |  | 2016-12-20
|  | MDP-CCW-FTS | CCW Motor-driven pump Fail to Start | EPIX/RADS | 69 | 88692.5 | h | 291 | Beta | EB/PL/KS | 5.86e-05 | 0.000632 | 0.000878 | 0.00252 | 1.12 | 1280 | 3.9779 | 1998--2015 |  | 2016-12-20
|  | MDP-CCW-FTR | CCW Motor-driven pump Fail to Run (Yr-1) | EPIX/RADS | 53 | 19648220 | h | 291 | Gamma | EB/PL/KS | 2.87e-07 | 2.13e-06 | 2.76e-06 | 7.33e-06 | 1.4 | 509000 | 3.4421 | 1998--2015 |  | 2016-12-20
|  | MDP-SWS-FTS | SWS Pump FTS | EPIX/RADS | 180 | 264383.9 | d | 549 | Beta | EB/PL/KS | 6.2e-05 | 0.000617 | 0.000841 | 0.00238 | 1.17 | 1390 | 3.8603 | 1998--2015 |  | 2016-12-20
|  | SWS-MDP-FS-NE | SWS Pump Non-Enviro-FTS | EPIX/RADS | 149 | 249956.9 | h | 446 | Beta | EB/PL/KS | 5.67e-05 | 0.000556 | 0.000755 | 0.00214 | 1.18 | 1560 | 3.8384 | 1998--2015 |  | 2016-12-20
|  | SWS-MDP-FR-NE | Service Water Motor-Driven Pump (Running) Fail to Run Non-ExEE (yr-1) | EPIX/RADS | 2 | 16692670 | h | 446 | Gamma | JNID/IL | 3.43e-08 | 1.3e-07 | 1.5e-07 | 3.31e-07 | 2.5 | 16700000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | MDP-SWS-FTR | SWS Pump FTR (hr-1) | EPIX/RADS | 64 | 10443960 | h | 106 | Gamma | EB/PL/KS | 4.14e-07 | 4.7e-06 | 6.56e-06 | 1.91e-05 | 1.09 | 166000 | 4.0585 | 1998--2015 |  | 2016-12-20
|  | NSW-MDP-FR | Nuclear Service Water MDP Fails to Run | EPIX/RADS | 64 | 10256170 | h | 104 | Gamma | EB/PL/KS | 4.34e-07 | 4.85e-06 | 6.72e-06 | 1.96e-05 | 1.1 | 163000 | 4.0323 | 1998--2015 |  | 2016-12-20
|  | MDP-FS-NE-SWS | Service Water MDP Fail to Run, Non-Environmental | EPIX/RADS | 179 | 264383.9 | d | 549 | Beta | EB/PL/KS | 6.39e-05 | 0.000618 | 0.000836 | 0.00236 | 1.19 | 1420 | 3.8164 | 1998--2015 |  | 2016-12-20
|  | MDP-FR-NE-SWS | Service Water MDP Fail to Run, Non-Environmental | EPIX/RADS | 151 | 26944240 | h | 548 | Gamma | EB/PL/KS | 8.93e-07 | 4.69e-06 | 5.67e-06 | 1.39e-05 | 1.82 | 320000 | 2.9666 | 1998--2015 |  | 2016-12-20
|  | CSW-MDP-FR | CSW Motor Driven Pump Fails to Run | EPIX/RADS | 25 | 3654539 | h | 32 | Gamma | JNID/IL | 4.88e-06 | 6.9e-06 | 6.98e-06 | 9.41e-06 | 25.5 | 3650000 | 1.3642 | 1998--2015 |  | 2016-12-20
| Turbine-Driven Pump (TDP) | TDP-SBY-FTS | Turbine Driven Pump Fails To Start (Pooled Systems), Normally Standby | EPIX/RADS | 146 | 26557.9 | d | 133 | Beta | EB/PL/KS | 0.00047 | 0.00447 | 0.00601 | 0.0169 | 1.2 | 198 | 3.7746 | 1998--2015 |  | 2016-12-20
|  | TDP-SBY-FTR<1H | Turbine Driven Pump Fails To Run (Pooled Systems), Early Term | EPIX/RADS | 61 | 18025.1 | h | 133 | Gamma | EB/PL/KS | 0.000134 | 0.00243 | 0.0037 | 0.0116 | 0.878 | 237 | 4.7854 | 1998--2015 |  | 2016-12-20
|  | TDP-SBY-FTR>1H | Turbine Driven Pump Fails To Run (Pooled Systems), Late Term | EPIX/RADS | 23 | 11204.6 | h | 133 | Gamma | JNID/IL | 0.00144 | 0.00207 | 0.0021 | 0.00286 | 23.5 | 11200 | 1.3813 | 1998--2015 |  | 2016-12-20
|  | TDP-NR-FTS | Turbine Driven Pump Fails To Start (Pooled Systems), Normally Running | EPIX/RADS | 12 | 1395 | d | 43 | Beta | EB/PL/KS | 0.000404 | 0.00625 | 0.00917 | 0.0281 | 0.938 | 101 | 4.4891 | 1998--2015 |  | 2016-12-20
|  | TDP-NR-FTR | Turbine Driven Pump Fails To Run (Pooled Systems), Normally Running | EPIX/RADS | 62 | 5984882 | h | 43 | Gamma | EB/PL/KS | 1.43e-06 | 8.73e-06 | 1.09e-05 | 2.77e-05 | 1.61 | 148000 | 3.1714 | 1998--2015 |  | 2016-12-20
|  | TDP-ELS | Turbine-Driven Pump External Leakage (Small) | EPIX/RADS | 15 | 28788990 | h | 186 | Gamma | JNID/IL | 3.35e-07 | 5.27e-07 | 5.38e-07 | 7.81e-07 | 15.5 | 28800000 | 1.4829 | 1998--2015 |  | 2016-12-20
|  | TDP-ELL | Turbine Bypass Valve External Leakage (Rupture) | EPIX/RADS | 15 | 28788990 | h | 186 | Gamma | JNID/IL | 4.03e-12 | 9.18e-09 | 3.77e-08 | 1.72e-07 | 0.3 | 7966010 | 18.7656 | 1998--2015 | TDP leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | TDP-FS-NS-AFW | AFW Turbine Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 72 | 18053.8 | d | 74 | Beta | EB/PL/KS | 9.44e-05 | 0.00262 | 0.00433 | 0.0143 | 0.746 | 172 | 5.4772 | 1998--2015 |  | 2016-12-20
|  | TDP-FR-E-AFW | AFW Turbine Driven Pump Fails To Run, Early Term | EPIX/RADS | 40 | 12075.8 | h | 74 | Gamma | EB/PL/KS | 9.03e-05 | 0.00226 | 0.00367 | 0.012 | 0.774 | 211 | 5.3293 | 1998--2015 |  | 2016-12-20
|  | TDP-FR-L-AFW | AFW Turbine Driven Pump Fails To Run, Late Term | EPIX/RADS | 13 | 9282.6 | h | 74 | Gamma | JNID/IL | 0.00087 | 0.00142 | 0.00145 | 0.00216 | 13.5 | 9280 | 1.5231 | 1998--2015 |  | 2016-12-20
|  | TDP-FS-NS-HCI-RCI | HCI-RCI Turbine Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 41 | 4929.2 | d | 31 | Beta | EB/PL/KS | 0.00252 | 0.0079 | 0.00878 | 0.0181 | 3.16 | 356 | 2.294 | 1998--2015 |  | 2016-12-20
|  | TDP-FR-E-HCI-RCI | HCI Turbine Driven Pump Fails To Run, Early Term | EPIX/RADS | 21 | 5949.3 | h | 59 | Gamma | EB/PL/KS | 0.000236 | 0.00268 | 0.00375 | 0.0109 | 1.09 | 291 | 4.0585 | 1998--2015 |  | 2016-12-20
|  | TDP-FR-L-HCI-RCI | HCI-RCI Turbine Driven Pump Fails To Run, Late Term | EPIX/RADS | 10 | 1922 | h | 59 | Gamma | EB/PL/KS | 0.00104 | 0.00467 | 0.00552 | 0.0129 | 2.1 | 381 | 2.7593 | 1998--2015 |  | 2016-12-20
|  | TDP-FS-NR-MFW | MFW Turbine Driven Pump Fails To Start, Normally Running | EPIX/RADS | 62 | 5984882 | d | 43 | Gamma | EB/PL/KS | 1.43e-06 | 8.73e-06 | 1.09e-05 | 2.77e-05 | 1.61 | 148000 | 3.1714 | 1998--2015 |  | 2016-12-20
|  | TDP-FR-NR-MFW | MFW Turbine Driven Pump Fails To Run, Normally Running | EPIX/RADS | 62 | 5984882 | h | 43 | Gamma | EB/PL/KS | 1.43e-06 | 8.73e-06 | 1.09e-05 | 2.77e-05 | 1.61 | 148000 | 3.1714 | 1998--2015 |  | 2016-12-20
| Engine-Driven Pump (EDP) | EDP-FTS | Engine Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 26 | 17987.9 | d | 37 | Beta | EB/PL/KS | 2.52e-05 | 0.00119 | 0.00217 | 0.00768 | 0.63 | 289 | 6.4743 | 1998--2015 |  | 2016-12-20
|  | EDP-FTR<1H | Engine Driven Pump Fails To Run, Early Term, Normally Standby | EPIX/RADS | 10 | 10716.5 | h | 37 | Gamma | JNID/IL | 0.000542 | 0.00095 | 0.00098 | 0.00153 | 10.5 | 10700 | 1.6064 | 1998--2015 |  | 2016-12-20
|  | EDP-FTR>1H | Engine Driven Pump Fails To Run, Late Term, Normally Standby | EPIX/RADS | 11 | 5820.1 | h | 37 | Gamma | JNID/IL | 0.00112 | 0.00192 | 0.00198 | 0.00302 | 11.5 | 5820 | 1.5746 | 1998--2015 |  | 2016-12-20
|  | EDP-ELS | Engine-Driven Pump External Leakage (Small) | EPIX/RADS | 8 | 9129089 | h | 69 | Gamma | EB/PL/KS | 5.15e-08 | 6.42e-07 | 9.12e-07 | 2.7e-06 | 1.04 | 1140000 | 4.1982 | 1998--2015 |  | 2016-12-20
|  | EDP-ELL | Engine Driven Pump External Leakage (Rupture) | EPIX/RADS | 8 | 9129089 | h | 69 | Gamma | EB/PL/KS | 6.83e-12 | 1.56e-08 | 6.38e-08 | 2.92e-07 | 0.3 | 4699250 | 18.7656 | 1998--2015 | EDP leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | AFW-EDP-FTS | AFW Engine-driven pump Fails to Start | EPIX/RADS | 3 | 1274.8 | d | 5 | Beta | JNID/IL | 0.000852 | 0.00249 | 0.00274 | 0.00552 | 3.5 | 1270 | 2.2134 | 1998--2015 |  | 2016-12-20
|  | AFW-EDP-FTR<1H | AFW Engine-driven pump Fails to Run <1H | EPIX/RADS | 4 | 739.2 | h | 5 | Gamma | JNID/IL | 0.00225 | 0.00564 | 0.00609 | 0.0114 | 4.5 | 739 | 2.028 | 1998--2015 |  | 2016-12-20
|  | AFW-EDP-FTR>1H | AFW Engine-driven pump Fails to Run >1H | EPIX/RADS | 2 | 262.4 | h | 5 | Gamma | JNID/IL | 0.00219 | 0.0083 | 0.00953 | 0.0211 | 2.5 | 262 | 2.5441 | 1998--2015 |  | 2016-12-20
| Positive Displacement Pump (PDP) | PDP-NR-FTS | Positive Displacement Pump Fails To Start, Normally Running | EPIX/RADS | 78 | 35863.1 | d | 63 | Beta | EB/PL/KS | 0.000363 | 0.00213 | 0.00263 | 0.00663 | 1.66 | 628 | 3.1106 | 1998--2015 |  | 2016-12-20
|  | PDP-NR-FTR | Positive Displacement Pump Fails To Run, Normally Running | EPIX/RADS | 71 | 2905081 | h | 60 | Gamma | EB/PL/KS | 1.43e-06 | 2.49e-05 | 3.77e-05 | 0.000117 | 0.892 | 23700 | 4.7243 | 1998--2015 |  | 2016-12-20
|  | PDP-SBY-FTS | Positive Displacement Pump Fails To Start, Normally Standby | EPIX/RADS | 16 | 10798.5 | d | 72 | Beta | JNID/IL | 0.000965 | 0.00149 | 0.00153 | 0.00219 | 16.5 | 10800 | 1.4654 | 1998--2015 |  | 2016-12-20
|  | PDP-SBY-FTR<1H | Positive Displacement Pump Fails To Run, Early Term | EPIX/RADS | 2 | 4699.4 | h | 72 | Gamma | JNID/IL | 0.000122 | 0.000463 | 0.000532 | 0.00118 | 2.5 | 4700 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | PDP-SBY-FTR>1H | Positive Displacement Pump Fails To Run, Late Term | EPIX/RADS | 2 | 1709.5 | h | 72 | Gamma | JNID/IL | 0.000335 | 0.00127 | 0.00146 | 0.00324 | 2.5 | 1710 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | PDP-ELS | Positive Displacement Pump External Leakage (Small) | EPIX/RADS | 28 | 26271740 | h | 175 | Gamma | JNID/IL | 7.73e-07 | 1.07e-06 | 1.08e-06 | 1.44e-06 | 28.5 | 26300000 | 1.3424 | 1998--2015 |  | 2016-12-20
|  | PDP-ELL | Positive Displacement Pump External Leakage (Rupture) | EPIX/RADS | 28 | 26271740 | h | 175 | Gamma | JNID/IL | 8.09e-12 | 1.84e-08 | 7.56e-08 | 3.46e-07 | 0.3 | 3968250 | 18.7656 | 1998--2015 | PDP leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Pump Volute (PMP) | PMP-Volute | Pump Volute Fails To Run (Driver Independent Centrifugal Pumps) | EPIX/RADS | 25 | 158885.3 | h | 207 | Gamma | JNID/IL | 0.000112 | 0.000158 | 0.00016 | 0.000216 | 25.5 | 159000 | 1.3642 | 1998--2015 |  | 2016-12-20
Generators | Emergency Diesel Generator (EDG) | EDG-FTS | Diesel Generator Fails To Start, Normally Standby | EPIX/RADS | 214 | 75451.5 | d | 232 | Beta | EB/PL/KS | 0.00152 | 0.00278 | 0.00288 | 0.0046 | 9.19 | 3180 | 1.6553 | 1998--2015 |  | 2016-12-20
|  | EDG-FTLR | Diesel Generator Fails To Load And Run, Early | EPIX/RADS | 239 | 65993.2 | h | 232 | Gamma | EB/PL/KS | 0.00114 | 0.00337 | 0.00372 | 0.00749 | 3.47 | 933 | 2.224 | 1998--2015 |  | 2016-12-20
|  | EDG-FTR | Diesel Generator Fails To Run, Late Term | EPIX/RADS | 184 | 133975.8 | h | 232 | Gamma | EB/PL/KS | 0.000353 | 0.00133 | 0.00152 | 0.00336 | 2.53 | 1660 | 2.5307 | 1998--2015 |  | 2016-12-20
| Hydro Turbine Generator (HTG) | HTG-FTS | Hydro Electric Turbine Generator Fails To Start | EPIX/RADS | 11 | 7270 | d | 2 | Beta | JNID/IL | 0.0009 | 0.00154 | 0.00158 | 0.00242 | 11.5 | 7260 | 1.5739 | 1998--2015 |  | 2016-12-20
|  | HTG-FTLR | Hydro Electric Turbine Generator Fail To Run (< 1 Hour) | EPIX/RADS | 7 | 4629 | h | 2 | Gamma | JNID/IL | 0.000784 | 0.00155 | 0.00162 | 0.0027 | 7.5 | 4630 | 1.7432 | 1998--2015 |  | 2016-12-20
|  | HTG-FTR | Hydro Electric Turbine Generator Fail To Run (> 1 Hour) | EPIX/RADS | 1 | 10678.3 | h | 2 | Gamma | JNID/IL | 1.64e-05 | 0.000111 | 0.00014 | 0.000365 | 1.5 | 10700 | 3.303 | 1998--2015 |  | 2016-12-20
| Combustion Turbine Generator (CTG) | CTG-FTS | Gas Turbine Generator Fails To Start, Normally Standby | EPIX/RADS | 18 | 503.3 | d | 3 | Beta | EB/PL/KS | 0.00298 | 0.0373 | 0.0512 | 0.148 | 1.03 | 19 | 3.9807 | 1998--2015 |  | 2016-12-20
|  | CTG-FTLR | Gas Turbine Generator Fails To Load And Run, Early Term | EPIX/RADS | 2 | 432 | d | 2 | Gamma | JNID/IL | 0.00133 | 0.00504 | 0.00579 | 0.0128 | 2.5 | 432 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | CTG-FTR | Gas Turbine Generator Fails To Run, Late Term | EPIX/RADS | 5 | 648 | h | 2 | Gamma | JNID/IL | 0.00353 | 0.00798 | 0.00849 | 0.0152 | 5.5 | 648 | 1.9026 | 1998--2015 |  | 2016-12-20
| High-Pressure Core Spray Generator (HPCS) | EDG-HCS-FTS | HCS Generator Fail to Start | EPIX/RADS | 2 | 2653.9 | d | 8 | Beta | JNID/IL | 0.000216 | 0.00082 | 0.000942 | 0.00209 | 2.5 | 2650 | 2.5425 | 1998--2015 |  | 2016-12-20
|  | EDG-HCS-FTR | HCS Generator Fail to Run | EPIX/RADS | 4 | 3948 | h | 8 | Gamma | JNID/IL | 0.000421 | 0.00106 | 0.00114 | 0.00214 | 4.5 | 3950 | 2.028 | 1998--2015 |  | 2016-12-20
| Station Blackout Generator (SBO) | EDG-SBO-FTS | SBO Generator Fail to Start | EPIX/RADS | 12 | 419.1 | d | 4 | Beta | JNID/IL | 0.0175 | 0.029 | 0.0298 | 0.0445 | 12.5 | 408 | 1.5349 | 1998--2015 |  | 2016-12-20
|  | EDG-SBO-FTR | SBO Generator Fail to Run | EPIX/RADS | 2 | 1667.7 | h | 4 | Gamma | JNID/IL | 0.000343 | 0.0013 | 0.0015 | 0.00331 | 2.5 | 1670 | 2.5441 | 1998--2015 |  | 2016-12-20
Relief Valves | Safety Relief Valve (SRV) | SRV-FTO | Safety relief valve fails to open | EPIX/RADS | 23 | 9719.7 | d | 440 | Beta | JNID/IL | 0.00166 | 0.00238 | 0.00242 | 0.00329 | 23.5 | 9700 | 1.3806 | 1998--2015 |  | 2016-12-20
|  | SRV-FTC | BWR ADS/SRV Fails To Reclose | EPIX/RADS | 8 | 9719.7 | d | 440 | Beta | EB/PL/KS | 9.42e-05 | 0.000685 | 0.000886 | 0.00234 | 1.42 | 1610 | 3.4097 | 1998--2015 |  | 2016-12-20
|  | SRV-FC | Safety Relief Valve (BWR Only) Fails To Control | EPIX/RADS | 0 | 72220220 | h | 558 | Gamma | JNID/IL | 2.72e-11 | 3.15e-09 | 6.92e-09 | 2.66e-08 | 0.5 | 72200000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | SRV-SOP | Safety Relief Valve (BWR Only) SPURIOUSLY OPENS | EPIX/RADS | 9 | 72220220 | h | 558 | Gamma | EB/PL/KS | 6.03e-09 | 9.44e-08 | 1.4e-07 | 4.29e-07 | 0.935 | 6680000 | 4.5505 | 1998--2015 |  | 2016-12-20
|  | SRV-SOP | Safety Relief Valve (BWR Only) SPURIOUSLY OPENS | EPIX/RADS | 9 | 72220220 | h | 558 | Gamma | EB/PL/KS | 6.03e-09 | 9.44e-08 | 1.4e-07 | 4.29e-07 | 0.935 | 6680000 | 4.5505 | 1998--2015 |  | 2016-12-20
|  | SRV-ILS | Safety Relief Valve (BWR Only) Internal Leakage (Small) | EPIX/RADS | 25 | 72220220 | h | 558 | Gamma | EB/PL/KS | 1.16e-09 | 1.76e-07 | 4.09e-07 | 1.61e-06 | 0.471 | 1150000 | 9.1119 | 1998--2015 |  | 2016-12-20
|  | SRV-ILL | Safety Relief Valve (BWR Only) Internal Leakage (Rupture) | EPIX/RADS | 25 | 72220220 | h | 558 | Gamma | EB/PL/KS | 8.76e-13 | 1.99e-09 | 8.18e-09 | 3.74e-08 | 0.3 | 36674800 | 18.7656 | 1998--2015 | SRV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | SRV-ELS | Safety Relief Valve (BWR Only) External Leakage (Small) | EPIX/RADS | 0 | 72220220 | h | 558 | Gamma | JNID/IL | 2.72e-11 | 3.15e-09 | 6.92e-09 | 2.66e-08 | 0.5 | 72200000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | SRV-ELL | Safety Relief Valve (BWR Only) External Leakage (Rupture) | EPIX/RADS | 0 | 72220220 | h | 558 | Gamma | JNID/IL | 5.18e-14 | 1.18e-10 | 4.84e-10 | 2.22e-09 | 0.3 | 619323000 | 18.7656 | 1998--2015 | SRV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Safety Valve (SVV) | SVV-FTO | BWR Code Safety Fails To Open | EPIX/RADS | 5 | 23800.6 | d | 960 | Beta | EB/PL/KS | 4.04e-07 | 8.73e-05 | 0.000218 | 0.000877 | 0.438 | 2010 | 10.0443 | 1998--2015 |  | 2016-12-20
|  | SVV-FTC | BWR Code Safety Fails To Reclose | EPIX/RADS | 3 | 23800.6 | d | 960 | Beta | JNID/IL | 4.55e-05 | 0.000133 | 0.000147 | 0.000295 | 3.5 | 23800 | 2.2166 | 1998--2015 |  | 2016-12-20
|  | SVV-SOP | Code Safety Valve Spurious Operation | EPIX/RADS | 11 | 211426600 | h | 1426 | Gamma | JNID/IL | 3.1e-08 | 5.29e-08 | 5.44e-08 | 8.33e-08 | 11.5 | 211000000 | 1.5746 | 1998--2015 |  | 2016-12-20
|  | SVV-ILS | Code Safety Valve Internal Leakage (Small) | EPIX/RADS | 14 | 211426600 | h | 1426 | Gamma | JNID/IL | 4.2e-08 | 6.71e-08 | 6.86e-08 | 1.01e-07 | 14.5 | 211000000 | 1.5019 | 1998--2015 |  | 2016-12-20
|  | SVV-ILL | Code Safety Valve Internal Leakage (Rupture) | EPIX/RADS | 14 | 211426600 | h | 1426 | Gamma | JNID/IL | 1.47e-13 | 3.34e-10 | 1.37e-09 | 6.28e-09 | 0.3 | 218659000 | 18.7656 | 1998--2015 | SVV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | SVV-ELS | Code Safety Valve External Leakage (Small) | EPIX/RADS | 2 | 211426600 | h | 1426 | Gamma | JNID/IL | 2.71e-09 | 1.03e-08 | 1.18e-08 | 2.62e-08 | 2.5 | 211000000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | SVV-ELL | Code Safety Valve External Leakage (Rupture) | EPIX/RADS | 2 | 211426600 | h | 1426 | Gamma | JNID/IL | 8.84e-14 | 2.01e-10 | 8.26e-10 | 3.78e-09 | 0.3 | 363196000 | 18.7656 | 1998--2015 | SVV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | SVV-FTO-PWR-MSS | Safety valve fails to open (main steam system, PWRs) | EPIX/RADS | 4 | 20242.8 | d | 762 | Beta | JNID/IL | 8.23e-05 | 0.000206 | 0.000222 | 0.000419 | 4.5 | 20200 | 2.0278 | 1998--2015 |  | 2016-12-20
|  | SVV-FTC-PWR-MSS | Steam generator code safety valves fail to close | EPIX/RADS | 2 | 20242.8 | d | 762 | Beta | JNID/IL | 2.84e-05 | 0.000108 | 0.000123 | 0.000274 | 2.5 | 20200 | 2.5439 | 1998--2015 |  | 2016-12-20
|  | SVV-SOP-PWR-MSS | Safety valve spurious operation (main steam system) | EPIX/RADS | 8 | 172245500 | h | 1137 | Gamma | JNID/IL | 2.52e-08 | 4.75e-08 | 4.93e-08 | 8.02e-08 | 8.5 | 172000000 | 1.6885 | 1998--2015 |  | 2016-12-20
|  | SVV-FTO-PWR-RCS | PZR Code Safety Relief (SVV) Fails to Open | EPIX/RADS | 1 | 2906.5 | d | 155 | Beta | JNID/IL | 6.04e-05 | 0.000406 | 0.000516 | 0.00134 | 1.5 | 2910 | 3.3014 | 1998--2015 |  | 2016-12-20
|  | SVV-FTC-PWR-RCS | PZR Code Safety Relief (SVV) Fails to Close | EPIX/RADS | 1 | 2906.5 | d | 155 | Beta | JNID/IL | 6.04e-05 | 0.000406 | 0.000516 | 0.00134 | 1.5 | 2910 | 3.3014 | 1998--2015 |  | 2016-12-20
|  | SVV-SOP-PWR-RCS | Safety valve spurious operation (reactor coolant system) | EPIX/RADS | 3 | 29547930 | h | 224 | Gamma | JNID/IL | 3.67e-08 | 1.08e-07 | 1.18e-07 | 2.38e-07 | 3.5 | 29500000 | 2.2168 | 1998--2015 |  | 2016-12-20
| Power-Operated Relief Valve (PORV) | PORV-FTO-PPR | PZR Power Operated Relief/Dump Valve Fails To Open | EPIX/RADS | 16 | 6129.6 | d | 114 | Beta | EB/PL/KS | 2.05e-05 | 0.0016 | 0.00324 | 0.012 | 0.55 | 170 | 7.4949 | 1998--2015 |  | 2016-12-20
|  | PRV-CC-PZR | PZR Power Operated Relief/Dump Valve Fails To Open | EPIX/RADS | 16 | 6129.6 | d | 114 | Beta | EB/PL/KS | 2.05e-05 | 0.0016 | 0.00324 | 0.012 | 0.55 | 170 | 7.4949 | 1998--2015 |  | 2016-12-20
|  | PORV-FTC-PPR | PZR One PORV/SRV Fails To Reclose | EPIX/RADS | 4 | 6129.6 | d | 114 | Beta | JNID/IL | 0.000271 | 0.00068 | 0.000734 | 0.00138 | 4.5 | 6130 | 2.0273 | 1998--2015 |  | 2016-12-20
|  | PORV-FTO-MSS | Main Steam Power Operated Relief/Dump Valve Fails To Open | EPIX/RADS | 42 | 10401 | d | 111 | Beta | EB/PL/KS | 0.000408 | 0.00367 | 0.00491 | 0.0136 | 1.24 | 252 | 3.6982 | 1998--2015 |  | 2016-12-20
|  | ARV-OO-MSS | Main Steam Power Operated Relief/Dump Fails to Close | EPIX/RADS | 19 | 10401 | d | 111 | Beta | EB/PL/KS | 8.6e-06 | 0.001 | 0.00221 | 0.00846 | 0.499 | 226 | 8.4334 | 1998--2015 |  | 2016-12-20
|  | PORV-FTC-MSS | Main Steam Power Operated Relief/Dump Fails to Close | EPIX/RADS | 19 | 10401 | d | 111 | Beta | EB/PL/KS | 8.6e-06 | 0.001 | 0.00221 | 0.00846 | 0.499 | 226 | 8.4334 | 1998--2015 |  | 2016-12-20
|  | PORV-FC-MSS | Main Steam Power Operated Relief Fails To Control (Cooldown) | EPIX/RADS | 13 | 49398360 | d | 317 | Gamma | EB/PL/KS | 4.91e-10 | 1.04e-07 | 2.57e-07 | 1.03e-06 | 0.44 | 1710000 | 9.985 | 1998--2015 |  | 2016-12-20
|  | ARV-CC-MSS | Main Steam Power Operated Relief/Dump Valve Fails To Open | EPIX/RADS | 42 | 10401 | d | 111 | Beta | EB/PL/KS | 0.000408 | 0.00367 | 0.00491 | 0.0136 | 1.24 | 252 | 3.6982 | 1998--2015 |  | 2016-12-20
|  | PORV-FC | Main Steam Power Operated Relief Fails To Control (Cooldown) | EPIX/RADS | 13 | 49398360 | d | 317 | Gamma | EB/PL/KS | 4.91e-10 | 1.04e-07 | 2.57e-07 | 1.03e-06 | 0.44 | 1710000 | 9.985 | 1998--2015 |  | 2016-12-20
|  | PORV-SOP | Power Operated Relief Spurious Opening | EPIX/RADS | 24 | 69470980 | h | 448 | Gamma | JNID/IL | 2.44e-07 | 3.48e-07 | 3.53e-07 | 4.77e-07 | 24.5 | 69500000 | 1.3725 | 1998--2015 |  | 2016-12-20
|  | PORV-ILS | Power Operated Relief Internal Leakage (Small) | EPIX/RADS | 18 | 69470980 | h | 448 | Gamma | JNID/IL | 1.73e-07 | 2.61e-07 | 2.66e-07 | 3.75e-07 | 18.5 | 69500000 | 1.4364 | 1998--2015 |  | 2016-12-20
|  | PORV-ILL | Power Operated Relief Internal Leakage (Rupture) | EPIX/RADS | 18 | 69470980 | h | 448 | Gamma | JNID/IL | 5.69e-13 | 1.3e-09 | 5.32e-09 | 2.43e-08 | 0.3 | 56391000 | 18.7656 | 1998--2015 | PORV leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | PORV-ELS | Power Operated Relief External Leakage (Small) | EPIX/RADS | 0 | 69470980 | h | 448 | Gamma | JNID/IL | 2.83e-11 | 3.27e-09 | 7.2e-09 | 2.76e-08 | 0.5 | 69500000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | PORV-ELL | Power Operated Relief External Leakage (Rupture) | EPIX/RADS | 0 | 69470980 | h | 448 | Gamma | JNID/IL | 5.39e-14 | 1.23e-10 | 5.04e-10 | 2.31e-09 | 0.3 | 595238000 | 18.7656 | 1998--2015 | PORV leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | PORV-L | PORVs/SRVs Open During LOOP | Special Calc |  |  | d | 0 | Point Estimate | MLE |  |  | 0.148 | [6 empty] | 2011-11-02
|  | PORV-T | PORVs/SRVs Open During Transient | Special Calc |  |  | d | 0 | Point Estimate | MLE |  |  | 0.0355 | [6 empty] | 2011-11-02
|  | PORV-Lquid | PORVs Fail To Close After Passing Liquid | Special Calc | 0 | 7 | d | 0 | Beta | JNID/IL | 6.45e-05 | 0.0246 | 0.0625 | 0.254 | 0.393 | 5.895 | 10.3137 |  |  | 2011-11-02
|  | PORV-P1 | PWR One PORV/SRV Sticks Open | Special Calc | 18 | 13897 | d | 0 | Beta | JNID/IL | 0.000261 | 0.00123 | 0.00146 | 0.00346 | 2.009 | 1374.02 | 2.817 |  |  | 2011-11-02
| Low-Capacity Relief Valve (RVL) | RVL-FTO | Low Capacity Relief Valve Fails to Close | EPIX/RADS | 5 | 77.9 | d | 12 | Beta | EB/PL/KS | 0.000167 | 0.0478 | 0.107 | 0.414 | 0.413 | 3.45 | 8.644 | 1998--2015 |  | 2016-12-20
|  | RVL-FTC | Low Capacity Relief Valve Fails To Open | EPIX/RADS | 0 | 77.9 | d | 12 | Beta | JNID/IL | 2.52e-05 | 0.00291 | 0.00634 | 0.0243 | 0.5 | 78.4 | 8.3531 | 1998--2015 |  | 2016-12-20
|  | RVL-SO | Low Capacity Relief Valve Spurious Operation | EPIX/RADS | 0 | 9633048 | h | 81 | Gamma | JNID/IL | 2.04e-10 | 2.36e-08 | 5.19e-08 | 1.99e-07 | 0.5 | 9630000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | RVL-ILS | Low Capacity Relief Valve Internal Leakage (Small) | EPIX/RADS | 11 | 9633048 | h | 81 | Gamma | JNID/IL | 6.8e-07 | 1.16e-06 | 1.19e-06 | 1.83e-06 | 11.5 | 9630000 | 1.5746 | 1998--2015 |  | 2016-12-20
|  | RVL-ILL | Low Capacity Relief Valve Internal Leakage (Rupture) | EPIX/RADS | 11 | 9633048 | h | 81 | Gamma | JNID/IL | 2.55e-12 | 5.8e-09 | 2.38e-08 | 1.09e-07 | 0.3 | 12605000 | 18.7656 | 1998--2015 | RVL leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | RVL-ELS | Low Capacity Relief Valve External Leakage (Small) | EPIX/RADS | 2 | 9633048 | h | 81 | Gamma | JNID/IL | 5.95e-08 | 2.26e-07 | 2.6e-07 | 5.75e-07 | 2.5 | 9630000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | RVL-ELL | Low Capacity Relief Valve External Leakage (Rupture) | EPIX/RADS | 2 | 9633048 | h | 81 | Gamma | JNID/IL | 1.95e-12 | 4.44e-09 | 1.82e-08 | 8.33e-08 | 0.3 | 16483500 | 18.7656 | 1998--2015 | RVL leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
Electrical Equipment | Battery Charger (BCH) | BCH-FTOP | Battery Charger Fails to Operate | EPIX/RADS | 294 | 120676300 | h | 790 | Gamma | EB/PL/KS | 2.67e-07 | 2e-06 | 2.59e-06 | 6.93e-06 | 1.39 | 536000 | 3.4572 | 1998--2015 |  | 2016-12-20
| Battery (BAT) | BAT-FTOP | Battery Fails to Operate | EPIX/RADS | 23 | 63157740 | h | 415 | Gamma | JNID/IL | 2.55e-07 | 3.67e-07 | 3.72e-07 | 5.06e-07 | 23.5 | 63200000 | 1.3813 | 1998--2015 |  | 2016-12-20
| Automatic Bus Transfer Switch (ABT) | ABT-FF | Automatic Power Transfer Switch Fails To Transfer | EPIX/RADS | 4 | 3976.2 | d | 27 | Beta | JNID/IL | 0.000419 | 0.00105 | 0.00113 | 0.00213 | 4.5 | 3970 | 2.0269 | 1998--2015 |  | 2016-12-20
|  | ABT-SO | Automatic Power Transfer Switch Transfers Open | EPIX/RADS | 0 | 5048822 | h | 32 | Gamma | JNID/IL | 3.89e-10 | 4.5e-08 | 9.9e-08 | 3.8e-07 | 0.5 | 5050000 | 8.4439 | 1998--2015 |  | 2016-12-20
| Circuit Breaker (CBK) | CBK-FTOC | Circuit Breaker Fails To Open/Close | EPIX/RADS | 154 | 141621 | d | 3512 | Beta | EB/PL/KS | 4.77e-05 | 0.00126 | 0.00207 | 0.00685 | 0.758 | 365 | 5.415 | 1998--2015 |  | 2016-12-20
|  | CBK-SOP | Circuit Breaker (All Voltages) Transfers Open | EPIX/RADS | 77 | 690765200 | h | 4609 | Gamma | EB/PL/KS | 2.06e-09 | 9.01e-08 | 1.63e-07 | 5.72e-07 | 0.644 | 3950000 | 6.3503 | 1998--2015 |  | 2016-12-20
|  | CBKHV-FTOC | High Voltage (13.8 and 16 Kv) Circuit Breaker Fails To Open/Close | EPIX/RADS | 21 | 11066 | d | 258 | Beta | EB/PL/KS | 3.93e-05 | 0.00159 | 0.00283 | 0.00984 | 0.659 | 232 | 6.1786 | 1998--2015 |  | 2016-12-20
|  | CBKHV-SOP | High Voltage (13.8 and 16 Kv) Circuit Breaker Spurious Operation | EPIX/RADS | 17 | 43105710 | h | 298 | Gamma | EB/PL/KS | 1.67e-09 | 2.15e-07 | 4.83e-07 | 1.87e-06 | 0.488 | 1010000 | 8.7055 | 1998--2015 |  | 2016-12-20
|  | CBKMV-FTOC | Medium Voltage (4160 v and 6.9 Kv) Circuit Breaker Fails To Open/Close | EPIX/RADS | 72 | 60179 | d | 1093 | Beta | EB/PL/KS | 3.15e-05 | 0.00138 | 0.00249 | 0.00872 | 0.644 | 258 | 6.327 | 1998--2015 |  | 2016-12-20
|  | CBKMV-SOP | Medium Voltage (4160 v and 6.9 Kv) Circuit Breaker Spurious Operation | EPIX/RADS | 19 | 184867300 | h | 1245 | Gamma | EB/PL/KS | 2.8e-10 | 4.81e-08 | 1.15e-07 | 4.53e-07 | 0.459 | 4010000 | 9.4277 | 1998--2015 |  | 2016-12-20
|  | CRB-FTOC-480 | Low Voltage (480 v) Circuit Breaker Fails To Open/Close | EPIX/RADS | 56 | 55060.3 | d | 1776 | Beta | JNID/IL | 0.000813 | 0.00102 | 0.00103 | 0.00126 | 56.5 | 55000 | 1.2356 | 1998--2015 |  | 2016-12-20
|  | CRB-CO-480 | Low Voltage (480 v) Circuit Breaker Spurious Operation | EPIX/RADS | 39 | 396295000 | h | 2629 | Gamma | JNID/IL | 7.52e-08 | 9.89e-08 | 9.97e-08 | 1.27e-07 | 39.5 | 396000000 | 1.2861 | 1998--2015 |  | 2016-12-20
|  | CBKDC-FTOC | DC Circuit Breaker Fails to Open/Close | EPIX/RADS | 2 | 5777.3 | d | 217 | Beta | JNID/IL | 9.91e-05 | 0.000376 | 0.000433 | 0.000957 | 2.5 | 5780 | 2.5433 | 1998--2015 |  | 2016-12-20
|  | CBKDC-SOP | DC Circuit Breaker Spurious Operation | EPIX/RADS | 1 | 42345960 | h | 271 | Gamma | JNID/IL | 4.16e-09 | 2.8e-08 | 3.54e-08 | 9.24e-08 | 1.5 | 42300000 | 3.303 | 1998--2015 |  | 2016-12-20
| Inverter (INV) | INV-FTOP | Inverter Fails to Operate | EPIX/RADS | 92 | 30051790 | h | 210 | Gamma | EB/PL/KS | 3.4e-07 | 3.61e-06 | 4.97e-06 | 1.43e-05 | 1.13 | 227000 | 3.9571 | 1998--2015 |  | 2016-12-20
| Bus (BUS) | BUS-FTOP-AC | AC Bus Fails to Operate | EPIX/RADS | 129 | 198241600 | h | 1352 | Gamma | EB/PL/KS | 6.1e-08 | 6.81e-07 | 9.55e-07 | 2.75e-06 | 1.1 | 1160000 | 4.0323 | 1998--2015 |  | 2016-12-20
|  | BUS-FTOP-DC | DC Bus Fails to Operate | EPIX/RADS | 0 | 2305320 | h | 15 | Gamma | JNID/IL | 8.51e-10 | 9.85e-08 | 2.17e-07 | 8.31e-07 | 0.5 | 2310000 | 8.4439 | 1998--2015 |  | 2016-12-20
| Motor Control Center (MCC) | MCC-FTOP | Motor Control Center Fail to Operate | EPIX/RADS | 6 | 34080880 | h | 217 | Gamma | JNID/IL | 8.64e-08 | 1.81e-07 | 1.91e-07 | 3.28e-07 | 6.5 | 34100000 | 1.8122 | 1998--2018 |  | 2016-12-20
| Transformer (TFM) | TFM-FTOP | Transformer Fail to Operate | EPIX/RADS | 185 | 71234060 | h | 506 | Gamma | EB/PL/KS | 6.33e-07 | 2.5e-06 | 2.89e-06 | 6.47e-06 | 2.4 | 832000 | 2.5912 | 1998--2015 |  | 2016-12-20
| Sequencer (SEQ) | SEQ | Sequencer fails to operate (as a Sub Component of the EDG) | EPIX/RADS | 8 | 65993.2 | d | 232 | Gamma | EB/PL/KS | 1.37e-06 | 6.51e-05 | 0.00012 | 0.000424 | 0.628 | 5240 | 6.5169 | 1998--2015 |  | 2016-12-20
| Fuse | FUS-CO | Fuse Transfer to Open State | EPIX/RADS | 2 | 203224300 | h | 1289 | Gamma | JNID/IL | 2.82e-09 | 1.07e-08 | 1.23e-08 | 2.73e-08 | 2.5 | 203000000 | 2.5441 | 1998--2015 |  | 2016-12-20
Strainers/Filters | Filter (FLT) | STR-FLT-PG | Strainer Plugging (Dirty water systems) | EPIX/RADS | 10 | 9300024 | h | 59 | Gamma | JNID/IL | 6.23e-07 | 1.09e-06 | 1.13e-06 | 1.76e-06 | 10.5 | 9300000 | 1.6064 | 1998--2015 |  | 2016-12-20
|  | STR-FLT-ELS | Filter External Leakage (Small) All Systems | EPIX/RADS | 3 | 33686420 | h | 220 | Gamma | JNID/IL | 3.22e-08 | 9.42e-08 | 1.04e-07 | 2.09e-07 | 3.5 | 33700000 | 2.2168 | 1998--2015 |  | 2016-12-20
|  | STR-FLT-ELL | Filter External Leakage (Small) All Systems | EPIX/RADS | 3 | 33686420 | h | 220 | Gamma | JNID/IL | 7.79e-13 | 1.77e-09 | 7.28e-09 | 3.33e-08 | 0.3 | 41208800 | 18.7656 | 1998--2015 | STR leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | STR-FLT-CLEAN-PG | Filter Plugging, Clean Systems | EPIX/RADS | 2 | 10115010 | h | 68 | Gamma | JNID/IL | 5.67e-08 | 2.15e-07 | 2.47e-07 | 5.48e-07 | 2.5 | 10100000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | STR-FLT-CLEAN-BYP | Clean Systems Passive Filter Bypass | EPIX/RADS | 0 | 10115010 | h | 68 | Gamma | JNID/IL | 1.95e-10 | 2.25e-08 | 4.94e-08 | 1.9e-07 | 0.5 | 10100000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | IAS-FLT-PG | Instrument Air System Filter Plugs | EPIX/RADS | 0 | 122688 | h | 2 | Gamma | JNID/IL | 1.6e-08 | 1.85e-06 | 4.08e-06 | 1.56e-05 | 0.5 | 123000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | IAS-FLT-FC | Instrument Air System Filter Fails | EPIX/RADS | 0 | 122688 | h | 2 | Gamma | JNID/IL | 1.6e-08 | 1.85e-06 | 4.08e-06 | 1.56e-05 | 0.5 | 123000 | 8.4439 | 1998--2015 |  | 2016-12-20
| Self-Cleaning Strainer (FLTSC) | STR-FLTSC-PG | Self Cleaning Filter Plugging | EPIX/RADS | 55 | 25738850 | h | 166 | Gamma | JNID/IL | 1.71e-06 | 2.15e-06 | 2.16e-06 | 2.66e-06 | 55.5 | 25700000 | 1.238 | 1998--2015 |  | 2016-12-20
|  | STR-FLTSC-BYP | Self Cleaning Filter Bypass | EPIX/RADS | 1 | 25738850 | h | 166 | Gamma | JNID/IL | 6.85e-09 | 4.6e-08 | 5.83e-08 | 1.52e-07 | 1.5 | 25700000 | 3.303 | 1998--2015 |  | 2016-12-20
|  | STR-FLTSC-FTOP | Self Cleaning Filter Fails to Operate | EPIX/RADS | 91 | 25738850 | h | 166 | Gamma | JNID/IL | 2.97e-06 | 3.55e-06 | 3.55e-06 | 4.19e-06 | 91.5 | 25700000 | 1.1822 | 1998--2015 |  | 2016-12-20
|  | STR-FLTSC-ELS | Self Cleaning Filter External Leakage (Small) | EPIX/RADS | 14 | 25738850 | h | 166 | Gamma | JNID/IL | 3.45e-07 | 5.51e-07 | 5.63e-07 | 8.28e-07 | 14.5 | 25700000 | 1.5019 | 1998--2015 |  | 2016-12-20
|  | STR-FLTSC-ELL | Self Cleaning Filter External Leakage (Rupture) | EPIX/RADS | 14 | 25738850 | h | 166 | Gamma | JNID/IL | 4.22e-12 | 9.61e-09 | 3.94e-08 | 1.8e-07 | 0.3 | 7612280 | 18.7656 | 1998--2015 | STR leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | STR-PE-SWS | Strainer Plugging (Dirty water systems), Environmental | EPIX/RADS | 1 | 9198527 | h | 59 | Gamma | JNID/IL | 1.91e-08 | 1.29e-07 | 1.63e-07 | 4.25e-07 | 1.5 | 9200000 | 3.303 | 1998--2015 |  | 2016-12-20
|  | STR-PG-NE-SWS | Strainer Plugging (Dirty water systems), Non-Environmental | EPIX/RADS | 35 | 25738850 | h | 166 | Gamma | JNID/IL | 1.02e-06 | 1.37e-06 | 1.38e-06 | 1.78e-06 | 35.5 | 25700000 | 1.3033 | 1998--2015 |  | 2016-12-20
|  | SWS-STR-PG | Standby Service Water Strainer Plugs | EPIX/RADS | 13 | 9198527 | h | 59 | Gamma | JNID/IL | 8.78e-07 | 1.43e-06 | 1.47e-06 | 2.18e-06 | 13.5 | 9200000 | 1.5231 | 1998--2015 |  | 2016-12-20
|  | NSW-STR-PG | Nuclear Service Water Strainer Plugs | EPIX/RADS | 42 | 15944260 | h | 103 | Gamma | JNID/IL | 2.04e-06 | 2.65e-06 | 2.67e-06 | 3.38e-06 | 42.5 | 15900000 | 1.2749 | 1998--2015 |  | 2016-12-20
| Sump Strainer (SMP) | SMP-PG | Containment Sump Plugging (pooled BWR and PWR) | EPIX/RADS | 1 | 14682020 | h | 95 | Gamma | JNID/IL | 1.2e-08 | 8.05e-08 | 1.02e-07 | 2.66e-07 | 1.5 | 14700000 | 3.303 | 1998--2015 |  | 2016-12-20
|  | STR-SUMP-PG | Containment Sump Plugging (pooled PWR and BWR) | EPIX/RADS | 4 | 14682020 | h | 95 | Gamma | JNID/IL | 1.13e-07 | 2.84e-07 | 3.06e-07 | 5.75e-07 | 4.5 | 14700000 | 2.028 | 1998--2015 |  | 2016-12-20
|  | BWR-RHR-SUMP-PG | Containment Sump Plugging (BWRs, suppression pool strainers) | EPIX/RADS | 0 | 6565272 | h | 42 | Gamma | JNID/IL | 2.99e-10 | 3.46e-08 | 7.62e-08 | 2.92e-07 | 0.5 | 6570000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | SMP-PG-PWR | Containment Sump Plugging (PWRs) | EPIX/RADS | 1 | 4382688 | h | 29 | Gamma | JNID/IL | 4.02e-08 | 2.7e-07 | 3.42e-07 | 8.92e-07 | 1.5 | 4380000 | 3.303 | 1998--2015 |  | 2016-12-20
| Traveling Screen Assembly (TSA) | TSA-FS | Traveling Screen Fails To Start | EPIX/RADS | 97 | 30417290 | d | 212 | Gamma | EB/PL/KS | 3.3e-08 | 1.92e-06 | 3.67e-06 | 1.32e-05 | 0.594 | 162000 | 6.9134 | 1998--2015 |  | 2016-12-20
|  | TSA-PG | Traveling Screen Plugging | EPIX/RADS | 68 | 30417290 | h | 212 | Gamma | EB/PL/KS | 6.77e-09 | 1.08e-06 | 2.53e-06 | 9.98e-06 | 0.466 | 184000 | 9.2403 | 1998--2015 |  | 2016-12-20
|  | TSA-BYP | Traveling Screen Bypass | EPIX/RADS | 8 | 30417290 | h | 212 | Gamma | JNID/IL | 1.43e-07 | 2.69e-07 | 2.79e-07 | 4.54e-07 | 8.5 | 30400000 | 1.6885 | 1998--2015 |  | 2016-12-20
|  | TSA-FR | Traveling Screen Fails To Run | EPIX/RADS | 97 | 30417290 | h | 212 | Gamma | EB/PL/KS | 3.3e-08 | 1.92e-06 | 3.67e-06 | 1.32e-05 | 0.594 | 162000 | 6.9134 | 1998--2015 |  | 2016-12-20
|  | TSA-FTOP | Traveling Screen Fails to Operate | EPIX/RADS | 97 | 30417290 | h | 212 | Gamma | EB/PL/KS | 3.3e-08 | 1.92e-06 | 3.67e-06 | 1.32e-05 | 0.594 | 162000 | 6.9134 | 1998--2015 |  | 2016-12-20
|  | TSA-PG-NE-SWS | Traveling Screens Plug Nonenvironmental (hr-1) | EPIX/RADS | 0 | 2331600 | h | 15 | Gamma | JNID/IL | 8.44e-10 | 9.76e-08 | 2.14e-07 | 8.24e-07 | 0.5 | 2330000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | SWS-TSA-PG | Standby Service Water Traveling Screen Plugs | EPIX/RADS | 0 | 2331600 | h | 15 | Gamma | JNID/IL | 8.44e-10 | 9.76e-08 | 2.14e-07 | 8.24e-07 | 0.5 | 2330000 | 8.4439 | 1998--2015 |  | 2016-12-20
| Trash Rack (TRK) | TRK-PG | Trash Rack Plugging | EPIX/RADS | 3 | 1577760 | h | 10 | Gamma | EB/PL/KS | 2.05e-08 | 1.17e-06 | 2.23e-06 | 8.03e-06 | 0.597 | 268000 | 6.8758 | 1998--2015 |  | 2016-12-20
RPS | Bistable (BIS) | BIS FTOP | Bistable Fail to Operate | RPS SSs | 55 | 102094 | d |  | Beta | JNID/IL | 2.14e-06 | 0.000247 | 0.000544 | 0.00209 | 0.5 | 919.266 | 8.4362 |  |  | 2007-02-01
| Process Logic Components | PLF FTOP | Process Logic (Flow) Fail to Operate | RPS SSs | 3 | 6075 | d |  | Beta | JNID/IL | 2.46e-06 | 0.000285 | 0.000625 | 0.0024 | 0.5 | 798.974 | 8.435 |  | The PLL data was used to estimate the flow process logic reliability. | 2007-02-01
|  | PLL FTOP | Process Logic (Level) Fail to Operate | RPS SSs | 3 | 6075 | d |  | Beta | JNID/IL | 2.46e-06 | 0.000285 | 0.000625 | 0.0024 | 0.5 | 798.974 | 8.435 |  |  | 2007-02-01
|  | PLP FTOP | Process Logic (Pressure) Fail to Operate | RPS SSs | 6 | 38115 | d |  | Beta | JNID/IL | 6.29e-07 | 7.28e-05 | 0.00016 | 0.000615 | 0.5 | 3123.76 | 8.4417 |  |  | 2007-02-01
|  | PLDT FTOP | Process Logic (Delta Temperature) Fail to Operate | RPS SSs | 24 | 4887 | d |  | Beta | JNID/IL | 2.01e-05 | 0.00232 | 0.00507 | 0.0194 | 0.5 | 98.0484 | 8.3713 |  | The PLL data was used to estimate the flow process logic reliability. | 2007-02-01
| Sensor/Transmitter Components | STF FTOP-D | Sensor/Transmitter (Flow) Fail to Operate on Demand | RPS SSs | 5 | 6750 | d |  | Beta | JNID/IL | 3.21e-06 | 0.000371 | 0.000815 | 0.00313 | 0.5 | 613.227 | 8.4323 |  | The STL data was used to estimate the flow senser/transmitter reliability. | 2007-02-01
|  | STF FTOP-R | Sensor/Transmitter (Flow) Fail to Operate per Hour | RPS SSs | 0 | 9831970 | h |  | Gamma | JNID/IL | 4e-10 | 4.63e-08 | 1.02e-07 | 3.91e-07 | 0.5 | 4915980 | 8.4439 |  |  | 2007-02-01
|  | STL FTOP-D | Sensor/Transmitter (Level) Fail to Operate on Demand | RPS SSs | 5 | 6750 | d |  | Beta | JNID/IL | 3.21e-06 | 0.000371 | 0.000815 | 0.00313 | 0.5 | 613.227 | 8.4323 |  |  | 2007-02-01
|  | STL FTOP-R | Sensor/Transmitter (Level) Fail to Operate per Hour | RPS SSs | 0 | 9831970 | h |  | Gamma | JNID/IL | 4e-10 | 4.63e-08 | 1.02e-07 | 3.91e-07 | 0.5 | 4915980 | 8.4439 |  |  | 2007-02-01
|  | STP FTOP-D | Sensor/Transmitter (Pressure) Fail to Operate on Demand | RPS SSs | 2 | 23960 | d |  | Beta | JNID/IL | 4.6e-07 | 5.32e-05 | 0.000117 | 0.000449 | 0.5 | 4278.25 | 8.4423 |  |  | 2007-02-01
|  | STP FTOP-R | Sensor/Transmitter (Pressure) Fail to Operate per Hour | RPS SSs | 35 | 43430500 | h |  | Gamma | JNID/IL | 3.23e-09 | 3.74e-07 | 8.22e-07 | 3.16e-06 | 0.5 | 608270 | 8.4439 |  |  | 2007-02-01
|  | STT FTOP-D | Sensor/Transmitter (Temperature) Fail to Operate on Demand | RPS SSs | 17 | 40759 | d |  | Beta | JNID/IL | 1.7e-06 | 0.000197 | 0.000432 | 0.00166 | 0.5 | 1157.45 | 8.4378 |  | The STL data was used to estimate the flow senser/transmitter reliability. | 2007-02-01
|  | STT FTOP-R | Sensor/Transmitter (Temperature) Fail to Operate per Hour | RPS SSs | 29 | 35107400 | h |  | Gamma | JNID/IL | 3.3e-09 | 3.82e-07 | 8.4e-07 | 3.23e-06 | 0.5 | 595041 | 8.4439 |  |  | 2007-02-01
| Reactor Trip Breaker (RTB) | RTB (BME) FTO/C | RPS Breaker (Mechanical) Fail to Open or Close | RPS SSs | 1 | 97359 | d |  | Beta | JNID/IL | 6.06e-08 | 7.01e-06 | 1.54e-05 | 5.92e-05 | 0.5 | 32452.5 | 8.4437 |  |  | 2007-02-01
|  | RTB (BSN) FTOP | RPS Breaker (Shunt Trip) Fail to Operate | RPS SSs | 14 | 44104 | d |  | Beta | JNID/IL | 1.29e-06 | 0.00015 | 0.000329 | 0.00126 | 0.5 | 1520.33 | 8.4392 |  |  | 2007-02-01
|  | RTB (BUV) FTOP | RPS Breaker (Undervoltage Trip) Fail to Operate | RPS SSs | 23 | 57199 | d |  | Beta | JNID/IL | 1.62e-06 | 0.000188 | 0.000413 | 0.00158 | 0.5 | 1211.34 | 8.438 |  |  | 2007-02-01
|  | RTB FTO/C | RPS Breaker (Combined) Fail to Open or Close | RPS SSs |  |  | d |  | Beta | JNID/IL | 6.11e-08 | 7.07e-06 | 1.55e-05 | 5.97e-05 | 0.5 | 32169.3 | 8.4437 |  |  | 2007-02-01
| Manual Switch (MSW) | MSW FTO/C | Manual Switch Fail to Open or Close | RPS SSs | 2 | 19789 | d |  | Beta | JNID/IL | 4.97e-07 | 5.75e-05 | 0.000126 | 0.000485 | 0.5 | 3957.5 | 8.4421 |  |  | 2007-02-01
| Relay (RLY) | RLY FTOP | Relay Fail to Operate | RPS SSs | 24 | 974417 | d |  | Beta | JNID/IL | 9.77e-08 | 1.13e-05 | 2.48e-05 | 9.54e-05 | 0.5 | 20132.1 | 8.4436 |  |  | 2007-02-01
Control Rods | Control Rod Drive (CRD) | CRD-FTOP | Control Rod Fail to Insert Rod | EPIX/RADS | 18 | 183267700 | d | 1201 | Gamma | EB/PL/KS | 1.62e-10 | 4.4e-08 | 1.15e-07 | 4.71e-07 | 0.419 | 3640000 | 10.6992 | 1998--2015 |  | 2016-12-20
|  | CRD-SOP | Control Rod Drive Spurious Operation | EPIX/RADS | 34 | 183267700 | h | 1201 | Gamma | JNID/IL | 1.39e-07 | 1.87e-07 | 1.88e-07 | 2.44e-07 | 34.5 | 183000000 | 1.3081 | 1998--2015 |  | 2016-12-20
| Control Rod (ROD) | ROD-FTOP | Control Rod Fails to Operate/ Insert Rod | EPIX/RADS | 20 | 132832800 | d | 846 | Gamma | JNID/IL | 1.03e-07 | 1.52e-07 | 1.54e-07 | 2.14e-07 | 20.5 | 133000000 | 1.4117 | 1998--2015 |  | 2016-12-20
|  | ROD-SOP | Control Rod Spurious Operation | EPIX/RADS | 20 | 132832800 | h | 846 | Gamma | JNID/IL | 1.03e-07 | 1.52e-07 | 1.54e-07 | 2.14e-07 | 20.5 | 133000000 | 1.4117 | 1998--2015 |  | 2016-12-20
| Hydraulic Control Unit (HCU) | HCU-FTI | Hydraulic Control Unit Fails to Insert | EPIX/RADS | 0 | 0 | d | 0 | -- | -- | -- |  | -- | -- | -- | -- |  | 1998--2015 |  | 2016-12-20
|  | HCU-FTOP | Hydraulic Control Unit Fails to Operate | EPIX/RADS | 29 | 1625902000 | h | 10436 | Gamma | EB/PL/KS | 1.16e-09 | 1.3e-08 | 1.81e-08 | 5.23e-08 | 1.1 | 60900000 | 4.0323 | 1998--2015 |  | 2016-12-20
|  | HCU-SOP | Hydraulic Control Unit Spurious Operation | EPIX/RADS | 35 | 1625902000 | h | 10436 | Gamma | EB/PL/KS | 6.01e-09 | 1.93e-08 | 2.16e-08 | 4.49e-08 | 3.08 | 143000000 | 2.3295 | 1998--2015 |  | 2016-12-20
Heating & Ventilation | Air Damper (DMP) | AOD-FTOC | Air-Operated Damper Fails To Open/Close | EPIX/RADS | 2 | 7799.1 | d | 49 | Beta | JNID/IL | 7.34e-05 | 0.000279 | 0.000321 | 0.000709 | 2.5 | 7800 | 2.5435 | 1998--2015 |  | 2016-12-20
|  | AOD-SOP | Air-Operated Damper Spurious Operation | EPIX/RADS | 3 | 31342830 | h | 209 | Gamma | JNID/IL | 3.46e-08 | 1.01e-07 | 1.12e-07 | 2.25e-07 | 3.5 | 31300000 | 2.2168 | 1998--2015 |  | 2016-12-20
|  | AOD-ILS | Air-Operated Damper Internal Leakage (Small) | EPIX/RADS | 5 | 31342830 | h | 209 | Gamma | JNID/IL | 7.31e-08 | 1.65e-07 | 1.75e-07 | 3.14e-07 | 5.5 | 31300000 | 1.9026 | 1998--2015 |  | 2016-12-20
|  | AOD-ILL | Air-Operated Damper Internal Leakage (Rupture) | EPIX/RADS | 5 | 31342830 | h | 209 | Gamma | JNID/IL | 3.75e-13 | 8.53e-10 | 3.5e-09 | 1.6e-08 | 0.3 | 85714300 | 18.7656 | 1998--2015 | DMP leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | HOD-FTOC | Hydraulic Operated Damper Fails To Open/Close | EPIX/RADS | 11 | 6225.1 | d | 39 | Beta | EB/PL/KS | 3.41e-05 | 0.00274 | 0.00557 | 0.0207 | 0.545 | 97.3 | 7.5452 | 1998--2015 |  | 2016-12-20
|  | HOD-SOP | Hydraulic Operated Damper Spurious Operation | EPIX/RADS | 8 | 19397950 | h | 128 | Gamma | JNID/IL | 2.23e-07 | 4.21e-07 | 4.38e-07 | 7.11e-07 | 8.5 | 19400000 | 1.6885 | 1998--2015 |  | 2016-12-20
|  | HOD-ILS | Hydraulic Operated Damper Internal Leakage (Small) | EPIX/RADS | 0 | 19397950 | h | 128 | Gamma | JNID/IL | 1.01e-10 | 1.17e-08 | 2.58e-08 | 9.9e-08 | 0.5 | 19400000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | HOD-ILL | Hydraulic Operated Damper Internal Leakage (Rupture) | EPIX/RADS | 0 | 19397950 | h | 128 | Gamma | JNID/IL | 5.52e-14 | 1.26e-10 | 5.16e-10 | 2.36e-09 | 0.3 | 581395000 | 18.7656 | 1998--2015 | DMP leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | MOD-FTOC | Motor Operated Damper Fails To Open | EPIX/RADS | 7 | 33254.2 | d | 45 | Beta | JNID/IL | 0.000109 | 0.000216 | 0.000226 | 0.000376 | 7.5 | 33200 | 1.7431 | 1998--2015 |  | 2016-12-20
|  | MOD-SOP | Motor Operated Damper Fails To Remain Open | EPIX/RADS | 0 | 17147900 | h | 111 | Gamma | JNID/IL | 1.15e-10 | 1.33e-08 | 2.92e-08 | 1.12e-07 | 0.5 | 17100000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | MOD-ILS | Motor Operated Damper Internal Leakage (Small) | EPIX/RADS | 1 | 17147900 | d | 111 | Gamma | JNID/IL | 1.03e-08 | 6.92e-08 | 8.75e-08 | 2.29e-07 | 1.5 | 17100000 | 3.303 | 1998--2015 |  | 2016-12-20
|  | MOD-ILL | Motor Operated Damper Internal Leakage (Rupture) | EPIX/RADS | 1 | 17147900 | h | 111 | Gamma | JNID/IL | 1.87e-13 | 4.27e-10 | 1.75e-09 | 8.01e-09 | 0.3 | 171429000 | 18.7656 | 1998--2015 | DMP leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
| Air Handling | AHU-NR-FTS | Air Handling/Heating Fan Fails To Start, Normally Running | EPIX/RADS | 45 | 17336.4 | d | 139 | Beta | EB/PL/KS | 7.32e-06 | 0.00118 | 0.00276 | 0.0109 | 0.465 | 168 | 9.2215 | 1998--2015 |  | 2016-12-20
|  | AHU-NR-FTR | Air Handling/Heating Unit Fails To Run, Normally Running | EPIX/RADS | 62 | 17498560 | h | 139 | Gamma | EB/PL/KS | 2.64e-08 | 3.03e-06 | 6.65e-06 | 2.55e-05 | 0.501 | 75300 | 8.423 | 1998--2015 |  | 2016-12-20
| Air Cooling | ACX-FTS | Air Handling/Heating Fan Fails To Start, Normally Running | EPIX/RADS | 45 | 17336.4 | d | 139 | Beta | EB/PL/KS | 7.32e-06 | 0.00118 | 0.00276 | 0.0109 | 0.465 | 168 | 9.2215 | 1998--2015 |  | 2016-12-20
|  | ACX-FTR | Air Handling/Heating Unit Fails To Run, Normally Running | EPIX/RADS | 62 | 21790640 | h | 139 | Gamma | EB/PL/KS | 5.8e-08 | 2.25e-06 | 3.98e-06 | 1.38e-05 | 0.668 | 168000 | 6.121 | 1998--2015 |  | 2016-12-20
|  | ACX-FTS-NS | Air Cooling Heat Exchanger Fails to Start, Normally Standby | EPIX/RADS | 55 | 149242.4 | d | 382 | Beta | EB/PL/KS | 3.06e-06 | 0.000268 | 0.000557 | 0.00209 | 0.534 | 958 | 7.7905 | 1998--2015 |  | 2016-12-20
|  | ACX-FTR<1H | Air Cooling Heat Exchanger Fails to Run <1H Normally Standby | EPIX/RADS | 0 | 148102.7 | h | 382 | Gamma | JNID/IL | 1.33e-08 | 1.54e-06 | 3.38e-06 | 1.3e-05 | 0.5 | 148000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | ACX-FTR>1H | Air Cooling Heat Exchanger Fails to Run >1H Normally Standby | EPIX/RADS | 45 | 10793680 | h | 382 | Gamma | JNID/IL | 3.24e-06 | 4.18e-06 | 4.22e-06 | 5.29e-06 | 45.5 | 10800000 | 1.2649 | 1998--2015 |  | 2016-12-20
| Chiller (CHL) | CHL-FTS | Chiller Unit Fails To Start, Normally Running | EPIX/RADS | 121 | 18215.1 | d | 80 | Beta | EB/PL/KS | 0.000135 | 0.00525 | 0.00921 | 0.0317 | 0.667 | 71.8 | 6.0481 | 1998--2015 |  | 2016-12-20
|  | CHL-FTR | Chiller Unit Fails To Run, Normally Running | EPIX/RADS | 349 | 6464949 | h | 80 | Gamma | EB/PL/KS | 4.19e-06 | 4.94e-05 | 6.93e-05 | 0.000203 | 1.07 | 15400 | 4.1125 | 1998--2015 |  | 2016-12-20
|  | CHL-FTS-NS | Chiller Unit Fails To Start, Normally Standby | EPIX/RADS | 0 | 20433.4 | d | 63 | Beta | JNID/IL | 9.64e-08 | 1.12e-05 | 2.45e-05 | 9.42e-05 | 0.5 | 20400 | 8.4436 | 1998--2015 |  | 2016-12-20
|  | CHL-FTR<1H | Chiller Unit Fails To Run <1H, Normally Standby | EPIX/RADS | 61 | 279348.3 | h | 63 | Gamma | JNID/IL | 0.000176 | 0.000219 | 0.00022 | 0.000269 | 61.5 | 279000 | 1.2252 | 1998--2015 |  | 2016-12-20
|  | CHL-FTR>1H | Chiller Unit Fails To Run >1H, Normally Standby | EPIX/RADS | 61 | 279348.3 | h | 63 | Gamma | JNID/IL | 0.000176 | 0.000219 | 0.00022 | 0.000269 | 61.5 | 279000 | 1.2252 | 1998--2015 |  | 2016-12-20
| Fan (FAN) | FAN-SBY-FTS | HVAC Fan Fails To Start, Normally Standby | EPIX/RADS | 37 | 57511.6 | d | 130 | Beta | JNID/IL | 0.000487 | 0.000646 | 0.000652 | 0.000836 | 37.5 | 57500 | 1.2943 | 1998--2015 |  | 2016-12-20
|  | FAN-SBY-FTR<1H | HVAC Fan Fails To Run, Early Term, Normally Standby | EPIX/RADS | 16 | 43743.8 | h | 130 | Gamma | JNID/IL | 0.000239 | 0.00037 | 0.000377 | 0.000542 | 16.5 | 43700 | 1.4659 | 1998--2015 |  | 2016-12-20
|  | FAN-SBY-FTR>1H | HVAC Fan Fails To Run, Late Term, Normally Standby | EPIX/RADS | 27 | 137892 | h | 130 | Gamma | JNID/IL | 0.000141 | 0.000197 | 0.000199 | 0.000266 | 27.5 | 138000 | 1.3493 | 1998--2015 |  | 2016-12-20
|  | FAN-NR-FTS | HVAC Fan Fails To Start, Normally Running | EPIX/RADS | 46 | 85577.4 | d | 218 | Beta | JNID/IL | 0.000419 | 0.00054 | 0.000543 | 0.000681 | 46.5 | 85500 | 1.2618 | 1998--2015 |  | 2016-12-20
|  | FAN-NR-FTR | HVAC Fan Fails To Run, Normally Running | EPIX/RADS | 67 | 17511120 | h | 218 | Gamma | EB/PL/KS | 3.07e-08 | 2.21e-06 | 4.41e-06 | 1.63e-05 | 0.561 | 127000 | 7.3655 | 1998--2015 |  | 2016-12-20
Miscellaneous Equipment | Air Compressor (CMP) | MDC-FTS | Motor Driven Compressor Fail To Start, Normally Running | EPIX/RADS | 109 | 9196.9 | d | 70 | Beta | EB/PL/KS | 0.000206 | 0.0172 | 0.0341 | 0.125 | 0.539 | 15.3 | 7.281 | 1998--2015 |  | 2016-12-20
|  | MDC-FTR | Motor Driven Compressor Fails To Run | EPIX/RADS | 307 | 5595966 | h | 70 | Gamma | EB/PL/KS | 1.2e-05 | 5.5e-05 | 6.51e-05 | 0.000153 | 2.06 | 31600 | 2.7854 | 1998--2015 |  | 2016-12-20
|  | MDC-FTS-NS | Motor Driven Compressor Fail To Start, Normally Standby | EPIX/RADS | 61 | 23363.4 | d | 58 | Beta | EB/PL/KS | 0.000358 | 0.00314 | 0.00416 | 0.0115 | 1.26 | 301 | 3.6627 | 1998--2015 |  | 2016-12-20
|  | MDC-FTR<1H | Motor Driven Compressor Fail To Run (0 To 1 Hour) | EPIX/RADS | 22 | 1683943 | h | 58 | Gamma | JNID/IL | 9.11e-06 | 1.32e-05 | 1.34e-05 | 1.84e-05 | 22.5 | 1680000 | 1.3907 | 1998--2015 |  | 2016-12-20
|  | MDC-FTR>1H | Motor Driven Compressor Fail To Run (> 1 Hour) | EPIX/RADS | 22 | 1683943 | h | 58 | Gamma | JNID/IL | 9.11e-06 | 1.32e-05 | 1.34e-05 | 1.84e-05 | 22.5 | 1680000 | 1.3907 | 1998--2015 |  | 2016-12-20
|  | EDC-FS-NS | Engine Driven Compressor Fails To Start, Normally Standby | EPIX/RADS | 17 | 2121.7 | d | 5 | Beta | JNID/IL | 0.00529 | 0.00807 | 0.00824 | 0.0117 | 17.5 | 2110 | 1.4478 | 1998--2015 |  | 2016-12-20
|  | EDC-FR-E | Engine Driven Compressor Fails To Run <1H, Normally Standby | EPIX/RADS | 0 | 2121.7 | h | 5 | Gamma | JNID/IL | 9.27e-07 | 0.000107 | 0.000236 | 0.000906 | 0.5 | 2120 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | EDC-FR-L | Engine Driven Compressor Fails To Run >1H, Normally Standby | EPIX/RADS | 0 | 1735.2 | h | 5 | Gamma | JNID/IL | 1.13e-06 | 0.000131 | 0.000288 | 0.0011 | 0.5 | 1740 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | IAS-MDC-FR | Instrument Air System Motor Driven Compressor Fails to Run | EPIX/RADS | 186 | 2680601 | h | 41 | Gamma | EB/PL/KS | 1.95e-05 | 6.64e-05 | 7.5e-05 | 0.00016 | 2.85 | 38000 | 2.4046 | 1998--2015 |  | 2016-12-20
|  | PCA-MDC-FR | PCA Motor Driven Compressor Fails to Run | EPIX/RADS | 3 | 118273 | h | 2 | Gamma | JNID/IL | 9.18e-06 | 2.69e-05 | 2.96e-05 | 5.96e-05 | 3.5 | 118000 | 2.2168 | 1998--2015 |  | 2016-12-20
| Air Drier Unit (ADU) | ADU-FTOP | Air dryer unit fails to operate | NUREG/CR-6928 |  |  | h |  | Gamma | JNID/IL | 5.35e-10 | 1.22e-06 | 5e-06 | 2.29e-05 | 0.3 | 60000 | 18.7656 |  |  | 2005-06-23
| Accumulator (ACC) | ACC-FTOP | Accumulator Fails to Operate | EPIX/RADS | 18 | 96227420 | h | 617 | Gamma | JNID/IL | 1.25e-07 | 1.89e-07 | 1.92e-07 | 2.71e-07 | 18.5 | 96200000 | 1.4364 | 1998--2015 |  | 2016-12-20
|  | ACC-ELS | Accumulator External Leakage (Small) | EPIX/RADS | 11 | 96227420 | h | 617 | Gamma | JNID/IL | 6.8e-08 | 1.16e-07 | 1.2e-07 | 1.83e-07 | 11.5 | 96200000 | 1.5746 | 1998--2015 |  | 2016-12-20
|  | ACC-ELL | Accumulator External Leakage (Rupture) | EPIX/RADS | 11 | 96227420 | h | 617 | Gamma | JNID/IL | 8.99e-13 | 2.05e-09 | 8.4e-09 | 3.84e-08 | 0.3 | 35714300 | 18.7656 | 1998--2015 | ACC leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Cooling Tower Fan (CTF) | CTF-STBY-FTS | Cooling Tower Fan Fails To Start (Standby) | EPIX/RADS | 16 | 44600.3 | d | 54 | Beta | JNID/IL | 0.000234 | 0.000362 | 0.00037 | 0.000531 | 16.5 | 44600 | 1.4657 | 1998--2015 |  | 2016-12-20
|  | CTF-STBY-FTR<1H | Cooling Tower Fan Fails To Run <1H (Standby) | EPIX/RADS | 0 | 44487.8 | h | 54 | Gamma | JNID/IL | 4.42e-08 | 5.11e-06 | 1.12e-05 | 4.32e-05 | 0.5 | 44500 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | CTF-STBY-FTR>1H | Cooling Tower Fan Fails To Run >1H (Standby) | EPIX/RADS | 2 | 1073115 | h | 54 | Gamma | JNID/IL | 5.35e-07 | 2.03e-06 | 2.33e-06 | 5.17e-06 | 2.5 | 1070000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | CTF-NR-FTS | Cooling Tower Fan Fails To Start | EPIX/RADS | 1 | 2687 | d | 20 | Beta | JNID/IL | 6.54e-05 | 0.00044 | 0.000558 | 0.00145 | 1.5 | 2690 | 3.3013 | 1998--2015 |  | 2016-12-20
|  | CTF-NR-FTR | Cooling Tower Fan Fails To Run | EPIX/RADS | 3 | 1504717 | h | 20 | Gamma | JNID/IL | 7.22e-07 | 2.12e-06 | 2.33e-06 | 4.69e-06 | 3.5 | 1500000 | 2.2168 | 1998--2015 |  | 2016-12-20
| Tank (TNK) | TNK-FC | Tank Rupture | EPIX/RADS | 15 | 59350270 | h | 379 | Gamma | JNID/IL | 1.62e-07 | 2.55e-07 | 2.61e-07 | 3.79e-07 | 15.5 | 59400000 | 1.4829 | 1998--2018 |  | 2016-12-20
|  | TNK-PRESS-LIQ-ELS | Pressurized Liquid Tank Small Leakage External Leakage (Small) | EPIX/RADS | 8 | 24349940 | h | 156 | Gamma | EB/PL/KS | 1.22e-09 | 1.49e-07 | 3.31e-07 | 1.28e-06 | 0.494 | 1490000 | 8.5723 | 1998--2015 |  | 2016-12-20
|  | TNK-PRESS-LIQ-ELL | Pressurized Liquid Tank Small Leakage External Leakage (Rupture) | EPIX/RADS | 8 | 24349940 | h | 156 | Gamma | EB/PL/KS | 2.48e-12 | 5.65e-09 | 2.32e-08 | 1.06e-07 | 0.3 | 12947800 | 18.7656 | 1998--2015 | TNK leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | TNK-UNPRESS-LIQ-ELS | Unpressurized Liquid Tank Small Leakage External Leakage (Small) | EPIX/RADS | 7 | 29235430 | h | 191 | Gamma | JNID/IL | 1.24e-07 | 2.46e-07 | 2.57e-07 | 4.28e-07 | 7.5 | 29200000 | 1.7432 | 1998--2015 |  | 2016-12-20
|  | TNK-UNPRESS-LIQ-ELL | Unpressurized Liquid Tank Small Leakage External Leakage (Rupture) | EPIX/RADS | 7 | 29235430 | h | 191 | Gamma | JNID/IL | 1.93e-12 | 4.39e-09 | 1.8e-08 | 8.23e-08 | 0.3 | 16675900 | 18.7656 | 1998--2015 | TNK leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
|  | SWS-TNK-FC | Standby Service Water Tank Fails to Control | EPIX/RADS | 0 | 1086910 | h | 7 | Gamma | JNID/IL | 1.8e-09 | 2.09e-07 | 4.6e-07 | 1.76e-06 | 0.5 | 1090000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | IAS-TNK-FC | Instrument Air System Tank Fails to Control | EPIX/RADS | 0 | 3944400 | h | 25 | Gamma | JNID/IL | 4.99e-10 | 5.77e-08 | 1.27e-07 | 4.87e-07 | 0.5 | 3940000 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | TNK-GAS-ELS | Gas Tank Small Leakage External Leakage (Small) | EPIX/RADS | 2 | 5048832 | h | 32 | Gamma | JNID/IL | 1.13e-07 | 4.31e-07 | 4.95e-07 | 1.1e-06 | 2.5 | 5050000 | 2.5441 | 1998--2015 |  | 2016-12-20
|  | TNK-GAS-ELL | Gas Tank Small Leakage External Leakage (Rupture) | EPIX/RADS | 2 | 5048832 | h | 32 | Gamma | JNID/IL | 3.71e-12 | 8.45e-09 | 3.47e-08 | 1.59e-07 | 0.3 | 8658010 | 18.7656 | 1998--2015 | TNK leak rate > 50 gpm. Small external leak times 0.07. | 2016-12-20
| Orifice (ORF) | ORF-PG | Orifice Plugging | WSRV |  |  | h |  | Gamma | JNID/IL | 1.07e-10 | 2.44e-07 | 1e-06 | 4.57e-06 | 0.3 | 300000 | 18.7656 |  |  | 2005-06-23
| Pipe (PIPE) | PIPE OTHER-ELS | Piping Non-Service Water System External Leak Small | EPIX | 4.5 | 15830000000 | h-ft |  | Gamma | JNID/IL | 9.94e-13 | 1.15e-10 | 2.53e-10 | 9.71e-10 | 0.5 | 1978750000 | 8.4439 |  |  | 2007-02-01
|  | PIPE OTHER-ELL | Piping Non-Service Water System External Leak Large | EPIX | 4.5 | 15830000000 | h-ft |  | Gamma | JNID/IL | 2.7e-15 | 6.16e-12 | 2.53e-11 | 1.16e-10 | 0.3 | 11872500000 | 18.7656 |  | Pipe leakage > 50 gpm, small leakage times 0.1. | 2007-02-01
|  | PIPE SWS-ELS | Piping Service Water System External Leak Small | EPIX | 8.5 | 13060000000 | h-ft |  | Gamma | JNID/IL | 2.71e-12 | 3.14e-10 | 6.89e-10 | 2.65e-09 | 0.5 | 725556000 | 8.4439 |  |  | 2007-02-01
|  | PIPE SWS-ELL | Piping Service Water System External Leak Large | EPIX | 8.5 | 13060000000 | h-ft |  | Gamma | JNID/IL | 1.48e-14 | 3.36e-11 | 1.38e-10 | 6.3e-10 | 0.3 | 2176670000 | 18.7656 |  | Pipe leakage > 50 gpm, small leakage times 0.2. | 2007-02-01
| Heat Exchanger (HTX) | HTX-LOHT | Heat Exchanger Plugging/Heat Transfer (Pooled) | EPIX/RADS | 87 | 269796800 | h | 1770 | Gamma | EB/PL/KS | 2.32e-09 | 1.88e-07 | 3.85e-07 | 1.44e-06 | 0.544 | 1410000 | 7.6302 | 1998--2015 |  | 2016-12-20
|  | HTX-ILS | Heat Exchanger Internal Leakage (Small) | EPIX/RADS | 98 | 269796800 | h | 1770 | Gamma | EB/PL/KS | 5.03e-10 | 1.42e-07 | 3.73e-07 | 1.54e-06 | 0.416 | 1110000 | 10.811 | 1998--2015 |  | 2016-12-20
|  | HTX-ILL | Heat Exchanger Internal Leakage (Rupture) | EPIX/RADS | 98 | 269796800 | h | 1770 | Gamma | EB/PL/KS | 7.98e-13 | 1.82e-09 | 7.46e-09 | 3.41e-08 | 0.3 | 40214500 | 18.7656 | 1998--2015 | HTX leak rate > 50 gpm. Small internal leak times 0.02. | 2016-12-20
|  | HTX-ELS | Heat Exchanger External Leakage (Small) | EPIX/RADS | 65 | 269796800 | h | 1770 | Gamma | EB/PL/KS | 9.77e-09 | 1.82e-07 | 2.79e-07 | 8.81e-07 | 0.867 | 3100000 | 4.8352 | 1998--2015 |  | 2016-12-20
|  | HTX-ELL | Heat Exchanger External Leakage (Rupture) | EPIX/RADS | 65 | 269796800 | h | 1770 | Gamma | EB/PL/KS | 4.48e-12 | 1.02e-08 | 4.19e-08 | 1.91e-07 | 0.3 | 7168460 | 18.7656 | 1998--2015 | HTX leak rate > 50 gpm. Small external leak times 0.15. | 2016-12-20
|  | HTX-PG-CCW | Heat Exchanger Plugging Non Standby | EPIX/RADS | 17 | 34265020 | h | 227 | Gamma | EB/PL/KS | 5.34e-10 | 1.92e-07 | 5.33e-07 | 2.22e-06 | 0.398 | 747000 | 11.5424 | 1998--2015 |  | 2016-12-20
|  | HTX-CCW-LOHT | CCW Heat Exchanger Fails to Control | EPIX/RADS | 17 | 34265020 | h | 227 | Gamma | EB/PL/KS | 5.34e-10 | 1.92e-07 | 5.33e-07 | 2.22e-06 | 0.398 | 747000 | 11.5424 | 1998--2015 |  | 2016-12-20
|  | HTX-PG-NE-CCW | CCW Heat Exchanger Plugging Non-ExEE (hr-1) | EPIX/RADS | 7 | 34265020 | h | 227 | Gamma | EB/PL/KS | 2.32e-10 | 7.56e-08 | 2.06e-07 | 8.51e-07 | 0.405 | 1970000 | 11.245 | 1998--2015 |  | 2016-12-20
| Instrumentation | ICC-FA | Failure of instrument and control for a turbine trip | NUCLARR |  |  | d |  | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 |  | 2.2 |  |  | 2005-06-23
|  | ICC-FC | Instrumentation and Control Circuit Fails | NUCLARR |  |  | d |  | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 |  | 2.2 |  |  | 2005-06-23
|  | ACT-FC | Automatic actuation and control circuit fails | NUCLARR |  |  | d |  | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 |  | 2.2 |  |  | 2011-12-08
Acronyms - BWR (boiling water reactor), EB/PL/KS (empirical Bayes/plant level/Kass Steffey), EPIX (Equipment Performance and Information Exchange), JNID/IL (Jeffreys noninformative distribution/industry level), LL (lower limit), PLL (process logic level), PWR (pressurized water reactor), SCNID (simplified constrained noninformative distribution), SS (system study), SWS (service water system), WSRC (Westinghouse Savannah River Company)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The error factor is from an empirical Bayes analysis at the plant level, with Kass-Steffey adjustment. The error factor is the 95th percentile divided by the median.

## IE Data
SPAR Initiating Event Data and Results
2015 Paramater Estimation Update
2016-12-21 12:00
Section | Sub Section | Initiating Event | Description | Data |  |  | Industry-average Frequency Distribution (note a) | [8 empty] | Baseline Period | Comments (see Appendix D for details) | Effective Date
|  |  |  | Source | Number of Events | Critical Years (rcry) | Distribution | Analysis Type | 5th | Median | Mean | 95th | α | β | Error Factor
Primary/Secondary Inventory Control | High Energy Line Breaks | FWLB BWR FI | Feedwater Line Break (BWR) | RADS | 0 | 833.7 | Gamma | JNID/IL | 2.36e-06 | 0.000273 | 0.0006 | 0.0023 | 0.5 | 834 | 8.4439 | 1988--2015 |  | 2016-12-20
|  | FWLB PWR FI | Feedwater Line Break (PWR) | RADS | 2 | 1662.6 | Gamma | JNID/IL | 0.000345 | 0.00131 | 0.0015 | 0.00333 | 2.5 | 1660 | 2.5441 | 1988--2015 |  | 2016-12-20
|  | SLBIC PWR FI | Steamline Break Inside Containment (PWRs) | RADS | 0 | 1662.6 | Gamma | JNID/IL | 1.18e-06 | 0.000137 | 0.000301 | 0.00116 | 0.5 | 1660 | 8.4439 | 1988--2015 |  | 2016-12-20
|  | SLBOC BWR FI | Steamline Break Outside Containment (BWRs) | RADS | 2 | 833.7 | Gamma | JNID/IL | 0.000687 | 0.00261 | 0.003 | 0.00664 | 2.5 | 834 | 2.5441 | 1988--2015 |  | 2016-12-20
|  | SLBOC PWR FI | Steamline Break Outside Containment (PWRs) | RADS | 10 | 1662.6 | Gamma | JNID/IL | 0.00349 | 0.00613 | 0.00632 | 0.00984 | 10.5 | 1660 | 1.6064 | 1988--2015 |  | 2016-12-20
| Steam Generator Tube Rupture | SGTR | Steam Generator Tube Rupture | RADS | 2 | 1502.7 | Gamma | JNID/IL | 0.000382 | 0.00145 | 0.00166 | 0.00369 | 2.5 | 1500 | 2.5441 | 1991--2015 |  | 2016-12-20
| Loss of Coolant Accidents | LLOCA-BWR | Large Loss Of Coolant Event (BWR) | NUREG-1829 |  |  | Gamma | Geo Mean Aggregate | 1.2632e-09 | 2.8769e-06 | 1.18e-05 | 5.3987e-05 | 0.3 | 25420 | 18.7656 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | LLOCA-PWR | Large Loss Of Coolant Event (PWR) | NUREG-1829 |  |  | Gamma | Geo Mean Aggregate | 6.3209e-10 | 1.4396e-06 | 5.91e-06 | 2.7015e-05 | 0.3 | 50800 | 18.7656 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | MLOCA-BWR | Medium Loss-Of-Coolant Accident (BWRs) | NUREG-1829 |  |  | Gamma | Geo Mean Aggregate | 9.3856e-08 | 3.2838e-05 | 9.05e-05 | 0.00037618 | 0.4 | 4418 | 11.4556 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | MLOCA-PWR | Medium Loss-Of-Coolant Accident (PWRs) | NUREG-1829 |  |  | Gamma | Geo Mean Aggregate | 1.6079e-08 | 3.662e-05 | 0.00015 | 0.00068721 | 0.3 | 1997 | 18.7656 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | SLOCA BWR | Small Loss-Of-Coolant Accident (BWRs) | NUREG-1829 | 1 | 418 | Gamma | Geo Mean Aggregate | 3.8217e-07 | 0.00013371 | 0.000369 | 0.0015318 | 0.4 | 1085 | 11.4556 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | SLOCA PWR | Small Loss-Of-Coolant Accident (PWRs) | NUREG-1829 | 0 | 797 | Gamma | Geo Mean Aggregate | 4.1598e-07 | 0.00014554 | 0.000401 | 0.0016673 | 0.4 | 996.8 | 11.4556 |  | Expert Elicitation, converted from Rx-Calendar Years to Rx-Critical Years | 2017-07-12
|  | VSLOCA BWR FI | Very Small Loss-of-Coolant Accident (BWRs) | RADS | 2 | 734.9 | Gamma | JNID/IL | 0.000779 | 0.00296 | 0.0034 | 0.00753 | 2.5 | 735 | 2.5441 | 1992--2015 |  | 2016-12-20
|  | VSLOCA PWR FI | Very Small Loss-of-Coolant Accident (PWRs) | RADS | 0 | 1445 | Gamma | JNID/IL | 1.36e-06 | 0.000157 | 0.000346 | 0.00132 | 0.5 | 1450 | 8.4439 | 1992--2015 |  | 2016-12-20
|  | SORV1 BWR FI | Stuck Open Safety/Relief Valve (BWR) | RADS | 9 | 709.7 | Gamma | EB/PL/KS | 0.000531 | 0.00847 | 0.0126 | 0.0388 | 0.927 | 73.5 | 4.5813 | 1993--2015 |  | 2016-12-20
|  | SORV2 BWR FI | Stuck Open Relief Valve >2 (BWR) | RADS | 0 | 709.7 | Gamma | JNID/IL | 2.77e-06 | 0.00032 | 0.000705 | 0.00271 | 0.5 | 710 | 8.4439 | 1993--2015 |  | 2016-12-20
|  | SORV1 PWR FI | Stuck Open Safety/Relief Valve (PWR) | RADS | 2 | 1662.6 | Gamma | JNID/IL | 0.000345 | 0.00131 | 0.0015 | 0.00333 | 2.5 | 1660 | 2.5441 | 1988--2015 |  | 2016-12-20
|  | SORV2 PWR FI | Stuck Open Relief Valve >2 (PWR) | RADS | 0 | 1100.6 | Gamma | JNID/IL | 1.79e-06 | 0.000207 | 0.000454 | 0.00175 | 0.5 | 1100 | 8.4439 | 1998--2015 |  | 2016-12-20
|  | ISLOCA BWR FI | Interfacing System Loss of Coolant Accident (BWR) | RADS | 0 | 323.4 | Gamma | JNID/IL | 6.09e-06 | 0.000704 | 0.00155 | 0.00595 | 0.5 | 323 | 8.4439 | 2006--2015 |  | 2016-12-20
|  | ISLOCA PWR FI | Interfacing System Loss of Coolant Accident (PWR) | RADS | 0 | 610 | Gamma | JNID/IL | 3.22e-06 | 0.000373 | 0.00082 | 0.00315 | 0.5 | 610 | 8.4439 | 2006--2015 |  | 2016-12-20
|  | RCPLOCA | Reactor Coolant Pump Seal Loss-of-Coolant Accident (PWRs) | RADS | 0 | 610 | Gamma | JNID/IL | 3.22e-06 | 0.000373 | 0.00082 | 0.00315 | 0.5 | 610 | 8.4439 | 2006--2015 |  | 2016-12-20
|  | XLOCA | Excessive Loss Of Coolant Event (Vessel Rupture) | NUREG/CR-4550 |  |  | Gamma | JNID/IL | 1.07e-11 | 2.44e-08 | 1e-07 | 4.57e-07 | 0.3 | 3000000 | 18.7656 |  |  | 2005-06-23
Transients | General Transient | TRANS BWR | Transient Initiating Event (BWR) | RADS | 441 | 598.2 | Gamma | EB/PL/KS | 0.426 | 0.721 | 0.74 | 1.13 | 11.8 | 15.9 | 1.566 | 1997--2015 |  | 2016-12-20
|  | TRANS PWR | Transient Initiating Event (PWR) | RADS | 743 | 1100.6 | Gamma | EB/PL/KS | 0.335 | 0.649 | 0.676 | 1.12 | 7.86 | 11.6 | 1.7221 | 1998--2015 |  | 2016-12-20
| Loss of Condenser Heat Sink | LOCHS BWR FI | Loss Of Condenser Heat Sink (BWR) | RADS | 69 | 626.6 | Gamma | EB/PL/KS | 0.0351 | 0.1 | 0.11 | 0.218 | 3.65 | 33.2 | 2.1824 | 1996--2015 |  | 2016-12-20
|  | LOCHS PWR FI | Loss Of Condenser Heat Sink (PWR) | RADS | 61 | 1271.4 | Gamma | EB/PL/KS | 0.0111 | 0.042 | 0.0482 | 0.107 | 2.51 | 52.1 | 2.5396 | 1995--2015 |  | 2016-12-20
| Loss of Feedwater | LOMFW | Loss Of Main Feedwater | RADS | 124 | 2096.3 | Gamma | EB/PL/KS | 0.0111 | 0.0502 | 0.0594 | 0.139 | 2.08 | 35 | 2.7722 | 1993--2015 |  | 2016-12-20
Loss of Support Systems | Loss of Safety-Related Cooling Water | LOSWS | Loss Of Safety Related Cooling Water (Open System) | RADS | 0 | 2496.3 | Gamma | JNID/IL | 7.86e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2500 | 8.4439 | 1988--2015 |  | 2016-12-20
|  | PLOSWS FI | Partial Loss Of SWS Initiating Event | RADS | 4 | 2496.3 | Gamma | JNID/IL | 0.000665 | 0.00167 | 0.0018 | 0.00338 | 4.5 | 2500 | 2.028 | 1988--2015 |  | 2016-12-20
|  | LOCCW FI | Loss Of Safety Related Cooling Water (Closed System) | RADS | 0 | 2496.3 | Gamma | JNID/IL | 7.86e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2500 | 8.4439 | 1988--2015 |  | 2016-12-20
|  | PLOCCW FI | Partial Loss Of CCW Initiating Event | RADS | 4 | 2496.3 | Gamma | JNID/IL | 0.000665 | 0.00167 | 0.0018 | 0.00338 | 4.5 | 2500 | 2.028 | 1988--2015 |  | 2016-12-20
| Loss of Instrument Control Air | LOIA BWR | Loss Of Instrument Air (BWR) | RADS | 5 | 761.2 | Gamma | JNID/IL | 0.00301 | 0.00679 | 0.00723 | 0.0129 | 5.5 | 761 | 1.9026 | 1991--2015 |  | 2016-12-20
|  | LOIA PWR | Loss Of Instrument Air (PWR) | RADS | 9 | 1153.5 | Gamma | JNID/IL | 0.0044 | 0.00797 | 0.00824 | 0.0131 | 9.5 | 1150 | 1.6438 | 1997--2015 |  | 2016-12-20
Loss of Offsite Power | Loss of Offsite Power, Power Operations | PO.LOOP | Loss of offsite power, all categories, power operation, per rcry | RADS | 54 | 1751.7 | Gamma | JNID/IL | 0.0245 | 0.031 | 0.0311 | 0.0384 | 54.5 | 1750 | 1.2403 | 1997--2015 |  | 2016-12-20
|  | PO.LOOP-GR | Loss of offsite power, grid-related, power operation, per rcry | RADS | 18 | 1751.7 | Gamma | EB/PP/KS | 0.00011 | 0.00586 | 0.011 | 0.0394 | 0.609 | 55.3 | 6.7307 | 1997--2015 |  | 2017-04-07
|  | PO.LOOP-PC | Loss of offsite power, plant-centered, power operation, per rcry | RADS | 3 | 1751.7 | Gamma | JNID/IL | 0.000619 | 0.00181 | 0.002 | 0.00402 | 3.5 | 1750 | 2.2168 | 1997--2015 |  | 2017-04-07
|  | PO.LOOP-SC | Loss of offsite power, switchyard-centered, power operation, per rcry | RADS | 23 | 1751.7 | Gamma | JNID/IL | 0.00922 | 0.0132 | 0.0134 | 0.0183 | 23.5 | 1750 | 1.3813 | 1997--2015 |  | 2017-04-07
|  | PO.LOOP-WR | Loss of offsite power, weather-related, power operation, per rcry | RADS | 10 | 1751.7 | Gamma | JNID/IL | 0.00331 | 0.00581 | 0.00599 | 0.00933 | 10.5 | 1750 | 2.984 | 1997--2015 |  | 2017-04-07
| Loss of Offsite Power, Shutdown Operations | SD.LOOP | Loss of offsite power, all categories, Shutdown operation, per rcry | RADS | 36 | 213.4 | Gamma | EB/PL/KS | 0.0512 | 0.153 | 0.169 | 0.343 | 3.4 | 20.1 | 2.2412 | 1997--2015 |  | 2017-04-07
|  | SD.LOOP-GR | Loss of offsite power, grid-related, Shutdown operation, per rcry | RADS | 4 | 213.4 | Gamma | EB/PP/KS | 0.00265 | 0.0154 | 0.019 | 0.0479 | 1.67 | 87.6 | 1.8122 | 1997--2015 |  | 2017-04-07
|  | SD.LOOP-PC | Loss of offsite power, plant-centered, Shutdown operation, per rcry | RADS | 7 | 213.4 | Gamma | EB/PL/KS | 0.00781 | 0.0196 | 0.0211 | 0.0397 | 4.5 | 213 | 4.5735 | 1997--2015 |  | 2017-04-07
|  | SD.LOOP-SC | Loss of offsite power, switchyard-centered, Shutdown operation, per rcry | RADS | 17 | 213.5 | Gamma | JNID/IL | 0.0527 | 0.0806 | 0.082 | 0.117 | 17.5 | 213 | 1.4504 | 1997--2015 |  | 2017-04-07
|  | SD.LOOP-WR | Loss of offsite power, weather-related, Shutdown operation, per rcry | RADS | 8 | 213.4 | Gamma | JNID/IL | 0.0204 | 0.0384 | 0.0398 | 0.0648 | 8.5 | 213 | 7.1924 | 1997--2015 |  | 2017-04-07
Electrical Power | Loss of AC Electrical Bus | LOAC | Loss Of Vital AC Bus | RADS | 12 | 2179.9 | Gamma | JNID/IL | 0.00335 | 0.00558 | 0.00573 | 0.00864 | 12.5 | 2180 | 1.5472 | 1992--2015 |  | 2016-12-20
|  | LOAC 4160V FI | Loss Of Vital AC Bus (4160 Volt) | RADS | 7 | 2179.9 | Gamma | JNID/IL | 0.00167 | 0.00329 | 0.00344 | 0.00573 | 7.5 | 2180 | 1.7432 | 1992--2015 |  | 2016-12-20
|  | LOAC LOWV FI | Loss Of Vital AC Bus (Low Voltage) | RADS | 5 | 2179.9 | Gamma | JNID/IL | 0.00105 | 0.00237 | 0.00252 | 0.00451 | 5.5 | 2180 | 1.9026 | 1992--2015 |  | 2016-12-20
|  | LOACB2 | Loss Of Vital AC Bus Event (2 Buses modeled as IEs) | RADS Adjusted | 12 | 2179.9 | Gamma | JNID/IL | 3.07e-07 | 0.000698 | 0.00287 | 0.0131 | 0.3 | 104.712 | 18.7656 | 1992--2015 | Adjusted for initiation by 2-busses (0.5) | 2016-12-20
| Loss of DC Electrical Bus | LODC | Loss Of Vital DC Bus | RADS | 2 | 2496.3 | Gamma | JNID/IL | 0.000229 | 0.00087 | 0.001 | 0.00221 | 2.5 | 2500 | 2.5441 | 1988--2015 |  | 2016-12-20
|  | LODCB2 | Loss Of Vital DC Bus Event (2 Buses modeled as IEs) | RADS Adjusted | 2 | 2496.3 | Gamma | JNID/IL | 5.35e-08 | 0.000122 | 0.0005 | 0.00229 | 0.3 | 600 | 18.7656 | 1988--2015 | Adjusted for initiation by 2-busses (0.5) | 2016-12-20
Acronyms - BWR (boiling water reactor), EB (empirical Bayes), EE (expert elicitation), IE (initiating event), IEDB (initiating events database - http://nrcoe.inl.gov), PWR (pressurized water reactor)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.

## Train UA
SPAR Basic Event Unavailability Data and Results
2015 Paramater Estimation Update
2016-12-21 12:00
Section | Sub Section | Train Unavailability Event | Train Description | Data Source | Analysis | Data | Industry-average Probability Distribution (note a) | [7 empty] | Date Range | Comments (see Appendix B for details) | Effective Date
[6 empty] | MSPI Trains | Distribution (note b) | 5th | Median | Mean | 95th | α | β | Error Factor
Generators | 1E EDG | EDG-EPS | Diesel Generator Test And Maintenance | EPIX/RADS | CurveFit/Plant | 100 | Normal | 0.00444 | 0.0148 | 0.0148 | 0.0252 | 0.0148 | 0.0063 | 1.7002 | 2002--2015 |  | 2016-12-20
| Combustion Turbine | CTG | Combustion Turbine Generator Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 0.000212 | 0.0243 | 0.05 | 0.187 | 0.5 | 9.5 | 7.7165 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. IPEs | 2005-06-23
| HPCS | EDG-HCS | HPCS Diesel Generator Test And Maintenance | EPIX/RADS | CurveFit/Plant | 8 | Normal | 0.00759 | 0.0117 | 0.0117 | 0.0158 | 0.0117 | 0.0025 | 1.3515 | 2002--2015 |  | 2016-12-20
| Generator Service Water | EDG-SW | Service Water for the Emergency Diesel Generator | EPIX/RADS | CurveFit/Plant | 4 | Normal | -0.00231 | 0.0092 | 0.00917 | 0.0207 | 0.0092 | 0.007 | 2.2515 | 2002--2015 |  | 2016-12-20
|  | HCS-SW | Service Water for the High Pressure Core Spray Generator | EPIX/RADS | CurveFit/Plant | 7 | Normal | 0.00336 | 0.0055 | 0.00554 | 0.00764 | 0.0055 | 0.0013 | 1.3888 | 2002--2015 |  | 2016-12-20
Pumps | Motor Driven | MDP-ALL | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 103 | Normal | -0.0012 | 0.0062 | 0.00621 | 0.0136 | 0.0062 | 0.0045 | 2.1938 | 2002--2015 |  | 2016-12-20
|  | MDP-AFW | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 66 | Normal | 0.000175 | 0.0033 | 0.00334 | 0.00643 | 0.0033 | 0.0019 | 1.947 | 2002--2015 |  | 2016-12-20
|  | MDP-CCW | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 51 | Normal | -0.00191 | 0.0045 | 0.00446 | 0.0109 | 0.0045 | 0.0039 | 2.4255 | 2002--2015 |  | 2016-12-20
|  | MDP-ESW | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 99 | Normal | -0.00954 | 0.0097 | 0.00966 | 0.0289 | 0.0097 | 0.0117 | 2.984 | 2002--2015 |  | 2016-12-20
|  | MDP-FWS | Feed Water System Motor-Driven Pumps Total Unavailability | EPIX/RADS | CurveFit/Year | 14 | Normal | 0.000353 | 0.0094 | 0.00944 | 0.0184 | 0.0094 | 0.0055 | 1.9624 | 2002--2015 |  | 2016-12-20
|  | MDP-HCS | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 8 | Normal | 0.00352 | 0.0073 | 0.00735 | 0.0111 | 0.0073 | 0.0023 | 1.5182 | 2002--2015 |  | 2016-12-20
|  | MDP-HPI | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 69 | Normal | 1.03e-05 | 0.0033 | 0.00332 | 0.00659 | 0.0033 | 0.002 | 1.9969 | 2002--2015 |  | 2016-12-20
|  | MDP-RHR | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 103 | Normal | 0.00125 | 0.0052 | 0.00518 | 0.00915 | 0.0052 | 0.0024 | 1.7592 | 2002--2015 |  | 2016-12-20
|  | MDP-RHR-BWR | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 34 | Normal | 0.00271 | 0.006 | 0.00595 | 0.00929 | 0.006 | 0.002 | 1.5483 | 2002--2015 |  | 2016-12-20
|  | MDP-RHR-PWR | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 69 | Normal | 0.000523 | 0.0048 | 0.00481 | 0.00908 | 0.0048 | 0.0026 | 1.891 | 2002--2015 |  | 2016-12-20
|  | MDP-RHRSW | Motor Driven Pump Test And Maintenance, RHR Service Water | EPIX/RADS | CurveFit/Plant | 22 | Normal | 0.00105 | 0.0045 | 0.00455 | 0.00795 | 0.0045 | 0.0021 | 1.7676 | 2002--2015 |  | 2016-12-20
|  | PDP | Positive Displacement Pump Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 1.18e-05 | 0.00137 | 0.003 | 0.0115 | 0.5 | 166.167 | 8.401 |  | IPEs | 2005-06-23
|  | MDP-CLEAN | Motor Driven Pump Test And Maintenance, Clean System | EPIX/RADS | CurveFit/Plant | 81 | Normal | 8.79e-05 | 0.0042 | 0.00422 | 0.00831 | 0.0042 | 0.0025 | 1.9791 | 2002--2015 |  | 2016-12-20
|  | MDP-NR-CLEAN | Motor Driven Pump Test & Maintenance, Normally Running System, Clean | EPIX/RADS | CurveFit/Plant | 52 | Normal | -0.00181 | 0.0046 | 0.00456 | 0.011 | 0.0046 | 0.0039 | 2.3945 | 2002--2015 |  | 2016-12-20
|  | MDP-NS-CLEAN | Motor Driven Pump Test And Maintenance, Normally Standby System, Clean | EPIX/RADS | CurveFit/Plant | 103 | Normal | 0.00131 | 0.0046 | 0.0046 | 0.00789 | 0.0046 | 0.002 | 1.7152 | 2002--2015 |  | 2016-12-20
|  | MDP-NR-DIRTY | Motor Driven Pump Test And Maintenance, Normally Running System, Dirty | EPIX/RADS | CurveFit/Plant | 99 | Normal | -0.00954 | 0.0097 | 0.00966 | 0.0289 | 0.0097 | 0.0117 | 2.984 | 2002--2015 |  | 2016-12-20
|  | MDP-NS-DIRTY | Motor Driven Pump Test And Maintenance, Normally Standby System, Dirty | EPIX/RADS | CurveFit/Plant | 103 | Normal | -0.00945 | 0.0093 | 0.00934 | 0.0281 | 0.0093 | 0.0114 | 3.0163 | 2002--2015 |  | 2016-12-20
| Turbine Driven | TDP-ALL | Combined UA of TDPs from the AFW, HCI, and RCI systems | EPIX/RADS | CurveFit/Plant | 95 | Normal | 0.000292 | 0.0072 | 0.00725 | 0.0141 | 0.0072 | 0.0042 | 1.9595 | 2002--2015 |  | 2016-12-20
|  | TDP-AFW | Turbine Driven Pump Test Or Maintenance (AFW) | EPIX/RADS | CurveFit/Plant | 63 | Normal | 0.000265 | 0.0052 | 0.00524 | 0.0101 | 0.0052 | 0.003 | 1.949 | 2002--2015 |  | 2016-12-20
|  | TDP-HCI | Turbine Driven Pump Test Or Maintenance (HPCI-RCI) | EPIX/RADS | CurveFit/Plant | 24 | Normal | 0.00726 | 0.0117 | 0.0117 | 0.0161 | 0.0117 | 0.0027 | 1.3796 | 2002--2015 |  | 2016-12-20
|  | TDP-RCI | Turbine Driven Pump Test Or Maintenance (HPCI-RCI) | EPIX/RADS | CurveFit/Plant | 30 | Normal | 0.00283 | 0.0104 | 0.0104 | 0.018 | 0.0104 | 0.0046 | 1.7275 | 2002--2015 |  | 2016-12-20
|  | TDP-HCI-RCI | Turbine Driven Pump Test Or Maintenance (HPCI-RCI) | EPIX/RADS | CurveFit/Plant | 24 | Normal | 0.00726 | 0.0117 | 0.0117 | 0.0161 | 0.0117 | 0.0027 | 1.3796 | 2002--2015 |  | 2016-12-20
| Engine Driven | EDP | Engine Driven Pump Test And Maintenance | EPIX/RADS | CurveFit/Plant | 9 | Normal | -0.00383 | 0.0164 | 0.0164 | 0.0366 | 0.0164 | 0.0123 | 2.2336 | 2002--2015 |  | 2016-12-20
|  | EDP-AFW | Engine Driven Pump Test And Maintenance | EPIX/RADS | CurveFit/Plant | 5 | Normal | 0.0041 | 0.0064 | 0.00644 | 0.0087 | 0.0064 | 0.0014 | 1.3598 | 2002--2015 |  | 2016-12-20
|  | EDP-ESW | Engine Driven Pump Test And Maintenance | EPIX/RADS | CurveFit/Plant | 4 | Normal | 0.0205 | 0.0289 | 0.0289 | 0.0373 | 0.0289 | 0.0051 | 1.2903 | 2002--2015 |  | 2016-12-20
Heat Exchangers | Pooled | HTX | Heat Exchanger In Test Or Maintenance | EPIX/RADS | CurveFit/Plant | 37 | Normal | -0.00626 | 0.0069 | 0.00693 | 0.0201 | 0.0069 | 0.008 | 2.9071 | 2002--2015 |  | 2016-12-20
| CCW | HTX-CCW | Heat Exchanger Test Or Maintenance (CCW) | EPIX/RADS | CurveFit/Plant | 34 | Normal | -0.00619 | 0.0073 | 0.00731 | 0.0208 | 0.0073 | 0.0082 | 2.8476 | 2002--2015 |  | 2016-12-20
| Service Water | HTX-ESW | Heat Exchanger Test Or Maintenance (ESW) | EPIX/RADS | CurveFit/Year | 13 | Normal | 0.00381 | 0.015 | 0.015 | 0.0262 | 0.015 | 0.0068 | 1.7457 | 2002--2015 |  | 2016-12-20
| Residual Heat Removal | HTX-RHR-BWR | Heat Exchanger And Pump Train Test Or Maintenance (RHR-BWR) | EPIX/RADS | CurveFit/Plant | 3 | Normal | -0.000361 | 0.0026 | 0.00255 | 0.00556 | 0.0026 | 0.0018 | 2.1387 | 2002--2015 |  | 2016-12-20
|  | HTX-RHR-PWR | Heat Exchanger And Pump Train Test Or Maintenance (RHR-BWR) | EPIX/RADS | CurveFit/Year | 14 | Normal | -0.000458 | 0.0002 | 0.000242 | 0.000858 | 0.0002 | 0.0004 | 4.2897 | 2002--2015 |  | 2016-12-20
Electrical | Breaker | CRB | Circuit Breaker Unavailable | Unknown | CurveFit | -- | Beta | 0.00616 | 0.5 | 0.5 | 0.994 | 0.5 | 0.5 | 1.9877 |  |  | 2005-06-23
| Bus | BDC | Bus (DC) Test or Maintenance | IPEs | JNID/IL | -- | Beta | 7.87e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2499.5 | 8.4411 |  | IPEs | 2005-06-23
|  | BAC | Bus (AC) Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 7.87e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2499.5 | 8.4411 |  | IPEs | 2005-06-23
| Battery | BAT | Battery Test or Maintenance | Letter | CurveFit | -- | Lognormal | 2.8e-06 | 0.000148 | 0.00272 | 0.00784 | 52.9 |  | 52.8813 |  |  | 2005-06-23
|  | BCH | Battery Charger Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | 8.4153 |  | IPEs | 2005-06-23
| Transformer | TFM | Startup Transformer Test or Maintenance | Letter | CurveFit | -- | Lognormal | 4.55e-07 | 4.11e-05 | 0.00175 | 0.00372 | 90.5 |  | 90.4637 |  |  | 2005-06-23
| RPS | CCP-RPS | RPS CH-A IN T&M | NUREG/CR-5500, Vol 2,3,10, and 11 | JNID/IL | -- | Beta | 5.37e-08 | 0.000812 | 0.005 | 0.0245 | 0.24 | 47.76 | 30.1733 |  |  | 2005-06-23
Other | Ventilation | ACX | Air Handling Unit Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 9.87e-06 | 0.00114 | 0.0025 | 0.00959 | 0.5 | 199.5 | 8.4082 |  | IPEs | 2005-06-23
|  | CHL | Chiller Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 8.11e-05 | 0.00934 | 0.02 | 0.0761 | 0.5 | 24.5 | 8.1559 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. IPEs | 2005-06-23
| Compressor | MDC | Motor-Driven Compressor Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | 8.2716 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. IPEs | 2005-06-23
|  | DDC | Diesel Driven Compressor Fails Due To T&M | Existing SPAR | JNID/IL | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | 8.2716 |  | From MDC | 2005-06-23
|  | EDC | Engine-Driven Compressor Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | 8.2716 |  | Comparison of IPE UAs versus 2002 - 2004 MSPI UAs and 1998 - 2002 ROP SSU UAs indicates a drop of approximately 50% for IPE UAs > 5.0E-3. IPE value divided by 2. IPEs | 2005-06-23
| Fan | FAN | Fan Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | 8.4153 |  | IPEs | 2005-06-23
|  | CTF | Cooling Tower Fan Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | 8.4153 |  | IPEs | 2005-06-23
| Explosive Valve | EPV | Explosive-Operated (SQUIBB) Valve Test or Maintenance | NUREG/CR-6928 | JNID/IL | -- | Beta | 2.36e-06 | 0.000273 | 0.0006 | 0.0023 | 0.5 | 832.833 | 8.4354 |  | IPEs | 2005-06-23
Headers | Clean Water | HDR-AFW | AFW Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 7 | Normal | -0.000551 | 0.0006 | 0.000561 | 0.00175 | 0.0006 | 0.0007 | 2.919 | 2002--2015 |  | 2016-12-20
|  | HDR-CCW | CCW Header Total Unavailability | EPIX/RADS | CurveFit/Year | 14 | Normal | -0.000851 | 0.0003 | 0.000317 | 0.00145 | 0.0003 | 0.0007 | 4.838 | 2002--2015 |  | 2016-12-20
|  | HDR-HPI | HPI Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 8 | Normal | -0.000129 | 0.0002 | 0.000221 | 0.000529 | 0.0002 | 0.0002 | 2.6449 | 2002--2015 |  | 2016-12-20
|  | HDR-ISO | ISO Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 4 | Normal | 0.00104 | 0.004 | 0.00401 | 0.00696 | 0.004 | 0.0018 | 1.7402 | 2002--2015 |  | 2016-12-20
|  | HDR-RHR | RHR Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 8 | Normal | -0.00137 | 0.0006 | 0.000636 | 0.00257 | 0.0006 | 0.0012 | 4.2897 | 2002--2015 |  | 2016-12-20
| Service Water | HDR-ESW | ESW Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 26 | Normal | -0.0305 | 0.009 | 0.00895 | 0.0485 | 0.009 | 0.024 | 5.3863 | 2002--2015 |  | 2016-12-20
|  | HDR-RHRSW | RHRSW Header Total Unavailability | EPIX/RADS | CurveFit/Plant | 5 | Normal | -0.000445 | 0.0012 | 0.0012 | 0.00284 | 0.0012 | 0.001 | 2.3707 | 2002--2015 |  | 2016-12-20
Acronyms - AFWS (auxiliary feedwater system), BWR (boiling water reactor), CCW (component cooling water), EPS (emergency power system), ESW (emergency or essential service water), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), IC (isolation condenser), HTX
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
For the ROP UAs, the mean is the average of individual train UAs. Each train UA is the total number of planned and unplanned outage hours divided by total number of plant critical hours.
Note b - For the ROP UAs, the percentiles were obtained from the ordered set of train UAs. The error factor is the 95th percentile divided by the median.

## Special Events
SPAR Special Event Data and Results
2015 Paramater Estimation Update
Special Event Name | System Study Name | Description | Existing SPAR Value |  | Data Source | Data | [6 empty] | Industry-average Probability or Rate Distribution (note a) | [8 empty] | Comments (see Appendix C for details) | [5 empty] | Effective Date
|  |  | Mean | Units |  | Failures | Demands or Hours | MLE | Jeffreys Mean | Error Factor | Data Source | d or h | Distribution (note b) | Mean | α | β | Error Factor | Rounded Mean (note c) | Rounded α (note c) | β (note d) | Rounded Error Factor |  | Recommended Improvement | 95% | Median | 95% | Median
TDP-PRST (RCIC) | IFRS | RCIC TDP probability of restart | 0.26 | D | SS | 6 | 47 | 0.12766 | 0.13542 | ? | System Study (1996 - 2002) | d | Beta (Jeffreys, Jeffreys) | 0.13542 | 6.5 | 41.5 | 1.7163 | 0.15 | 6 | 34 | 1.7403 |  |  | 0.25085 | 0.14415 | 0.22371 | 0.13034 | 2007-02-01
TDP-FRST (RCIC) | LNRS | RCIC TDP restart failure per event | 0.24 | D | SS | 1 | 17 | 0.058824 | 0.083333 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.083333 | 0.5 | 5.5 | 7.2198 | 0.08 | 0.5 | 5.75 | 7.2698 |  |  | 0.29419 | 0.040467 | 0.30575 | 0.042348 | 2007-02-01
TDP-FRFRST (RCIC) | FRFTRS | RCIC failure to recover TDP restart failure | 0.5 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (RCIC) | PMI | RCIC injection valve probability of multiple injections | ? | D | SS | 14 | 28 | 0.5 | 0.5 | ? | System Study (1998 - 2002) | d | Beta (EB/YL/KS, EB/YL/KS) | 0.503 | 4.18 | 4.1301 | 1.5354 | 0.5 | 4 | 4 | 1.5494 |  |  | 0.77468 | 0.5 | 0.77267 | 0.50325 | 2007-02-01
MOV-FTRO (RCIC) | FRO | RCIC injection valve fails to reopen | ? | D | SS | 1 | 38 | 0.026316 | 0.038462 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.038462 | 0.5 | 12.5 | 7.8865 | 0.04 | 0.5 | 12 | 7.8639 |  |  | 0.15073 | 0.019168 | 0.14506 | 0.018393 | 2007-02-01
MOV-FRFTRO (RCIC) | FRFRO | RCIC failure to recover injection valve failure to reopen | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFRI (RCIC) | LNRC | RCIC failure to transfer back to injection mode (pump recirculation valve) | 0.034 | D | SS | 1 | 197.95 | 0.0050518 | 0.0075777 | ? | System Study (1988 - 2002) | h | Gamma (Jeffreys, SCNID) | 0.0075777 | 0.5 | 65.9833 | 8.4439 | 0.008 | 0.5 | 62 | 8.4439 | Note that this is per hour. Failure occurred 8 min after RCIC initiation. |  | 119.0852 | 14.103 | 126.7361 | 15.0091 | 2007-02-01
SUC-FRFTFR (RCIC) | FRFTRC | RCIC failure to recover transfer failure | 0.17 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | 0.77148 | 0.16319 | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (HPCI) | PMI | HPCI injection valve probability of multiple injections | 0.13 | D | SS | 2 | 17 | 0.11765 | 0.13889 | ? | System Study (1995 - 2002) | d | Beta (Jeffreys, SCNID) | 0.13889 | 0.5 | 3.1 | 6.38 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.48738 | 0.076392 | 2007-02-01
MOV-FTRO (HPCI) | FRO | HPCI injection valve fails to reopen | 0.192 | D | SS | 1 | 8 | 0.125 | 0.16667 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.16667 | 0.5 | 2.5 | 5.9592 | 0.15 | 0.5 | 2.8333 | 6.2115 |  |  | 0.52092 | 0.083863 | 0.56926 | 0.095526 | 2007-02-01
MOV-FRFTRO (HPCI) | FRFRO | HPCI failure to recover injection valve failure to reopen | 0.833 | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
SUC-FTFR (HPCI) | FTRT | HPCI failure to transfer | ? | D | SS | 0 | 1270 | 0 | 0.00039339 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.00039339 | 0.5 | 1270.5 | 8.4383 | 0.0004 | 0.5 | 1249.5 | 8.4382 |  |  | 0.0015363 | 0.00018207 | 0.0015109 | 0.00017906 | 2007-02-01
SUC-FRFTFR (HPCI) | FRFTRT | HPCI failure to recover transfer failure | ? | D | SS | 0 | 0 | #DIV/0! | 0.5 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.5 | 0.5 | 0.5 | 1.9877 | 0.5 | 0.5 | 0.5 | 1.9877 |  |  | 0.99384 | 0.5 | 0.99384 | 0.5 | 2007-02-01
SUC-FTFR (HPCS) | FTRT | HPCS failure to transfer | ? | D | SS | 1 | 478 | 0.0020921 | 0.0031315 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.0031315 | 0.5 | 159.1667 | 8.3991 | 0.003 | 0.5 | 166.1667 | 8.401 |  |  | 0.01151 | 0.00137 | 0.012014 | 0.0014303 | 2007-02-01
SUC-FRFTFR (HPCS) | FRFTRT | HPCS failure to recover transfer failure | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 | 0.8 | 0.5 | 0.125 | 1.0132 |  |  | 1 | 0.98695 | 1 | 0.95096 | 2007-02-01
Acronyms - EB (empirical Bayes), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), KS (Kass-Steffey), MOV (motor-operated valve), RCIC (reactor core isolation cooling), SCNID (simplified constrained noninformative distribution), SUC (suction), SS (updated system study), TDP (turbine-driven pump), YL (year level)
Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in Reference 59 in NUREG/CR-6928 and outlined in Section 6.2.3.5 in Reference 17 in NUREG/CR-6928.
Note b - The format for the distributions is the following: distribution type (source for mean, source for α factor).
Note c - The value is rounded to 1.0, 1.2, 1.5, 2.0, 2.5, 3.0, 4.0, 5.0, 6.0, 7.0, 8.0, or 9.0 times the appropriate power of ten.
Note d - The β factor is determined from mean and α. The β factor is presented to three significant figures to preserve the mean of the distribution.