## Component Reliability
Summary of SPAR Component Unreliability Data and Results
2020 Parameter Estimation Update
2021-11-01 18:55 |  | Parameter Estimate 2020 V1
Grouping | Component Type | Component Failure Mode | Description | Data Source | Data |  |  |  | Industry-average Failure Probability or Rate Distribution (note a) | [8 empty] | Date Range | Effective Date
[5 empty] | Failures | Demands or Hours | d or h | Components | Distribution | Analysis Type | 5th | Median | Mean | 95th | α | β | Error Factor (note b)
Valves | Air-Operated Valve (AOV) | AOV-FTO | Air-Operated Valve Fails To Open | EPIX/RADS | 50 | 165941.5 | d | 1755 | Beta | JNID/IL | 0.000237 | 0.000302 | 0.000304 | 0.000378 | 50.5 | 166000 | 1.2504 | 2006--2020 | 2021-11-01
|  | AOV-FTC | Air-Operated Valve Fails To Close | EPIX/RADS | 27 | 165941.5 | d | 1755 | Beta | EB/PL/KS | 2.3e-06 | 0.000104 | 0.000189 | 0.000664 | 0.638 | 3380 | 6.4096 | 2006--2020 | 2021-11-01
|  | AOV-FTOC | Air-Operated Valve Fails To Open/Close | EPIX/RADS | 83 | 165941.5 | d | 1755 | Beta | EB/PL/KS | 1.73e-05 | 0.000357 | 0.000558 | 0.00178 | 0.832 | 1490 | 5.0011 | 2006--2020 | 2021-11-01
|  | AOV-FC | Air-Operated Valve Fails To Control | EPIX/RADS | 167 | 1109287000 | h | 8788 | Gamma | EB/PL/KS | 1.5e-08 | 1.32e-07 | 1.75e-07 | 4.86e-07 | 1.26 | 7170000 | 3.6781 | 2006--2020 | 2021-11-01
|  | AOV-SOP | Air-Operated Valve Spurious Operation | EPIX/RADS | 61 | 1109287000 | h | 8788 | Gamma | EB/PL/KS | 1.99e-09 | 3.79e-08 | 5.83e-08 | 1.85e-07 | 0.859 | 14700000 | 4.8724 | 2006--2020 | 2021-11-01
|  | AOV-ILS | Air-Operated Valve Internal Leakage (Small) | EPIX/RADS | 35 | 1109287000 | h | 8788 | Gamma | JNID/IL | 2.37e-08 | 3.17e-08 | 3.2e-08 | 4.13e-08 | 35.5 | 1110000000 | 1.3033 | 2006--2020 | 2021-11-01
|  | AOV-ILL | Air-Operated Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 8788 | Gamma | JNID/IL | 6.85e-14 | 1.56e-10 | 6.4e-10 | 2.93e-09 | 0.3 | 468750000 | 18.7656 | 2006--2020 | 2021-11-01
|  | AOV-ELS | Air-Operated Valve External Leakage (Small) | EPIX/RADS | 35 | 1109287000 | h | 8788 | Gamma | EB/PL/KS | 2.67e-10 | 1.75e-08 | 3.43e-08 | 1.25e-07 | 0.575 | 16800000 | 7.1645 | 2006--2020 | 2021-11-01
|  | AOV-ELL | Air-Operated Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 8788 | Gamma | EB/PL/KS | 2.57e-13 | 5.85e-10 | 2.4e-09 | 1.1e-08 | 0.3 | 124948000 | 18.7656 | 2006--2020 | 2021-11-01
|  | AOV-SOP-CCW | Component Cooling Water AOV Spurious Operation | EPIX/RADS | 10 | 144615200 | h | 1164 | Gamma | JNID/IL | 4e-08 | 7.01e-08 | 7.26e-08 | 1.13e-07 | 10.5 | 145000000 | 1.6064 | 2006--2020 | 2021-11-01
|  | AOV-SOP-IAS | Instrument Air System AOV Spurious Operation | EPIX/RADS | 0 | 6218450 | h | 50 | Gamma | JNID/IL | 3.16e-10 | 3.66e-08 | 8.04e-08 | 3.09e-07 | 0.5 | 6220000 | 8.4439 | 2006--2020 | 2021-11-01
| Motor-Operated Valve (MOV) | MOV-FTO | Motor-Operated Valve Fails To Open | EPIX/RADS | 190 | 593626 | d | 7120 | Beta | EB/PL/KS | 7.8e-05 | 0.000299 | 0.000343 | 0.000762 | 2.48 | 7220 | 2.5526 | 2006--2020 | 2021-11-01
|  | MOV-FTC | Motor-Operated Valve Fails To Close | EPIX/RADS | 123 | 593626 | d | 7120 | Beta | EB/PL/KS | 1.09e-05 | 0.000156 | 0.000228 | 0.00069 | 0.972 | 4260 | 4.4147 | 2006--2020 | 2021-11-01
|  | MOV-FTOC | Motor-Operated Valve Fails To Open/Close | EPIX/RADS | 346 | 593626 | d | 7120 | Beta | EB/PL/KS | 0.000142 | 0.000554 | 0.00064 | 0.00143 | 2.43 | 3800 | 2.5756 | 2006--2020 | 2021-11-01
|  | MOV-FC | Motor-Operated Feed Control Valve Fails To Control | EPIX/RADS | 59 | 1634537000 | h | 13344 | Gamma | EB/PL/KS | 9.42e-10 | 2.17e-08 | 3.47e-08 | 1.13e-07 | 0.798 | 23000000 | 5.1876 | 2006--2020 | 2021-11-01
|  | MOV-SOP | Motor-Operated Valve Spurious Operation | EPIX/RADS | 41 | 1634537000 | h | 13344 | Gamma | JNID/IL | 1.93e-08 | 2.53e-08 | 2.54e-08 | 3.23e-08 | 41.5 | 1630000000 | 1.2785 | 2006--2020 | 2021-11-01
|  | MOV-ILS | Motor-Operated Valve Internal Leakage (Small) | EPIX/RADS | 55 | 1634537000 | h | 13344 | Gamma | EB/PL/KS | 7.97e-11 | 1.49e-08 | 3.61e-08 | 1.44e-07 | 0.451 | 12500000 | 9.6532 | 2006--2020 | 2021-11-01
|  | MOV-ILL | Motor-Operated Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 13344 | Gamma | EB/PL/KS | 7.73e-14 | 1.76e-10 | 7.22e-10 | 3.3e-09 | 0.3 | 415512000 | 18.7656 | 2006--2020 | 2021-11-01
|  | MOV-ELS | Motor-Operated Valve External Leakage (Small) | EPIX/RADS | 29 | 1634537000 | h | 13344 | Gamma | EB/PL/KS | 4.85e-11 | 7.97e-09 | 1.88e-08 | 7.43e-08 | 0.463 | 24600000 | 9.3195 | 2006--2020 | 2021-11-01
|  | MOV-ELL | Motor-Operated Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 13344 | Gamma | EB/PL/KS | 1.41e-13 | 3.21e-10 | 1.32e-09 | 6.02e-09 | 0.3 | 227964000 | 18.7656 | 2006--2020 | 2021-11-01
|  | MOV-FTO-BFV | Butterfly Valve Fails To Open | EPIX/RADS | 24 | 89398.7 | d | 983 | Beta | JNID/IL | 0.00019 | 0.00027 | 0.000274 | 0.000371 | 24.5 | 89400 | 1.3724 | 2006--2020 | 2021-11-01
|  | MOV-FTC-BFV | Butterfly Valve Fails To Close | EPIX/RADS | 24 | 89398.7 | d | 983 | Beta | EB/PL/KS | 2.52e-05 | 0.000218 | 0.000289 | 0.000797 | 1.27 | 4390 | 3.6583 | 2006--2020 | 2021-11-01
|  | MOV-FTOC-BFV | Butterfly Valve Fails To Open/Close | EPIX/RADS | 54 | 89398.7 | d | 983 | Beta | EB/PL/KS | 7.34e-06 | 0.000406 | 0.000769 | 0.00276 | 0.602 | 783 | 6.8063 | 2006--2020 | 2021-11-01
|  | MOV-SOP-CCW | Component Cooling Water MOV Spurious Operation | EPIX/RADS | 4 | 183661900 | h | 1472 | Gamma | JNID/IL | 9.04e-09 | 2.27e-08 | 2.45e-08 | 4.6e-08 | 4.5 | 184000000 | 2.028 | 2006--2020 | 2021-11-01
|  | MOV-SOP-SWS | Standby Service Water Motor-Operated Valve Spurious Operation | EPIX/RADS | 0 | 64725970 | h | 566 | Gamma | JNID/IL | 3.04e-11 | 3.52e-09 | 7.72e-09 | 2.97e-08 | 0.5 | 64700000 | 8.4439 | 2006--2020 | 2021-11-01
|  | MOV-BFV-SOP-CCW | Component Cooling Water Butterfly Valve Spurious Operation | EPIX/RADS | 2 | 86552190 | h | 738 | Gamma | JNID/IL | 6.61e-09 | 2.51e-08 | 2.89e-08 | 6.39e-08 | 2.5 | 86600000 | 2.5441 | 2006--2020 | 2021-11-01
| Hydraulic-Operated Valve (HOV) | HOV-FTOC | Hydraulic-Operated Valve Fails To Open | EPIX/RADS | 17 | 16401.2 | d | 219 | Beta | EB/PL/KS | 2.23e-06 | 0.000493 | 0.00123 | 0.00497 | 0.436 | 353 | 10.0898 | 2006--2020 | 2021-11-01
|  | HOV-FC | Hydraulic-Operated Valve Fails To Control | EPIX/RADS | 21 | 76176020 | h | 603 | Gamma | JNID/IL | 1.9e-07 | 2.78e-07 | 2.82e-07 | 3.89e-07 | 21.5 | 76200000 | 1.4008 | 2006--2020 | 2021-11-01
|  | HOV-SOP | Hydraulic-Operated Valve Spurious Operation | EPIX/RADS | 10 | 76176020 | h | 603 | Gamma | EB/PL/KS | 6.27e-10 | 5.84e-08 | 1.23e-07 | 4.64e-07 | 0.526 | 4280000 | 7.9384 | 2006--2020 | 2021-11-01
|  | HOV-ILS | Hydraulic-Operated Valve Internal Leakage (Small) | EPIX/RADS | 2 | 76176020 | h | 603 | Gamma | JNID/IL | 7.52e-09 | 2.86e-08 | 3.28e-08 | 7.26e-08 | 2.5 | 76200000 | 2.5441 | 2006--2020 | 2021-11-01
|  | HOV-ILL | Hydraulic-Operated Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 603 | Gamma | JNID/IL | 7.02e-14 | 1.6e-10 | 6.56e-10 | 3e-09 | 0.3 | 457317000 | 18.7656 | 2006--2020 | 2021-11-01
|  | HOV-ELS | Hydraulic-Operated Valve External Leakage (Small) | EPIX/RADS | 7 | 76176020 | h | 603 | Gamma | EB/PL/KS | 2.08e-10 | 3.97e-08 | 9.66e-08 | 3.85e-07 | 0.449 | 4650000 | 9.7116 | 2006--2020 | 2021-11-01
|  | HOV-ELL | Hydraulic-Operated Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 603 | Gamma | EB/PL/KS | 7.24e-13 | 1.65e-09 | 6.76e-09 | 3.09e-08 | 0.3 | 44365600 | 18.7656 | 2006--2020 | 2021-11-01
| Solenoid-Operated Valve (SOV) | SOV-FTOC | Solenoid-Operated Valve Fails To Open | EPIX/RADS | 13 | 27937.3 | d | 555 | Beta | JNID/IL | 0.000289 | 0.000472 | 0.000483 | 0.000718 | 13.5 | 27900 | 1.5229 | 2006--2020 | 2021-11-01
|  | SOV-FC | Solenoid-Operated Valve Fails To Control | EPIX/RADS | 15 | 115760700 | h | 921 | Gamma | EB/PL/KS | 1.52e-09 | 8.08e-08 | 1.52e-07 | 5.44e-07 | 0.609 | 4010000 | 6.7307 | 2006--2020 | 2021-11-01
|  | SOV-SOP | Solenoid-Operated Valve Spurious Operation | EPIX/RADS | 9 | 115760700 | h | 921 | Gamma | JNID/IL | 4.36e-08 | 7.9e-08 | 8.21e-08 | 1.3e-07 | 9.5 | 116000000 | 1.6438 | 2006--2020 | 2021-11-01
|  | SOV-ILS | Solenoid-Operated Valve Internal Leakage (Small) | EPIX/RADS | 8 | 115760700 | h | 921 | Gamma | JNID/IL | 3.74e-08 | 7.04e-08 | 7.34e-08 | 1.19e-07 | 8.5 | 116000000 | 1.6885 | 2006--2020 | 2021-11-01
|  | SOV-ILL | Solenoid-Operated Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 921 | Gamma | JNID/IL | 1.57e-13 | 3.58e-10 | 1.47e-09 | 6.72e-09 | 0.3 | 204360000 | 18.7656 | 2006--2020 | 2021-11-01
|  | SOV-ELS | Solenoid-Operated Valve External Leakage (Small) | EPIX/RADS | 2 | 115760700 | h | 921 | Gamma | JNID/IL | 4.94e-09 | 1.88e-08 | 2.16e-08 | 4.77e-08 | 2.5 | 116000000 | 2.5441 | 2006--2020 | 2021-11-01
|  | SOV-ELL | Solenoid-Operated Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 921 | Gamma | JNID/IL | 1.62e-13 | 3.69e-10 | 1.51e-09 | 6.92e-09 | 0.3 | 198413000 | 18.7656 | 2006--2020 | 2021-11-01
| Explosive-Operated Valve (EOV) | EOV-FTO | Explosive-Operated Valve Fails To Open | EPIX/RADS | 3 | 673.5 | d | 59 | Beta | EB/PL/KS | 0.000245 | 0.00323 | 0.00462 | 0.0138 | 1.01 | 217 | 4.2671 | 2006--2020 | 2021-11-01
| Vacuum Breaker Valve (VBV) | VBV-FTO | Vacuum Breaker Valve Fails To Open | EPIX/RADS | 1 | 23202 | d | 167 | Beta | JNID/IL | 7.58e-06 | 5.1e-05 | 6.46e-05 | 0.000168 | 1.5 | 23200 | 3.3028 | 2006--2020 | 2021-11-01
|  | VBV-FTC | Vacuum Breaker Valve Fails To Close | EPIX/RADS | 1 | 23202 | d | 167 | Beta | JNID/IL | 7.58e-06 | 5.1e-05 | 6.46e-05 | 0.000168 | 1.5 | 23200 | 3.3028 | 2006--2020 | 2021-11-01
|  | VBV-FTOC | Vacuum Breaker Valve Fails To Open/Close | EPIX/RADS | 2 | 23202 | d | 167 | Beta | JNID/IL | 2.47e-05 | 9.38e-05 | 0.000108 | 0.000239 | 2.5 | 23200 | 2.5439 | 2006--2020 | 2021-11-01
|  | VBV-SOP | Vacuum Breaker Valve Spurious Operation | EPIX/RADS | 0 | 43685040 | h | 343 | Gamma | JNID/IL | 4.5e-11 | 5.21e-09 | 1.14e-08 | 4.4e-08 | 0.5 | 43700000 | 8.4439 | 2006--2020 | 2021-11-01
|  | VBV-ILS | Vacuum Breaker Valve Internal Leakage (Small) | EPIX/RADS | 2 | 43685040 | h | 343 | Gamma | JNID/IL | 1.31e-08 | 4.98e-08 | 5.72e-08 | 1.27e-07 | 2.5 | 43700000 | 2.5441 | 2006--2020 | 2021-11-01
|  | VBV-ILL | Vacuum Breaker Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 343 | Gamma | JNID/IL | 1.22e-13 | 2.79e-10 | 1.14e-09 | 5.23e-09 | 0.3 | 262238000 | 18.7656 | 2006--2020 | 2021-11-01
| Turbine Bypass Valve (TBV) | TBV-FTO | Turbine Bypass Valve Fails To Open | EPIX/RADS | 1 | 2367 | d | 73 | Beta | JNID/IL | 7.42e-05 | 0.000499 | 0.000633 | 0.00165 | 1.5 | 2370 | 3.3011 | 2006--2020 | 2021-11-01
|  | TBV-FTC | Turbine Bypass Valve Fails To Close | EPIX/RADS | 0 | 2367 | d | 73 | Beta | JNID/IL | 8.3e-07 | 9.6e-05 | 0.000211 | 0.00081 | 0.5 | 2370 | 8.4409 | 2006--2020 | 2021-11-01
|  | TBV-FTOC | Turbine Bypass Valve Fails To Open/Close | EPIX/RADS | 1 | 2367 | d | 73 | Beta | JNID/IL | 7.42e-05 | 0.000499 | 0.000633 | 0.00165 | 1.5 | 2370 | 3.3011 | 2006--2020 | 2021-11-01
|  | TBV-FC | Turbine Bypass Valve Fails To Control | EPIX/RADS | 6 | 19263540 | h | 153 | Gamma | EB/PL/KS | 1.29e-09 | 1.6e-07 | 3.57e-07 | 1.38e-06 | 0.492 | 1380000 | 8.6161 | 2006--2020 | 2021-11-01
| Main Steam Isolation Valve (MSV) | MSV-FTOC | Main Steam Isolation Valve Fails To Open/Close | EPIX/RADS | 24 | 32198.9 | d | 425 | Beta | JNID/IL | 0.000527 | 0.00075 | 0.000761 | 0.00103 | 24.5 | 32200 | 1.3723 | 2006--2020 | 2021-11-01
|  | MSV-SOP | Main Steam Isolation Valve Spurious Operation | EPIX/RADS | 16 | 65768320 | h | 520 | Gamma | EB/PL/KS | 9.3e-10 | 1.07e-07 | 2.34e-07 | 8.99e-07 | 0.501 | 2140000 | 8.423 | 2006--2020 | 2021-11-01
|  | MSV-ILS | Main Steam Isolation Valve Internal Leakage (Small) | EPIX/RADS | 23 | 65768320 | h | 520 | Gamma | JNID/IL | 2.45e-07 | 3.52e-07 | 3.57e-07 | 4.86e-07 | 23.5 | 65800000 | 1.3813 | 2006--2020 | 2021-11-01
|  | MSV-ILL | Main Steam Isolation Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 520 | Gamma | JNID/IL | 7.64e-13 | 1.74e-09 | 7.14e-09 | 3.27e-08 | 0.3 | 42016800 | 18.7656 | 2006--2020 | 2021-11-01
|  | MSV-ELS | Main Steam Isolation Valve External Leakage (Small) | EPIX/RADS | 1 | 65768320 | h | 520 | Gamma | JNID/IL | 2.67e-09 | 1.8e-08 | 2.28e-08 | 5.94e-08 | 1.5 | 65800000 | 3.303 | 2006--2020 | 2021-11-01
|  | MSV-ELL | Main Steam Isolation Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 520 | Gamma | JNID/IL | 1.71e-13 | 3.89e-10 | 1.6e-09 | 7.3e-09 | 0.3 | 187970000 | 18.7656 | 2006--2020 | 2021-11-01
| Check Valve (CKV) | CKV-FTO | Check Valve Fails To Open | EPIX/RADS | 0 | 44791.1 | d | 489 | Beta | JNID/IL | 4.39e-08 | 5.08e-06 | 1.12e-05 | 4.29e-05 | 0.5 | 44800 | 8.4438 | 2006--2020 | 2021-11-01
|  | CKV-FTC | Check Valve Fails To Close | EPIX/RADS | 5 | 44791.1 | d | 489 | Beta | JNID/IL | 5.11e-05 | 0.000115 | 0.000123 | 0.00022 | 5.5 | 44800 | 1.9025 | 2006--2020 | 2021-11-01
|  | CKV-SOP | Check Valve Spurious Operation | EPIX/RADS | 0 | 806744700 | h | 6379 | Gamma | JNID/IL | 2.44e-12 | 2.82e-10 | 6.2e-10 | 2.38e-09 | 0.5 | 807000000 | 8.4439 | 2006--2020 | 2021-11-01
|  | CKV-ILS | Check Valve Internal Leakage (Small) | EPIX/RADS | 58 | 806744700 | h | 6379 | Gamma | JNID/IL | 5.76e-08 | 7.21e-08 | 7.25e-08 | 8.88e-08 | 58.5 | 807000000 | 1.2313 | 2006--2020 | 2021-11-01
|  | CKV-ILL | Check Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 6379 | Gamma | JNID/IL | 1.55e-13 | 3.53e-10 | 1.45e-09 | 6.63e-09 | 0.3 | 206897000 | 18.7656 | 2006--2020 | 2021-11-01
|  | CKV-ELS | Check Valve External Leakage (Small) | EPIX/RADS | 3 | 806744700 | h | 6379 | Gamma | JNID/IL | 1.34e-09 | 3.93e-09 | 4.34e-09 | 8.72e-09 | 3.5 | 807000000 | 2.2168 | 2006--2020 | 2021-11-01
|  | CKV-ELL | Check Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 6379 | Gamma | JNID/IL | 3.25e-14 | 7.41e-11 | 3.04e-10 | 1.39e-09 | 0.3 | 987492000 | 18.7656 | 2006--2020 | 2021-11-01
| Manual Valve (XVM) | XVM-FTOC | Manual Valve Fails To Open | EPIX/RADS | 1 | 2874.6 | d | 66 | Beta | JNID/IL | 6.13e-05 | 0.000412 | 0.000522 | 0.00136 | 1.5 | 2870 | 3.3014 | 2006--2020 | 2021-11-01
|  | XVM-SOP | Manual Valve Spurious Operation | EPIX/RADS | 2 | 132674000 | h | 1035 | Gamma | JNID/IL | 4.31e-09 | 1.64e-08 | 1.88e-08 | 4.16e-08 | 2.5 | 133000000 | 2.5441 | 2006--2020 | 2021-11-01
|  | XVM-ILS | Manual Valve Internal Leakage (Small) | EPIX/RADS | 3 | 132674000 | h | 1035 | Gamma | JNID/IL | 8.15e-09 | 2.39e-08 | 2.64e-08 | 5.29e-08 | 3.5 | 133000000 | 2.2168 | 2006--2020 | 2021-11-01
|  | XVM-ILL | Manual Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1035 | Gamma | JNID/IL | 5.65e-14 | 1.29e-10 | 5.28e-10 | 2.42e-09 | 0.3 | 568182000 | 18.7656 | 2006--2020 | 2021-11-01
|  | XVM-ELS | Manual Valve External Leakage (Small) | EPIX/RADS | 11 | 132674000 | h | 1035 | Gamma | JNID/IL | 4.92e-08 | 8.4e-08 | 8.67e-08 | 1.32e-07 | 11.5 | 133000000 | 1.5746 | 2006--2020 | 2021-11-01
|  | XVM-ELL | Manual Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1035 | Gamma | JNID/IL | 6.5e-13 | 1.48e-09 | 6.07e-09 | 2.78e-08 | 0.3 | 49431500 | 18.7656 | 2006--2020 | 2021-11-01
|  | XVM-SOP-SWS | Standby Service Water Manual Valve Spuriously Transfers | EPIX/RADS | 0 | 18055700 | h | 140 | Gamma | JNID/IL | 1.09e-10 | 1.26e-08 | 2.77e-08 | 1.06e-07 | 0.5 | 18100000 | 8.4439 | 2006--2020 | 2021-11-01
| Flow Control Valve (FCV) | FCV-FTOC | Flow Control Valve Fails To Open/Close | EPIX/RADS | 0 | 11345 | d | 105 | Beta | JNID/IL | 1.74e-07 | 2.01e-05 | 4.41e-05 | 0.00017 | 0.5 | 11300 | 8.4433 | 2006--2020 | 2021-11-01
|  | FCV-FC | Flow Control Valve Fails To Control | EPIX/RADS | 8 | 73637280 | h | 595 | Gamma | JNID/IL | 5.89e-08 | 1.11e-07 | 1.15e-07 | 1.87e-07 | 8.5 | 73600000 | 1.6885 | 2006--2020 | 2021-11-01
|  | FCV-SOP | Flow Control Valve Spurious Operation | EPIX/RADS | 2 | 73637280 | h | 595 | Gamma | JNID/IL | 7.78e-09 | 2.96e-08 | 3.4e-08 | 7.52e-08 | 2.5 | 73600000 | 2.5441 | 2006--2020 | 2021-11-01
|  | FRV-FTOP | Feedwater Regulating Valve Fails To Operate | EPIX/RADS | 49 | 27637200 | h | 221 | Gamma | EB/PL/KS | 2.71e-08 | 1.06e-06 | 1.88e-06 | 6.52e-06 | 0.666 | 354000 | 6.1392 | 2006--2020 | 2021-11-01
Pumps | Motor-Driven Pump (MDP) | MDP-FTS-NS | Motor-Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 227 | 410593.4 | d | 1311 | Beta | EB/PL/KS | 0.000109 | 0.000496 | 0.000588 | 0.00138 | 2.07 | 3520 | 2.7775 | 2006--2020 | 2021-11-01
|  | MDP-FTR<1H | Motor-Driven Pump FTR<1H | EPIX/RADS | 31 | 378369.4 | h | 1305 | Gamma | EB/PL/KS | 7.34e-07 | 4.68e-05 | 9.13e-05 | 0.000333 | 0.579 | 6340 | 7.1097 | 2006--2020 | 2021-11-01
|  | MDP-FTR>1H | Motor-Driven Pump FTR>1H | EPIX/RADS | 92 | 19248030 | h | 1311 | Gamma | EB/PL/KS | 3.58e-08 | 3.77e-06 | 8.12e-06 | 3.1e-05 | 0.511 | 62900 | 8.2206 | 2006--2020 | 2021-11-01
|  | MDP-ELS | Motor-Driven Pump External Leakage (Small) | EPIX/RADS | 59 | 288839600 | h | 2351 | Gamma | EB/PL/KS | 3.16e-09 | 1.14e-07 | 1.98e-07 | 6.8e-07 | 0.684 | 3450000 | 5.9802 | 2006--2020 | 2021-11-01
|  | MDP-ELL | Motor-Driven Pump External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 2351 | Gamma | EB/PL/KS | 1.48e-12 | 3.38e-09 | 1.39e-08 | 6.34e-08 | 0.3 | 21645000 | 18.7656 | 2006--2020 | 2021-11-01
|  | MDP-FTS-NR | Motor-Driven Pump Fails To Start, Normally Running | EPIX/RADS | 89 | 125004.6 | d | 649 | Beta | EB/PL/KS | 4.86e-05 | 0.000562 | 0.000786 | 0.0023 | 1.08 | 1370 | 4.0817 | 2006--2020 | 2021-11-01
|  | MDP-FTR-NR | Motor-Driven Pump Fails To Run, Normally Running | EPIX/RADS | 129 | 56750330 | h | 650 | Gamma | EB/PL/KS | 3.94e-07 | 1.89e-06 | 2.26e-06 | 5.38e-06 | 1.97 | 872000 | 2.848 | 2006--2020 | 2021-11-01
|  | MDP-FTS-CCW | Component Cooling Water Motor-Driven Pump Fails To Start | EPIX/RADS | 31 | 80066.8 | h | 288 | Beta | EB/PL/KS | 1.23e-05 | 0.000286 | 0.000457 | 0.00149 | 0.796 | 1740 | 5.1959 | 2006--2020 | 2021-11-01
|  | MDP-FTR-CCW | Component Cooling Water Motor-Driven Pump Fails To Run | EPIX/RADS | 31 | 17527790 | h | 288 | Gamma | EB/PL/KS | 2.86e-07 | 1.47e-06 | 1.77e-06 | 4.33e-06 | 1.85 | 1040000 | 2.9413 | 2006--2020 | 2021-11-01
|  | MDP-FTS-SWS | Service Water Motor-Driven Pump Fails To Start | EPIX/RADS | 132 | 225635.6 | d | 529 | Beta | EB/PL/KS | 2.43e-05 | 0.00048 | 0.000743 | 0.00236 | 0.848 | 1140 | 4.9204 | 2006--2020 | 2021-11-01
|  | MDP-FTR-SWS | Service Water Motor-Driven Pump Fails To Run | EPIX/RADS | 100 | 25635460 | h | 529 | Gamma | EB/PL/KS | 3.09e-07 | 3.08e-06 | 4.2e-06 | 1.19e-05 | 1.17 | 279000 | 3.8637 | 2006--2020 | 2021-11-01
|  | MDP-FTR-CWS | Circulating Water Motor-Driven Pump Fails To Run | EPIX/RADS | 15 | 3116679 | h | 31 | Gamma | EB/PL/KS | 1.81e-06 | 4.51e-06 | 4.86e-06 | 9.09e-06 | 4.57 | 941000 | 2.0176 | 2006--2020 | 2021-11-01
| Turbine-Driven Pump (TDP) | TDP-FTS-NS | Turbine-Driven Pump Fails To Start (Pooled Systems), Normally Standby | EPIX/RADS | 105 | 22511.5 | d | 133 | Beta | EB/PL/KS | 0.000459 | 0.00402 | 0.00532 | 0.0147 | 1.26 | 235 | 3.6584 | 2006--2020 | 2021-11-01
|  | TDP-FTR<1H | Turbine-Driven Pump Fails To Run (Pooled Systems), Early Term | EPIX/RADS | 34 | 15529.6 | h | 133 | Gamma | EB/PL/KS | 5.17e-06 | 0.00104 | 0.00256 | 0.0103 | 0.444 | 173 | 9.8613 | 2006--2020 | 2021-11-01
|  | TDP-FTR>1H | Turbine-Driven Pump Fails To Run (Pooled Systems), Late Term | EPIX/RADS | 17 | 4454.3 | h | 133 | Gamma | EB/PL/KS | 1.23e-05 | 0.00256 | 0.00635 | 0.0255 | 0.441 | 69.5 | 9.9538 | 2006--2020 | 2021-11-01
|  | TDP-ELS | Turbine-Driven Pump External Leakage (Small) | EPIX/RADS | 10 | 24190380 | h | 191 | Gamma | EB/PL/KS | 7.42e-08 | 3.47e-07 | 4.13e-07 | 9.75e-07 | 2.02 | 4900000 | 2.8125 | 2006--2020 | 2021-11-01
|  | TDP-ELL | Turbine Bypass Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 191 | Gamma | EB/PL/KS | 3.09e-12 | 7.05e-09 | 2.89e-08 | 1.32e-07 | 0.3 | 10377000 | 18.7656 | 2006--2020 | 2021-11-01
|  | TDP-FTS-NS-AFW | Auxiliary Feedwater Turbine-Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 52 | 15672.4 | d | 74 | Beta | EB/PL/KS | 0.000117 | 0.00243 | 0.00379 | 0.0121 | 0.831 | 218 | 4.9854 | 2006--2020 | 2021-11-01
|  | TDP-FTR<1H-AFW | Auxiliary Feedwater Turbine-Driven Pump FTR<1H | EPIX/RADS | 18 | 10670.1 | h | 74 | Gamma | JNID/IL | 0.00112 | 0.0017 | 0.00173 | 0.00244 | 18.5 | 10700 | 1.4364 | 2006--2020 | 2021-11-01
|  | TDP-FTR>1H-AFW | Auxiliary Feedwater Turbine-Driven Pump FTR>1H | EPIX/RADS | 8 | 3295.2 | h | 74 | Gamma | JNID/IL | 0.00131 | 0.00248 | 0.00258 | 0.00418 | 8.5 | 3300 | 1.6885 | 2006--2020 | 2021-11-01
|  | TDP-FTS-NS-HCI-RCI | HCI-RCI Turbine-Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 25 | 4025.6 | d | 31 | Beta | EB/PL/KS | 0.000602 | 0.00507 | 0.00668 | 0.0182 | 1.29 | 192 | 3.5987 | 2006--2020 | 2021-11-01
|  | TDP-FTR<1H-HCI-RCI | HCI Turbine-Driven Pump FTR<1H | EPIX/RADS | 16 | 4859.5 | h | 59 | Gamma | EB/PL/KS | 0.000673 | 0.00286 | 0.00335 | 0.00768 | 2.22 | 664 | 2.6866 | 2006--2020 | 2021-11-01
|  | TDP-FTR>1H-HCI-RCI | HCI-RCI Turbine-Driven Pump FTR>1H | EPIX/RADS | 9 | 1159.1 | h | 59 | Gamma | JNID/IL | 0.00436 | 0.0079 | 0.0082 | 0.013 | 9.5 | 1160 | 1.6438 | 2006--2020 | 2021-11-01
|  | TDP-FTS-NR-MFW | Main Feedwater Turbine-Driven Pump Fails To Start, Normally Running | EPIX/RADS | 5 | 1147.3 | d | 42 | Beta | EB/PL/KS | 5.45e-05 | 0.00252 | 0.0046 | 0.0162 | 0.633 | 137 | 6.4192 | 2006--2020 | 2021-11-01
|  | TDP-FTR-NR-MFW | Main Feedwater Turbine-Driven Pump Fails To Run, Normally Running | EPIX/RADS | 39 | 4938575 | h | 42 | Gamma | EB/PL/KS | 2.53e-07 | 5.37e-06 | 8.45e-06 | 2.71e-05 | 0.824 | 97600 | 5.046 | 2006--2020 | 2021-11-01
| Engine-Driven Pump (EDP) | EDP-FTS-NS | Engine-Driven Pump Fails To Start, Normally Standby | EPIX/RADS | 13 | 17772.6 | d | 44 | Beta | JNID/IL | 0.000453 | 0.000739 | 0.00076 | 0.00113 | 13.5 | 17800 | 1.5228 | 2006--2020 | 2021-11-01
|  | EDP-FTR<1H | Engine-Driven Pump FTR<1H, Normally Standby | EPIX/RADS | 6 | 9888.4 | h | 39 | Gamma | JNID/IL | 0.000298 | 0.000624 | 0.000657 | 0.00113 | 6.5 | 9890 | 1.8122 | 2006--2020 | 2021-11-01
|  | EDP-FTR>1H | Engine-Driven Pump FTR>1H, Normally Standby | EPIX/RADS | 15 | 4753.5 | h | 44 | Gamma | JNID/IL | 0.00203 | 0.00319 | 0.00326 | 0.00474 | 15.5 | 4750 | 1.4829 | 2006--2020 | 2021-11-01
|  | EDP-ELS | Engine-Driven Pump External Leakage (Small) | EPIX/RADS | 6 | 7690189 | h | 69 | Gamma | JNID/IL | 3.83e-07 | 8.02e-07 | 8.45e-07 | 1.45e-06 | 6.5 | 7690000 | 1.8122 | 2006--2020 | 2021-11-01
|  | EDP-ELL | Engine-Driven Pump External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 69 | Gamma | JNID/IL | 6.33e-12 | 1.44e-08 | 5.92e-08 | 2.71e-07 | 0.3 | 5071850 | 18.7656 | 2006--2020 | 2021-11-01
|  | EDP-FTS-AFW | Auxiliary Feedwater Engine-driven pump Fails To Start | EPIX/RADS | 1 | 1163.2 | d | 5 | Beta | JNID/IL | 0.000152 | 0.00102 | 0.00129 | 0.00336 | 1.5 | 1160 | 3.2991 | 2006--2020 | 2021-11-01
|  | EDP-FTR<1H-AFW | Auxiliary Feedwater Engine-driven pump Fails To Run <1H | EPIX/RADS | 2 | 759.4 | h | 5 | Gamma | JNID/IL | 0.000755 | 0.00287 | 0.00329 | 0.00729 | 2.5 | 759 | 2.5441 | 2006--2020 | 2021-11-01
|  | EDP-FTR>1H-AFW | Auxiliary Feedwater Engine-driven pump Fails To Run >1H | EPIX/RADS | 2 | 234.4 | h | 5 | Gamma | JNID/IL | 0.00245 | 0.0093 | 0.0107 | 0.0237 | 2.5 | 234 | 2.5441 | 2006--2020 | 2021-11-01
| Positive Displacement Pump (PDP) | PDP-FTS-NR | Positive Displacement Pump Fails To Start, Normally Running | EPIX/RADS | 53 | 28865.4 | d | 57 | Beta | EB/PL/KS | 7.46e-05 | 0.00158 | 0.00247 | 0.00792 | 0.825 | 333 | 5.0248 | 2006--2020 | 2021-11-01
|  | PDP-FTR-NR | Positive Displacement Pump Fails To Run, Normally Running | EPIX/RADS | 40 | 2353162 | h | 54 | Gamma | EB/PL/KS | 1.81e-06 | 1.45e-05 | 1.91e-05 | 5.17e-05 | 1.33 | 69800 | 3.5532 | 2006--2020 | 2021-11-01
|  | PDP-FTS-NS | Positive Displacement Pump Fails To Start, Normally Standby | EPIX/RADS | 10 | 9064 | d | 72 | Beta | JNID/IL | 0.00064 | 0.00112 | 0.00116 | 0.0018 | 10.5 | 9050 | 1.6059 | 2006--2020 | 2021-11-01
|  | PDP-FTR<1H | Positive Displacement Pump FTR<1H | EPIX/RADS | 1 | 4045.1 | h | 72 | Gamma | JNID/IL | 4.34e-05 | 0.000292 | 0.000371 | 0.000965 | 1.5 | 4050 | 3.303 | 2006--2020 | 2021-11-01
|  | PDP-FTR>1H | Positive Displacement Pump FTR>1H | EPIX/RADS | 0 | 1504.8 | h | 72 | Gamma | JNID/IL | 1.31e-06 | 0.000152 | 0.000332 | 0.00128 | 0.5 | 1500 | 8.4439 | 2006--2020 | 2021-11-01
|  | PDP-ELS | Positive Displacement Pump External Leakage (Small) | EPIX/RADS | 15 | 21211980 | h | 171 | Gamma | JNID/IL | 4.55e-07 | 7.15e-07 | 7.31e-07 | 1.06e-06 | 15.5 | 21200000 | 1.4829 | 2006--2020 | 2021-11-01
|  | PDP-ELL | Positive Displacement Pump External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 171 | Gamma | JNID/IL | 5.48e-12 | 1.25e-08 | 5.12e-08 | 2.34e-07 | 0.3 | 5862810 | 18.7656 | 2006--2020 | 2021-11-01
| Pump Volute (PMP) | PMP-Volute | Pump Volute Fails To Run (Driver Independent Centrifugal Pumps) | EPIX/RADS | 16 | 133247.1 | h | 208 | Gamma | JNID/IL | 7.84e-05 | 0.000122 | 0.000124 | 0.000178 | 16.5 | 133000 | 1.4659 | 2006--2020 | 2021-11-01
Generators | Emergency Diesel Generator (EDG) | EDG-FTS | Diesel Generator Fails To Start, Normally Standby | EPIX/RADS | 136 | 61362.8 | d | 234 | Beta | EB/PL/KS | 0.00153 | 0.00219 | 0.00222 | 0.00302 | 23.8 | 10700 | 1.378 | 2006--2020 | 2021-11-01
|  | EDG-FTLR | Diesel Generator Fails To Load And Run, Early | EPIX/RADS | 172 | 53342.6 | h | 234 | Gamma | EB/PL/KS | 0.00105 | 0.00301 | 0.00331 | 0.0066 | 3.61 | 1090 | 2.1913 | 2006--2020 | 2021-11-01
|  | EDG-FTR | Diesel Generator Fails To Run, Late Term | EPIX/RADS | 155 | 137584.3 | h | 234 | Gamma | EB/PL/KS | 0.00039 | 0.00108 | 0.00118 | 0.00231 | 3.83 | 3250 | 2.1445 | 2006--2020 | 2021-11-01
| Hydro Turbine Generator (HTG) | HTG-FTS | Hydro Turbine Generator Fails To Start | EPIX/RADS | 6 | 6361.6 | d | 2 | Beta | JNID/IL | 0.000463 | 0.000969 | 0.00102 | 0.00176 | 6.5 | 6360 | 1.8115 | 2006--2020 | 2021-11-01
|  | HTG-FTLR | Hydro Turbine Generator Fails To Load And Run, Early | EPIX/RADS | 2 | 4582.2 | h | 2 | Gamma | JNID/IL | 0.000125 | 0.000475 | 0.000546 | 0.00121 | 2.5 | 4580 | 2.5441 | 2006--2020 | 2021-11-01
|  | HTG-FTR | Hydro Turbine Generator Fails To Run, Late Term | EPIX/RADS | 1 | 13874.4 | h | 2 | Gamma | JNID/IL | 1.27e-05 | 8.51e-05 | 0.000108 | 0.000281 | 1.5 | 13900 | 3.303 | 2006--2020 | 2021-11-01
| Combustion Turbine Generator (CTG) | CTG-FTS | Combustion Turbine Generator Fails To Start, Normally Standby | EPIX/RADS | 21 | 419.4 | d | 3 | Beta | EB/PL/KS | 0.00581 | 0.054 | 0.0703 | 0.19 | 1.2 | 15.9 | 3.5208 | 2006--2020 | 2021-11-01
|  | CTG-FTLR | Combustion Turbine Generator Fails To Load And Run, Early Term | EPIX/RADS | 2 | 360 | d | 2 | Gamma | JNID/IL | 0.00159 | 0.00604 | 0.00694 | 0.0154 | 2.5 | 360 | 2.5441 | 2006--2020 | 2021-11-01
|  | CTG-FTR | Combustion Turbine Generator Fails To Run, Late Term | EPIX/RADS | 4 | 959.4 | h | 3 | Gamma | JNID/IL | 0.00173 | 0.00435 | 0.00469 | 0.00882 | 4.5 | 959 | 2.028 | 2006--2020 | 2021-11-01
| High-Pressure Core Spray Generator (HPCS) | EDG-FTS-HCS | High-Pressure Core Spray Generator Fails To Start | EPIX/RADS | 4 | 2114.1 | d | 8 | Beta | JNID/IL | 0.000787 | 0.00197 | 0.00213 | 0.004 | 4.5 | 2110 | 2.0259 | 2006--2020 | 2021-11-01
|  | EDG-FTR-HCS | High-Pressure Core Spray Generator Fails To Run | EPIX/RADS | 3 | 4195.5 | h | 8 | Gamma | JNID/IL | 0.000258 | 0.000755 | 0.000834 | 0.00167 | 3.5 | 4200 | 2.2168 | 2006--2020 | 2021-11-01
| Station Blackout Generator (SBO) | EDG-FTS-SBO | SBO Generator Fails To Start | EPIX/RADS | 14 | 625.1 | d | 5 | Beta | EB/PL/KS | 0.00146 | 0.0206 | 0.0294 | 0.0875 | 0.975 | 32.2 | 4.2537 | 2006--2020 | 2021-11-01
|  | EDG-FTR-SBO | SBO Generator Fails To Run | EPIX/RADS | 2 | 2203.7 | h | 5 | Gamma | JNID/IL | 0.00026 | 0.000989 | 0.00113 | 0.00252 | 2.5 | 2200 | 2.5441 | 2006--2020 | 2021-11-01
Relief Valves | Safety Relief Valve (SRV) | SRV-FTO | Safety relief valve fails To open | RV Update, Table 26. | 7 | 3548 | d | -- | Beta | JNID | 0.00102 | 0.00202 | 0.00211 | 0.00352 | 7.5 | 3541.5 | 1.7419 | 1988--2020 | 2021-09-16
|  | SRV-FTC | BWR ADS/SRV Fails To Reclose | RV Update, Table 26. | 0 | 3548 | d | -- | Beta | CNID | 5.54e-07 | 6.41e-05 | 0.000141 | 0.000541 | 0.5 | 3547 | 8.4419 | 1988--2020 | 2021-09-16
|  | SRV-FC | Safety Relief Valve (BWR Only) Fails To Control | EPIX/RADS | 0 | 61005550 | h | 519 | Gamma | JNID/IL | 3.22e-11 | 3.73e-09 | 8.2e-09 | 3.15e-08 | 0.5 | 61000000 | 8.4439 | 2006--2020 | 2021-11-01
|  | SRV-SOP | Safety Relief Valve Spurious Operation | EPIX/RADS | 4 | 61005550 | h | 519 | Gamma | JNID/IL | 2.73e-08 | 6.84e-08 | 7.38e-08 | 1.39e-07 | 4.5 | 61000000 | 2.028 | 2006--2020 | 2021-11-01
|  | SRV-ILS | Safety Relief Valve (BWR Only) Internal Leakage (Small) | EPIX/RADS | 23 | 61005550 | h | 519 | Gamma | JNID/IL | 2.64e-07 | 3.8e-07 | 3.85e-07 | 5.25e-07 | 23.5 | 61000000 | 1.3813 | 2006--2020 | 2021-11-01
|  | SRV-ILL | Safety Relief Valve (BWR Only) Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 519 | Gamma | JNID/IL | 8.24e-13 | 1.88e-09 | 7.7e-09 | 3.52e-08 | 0.3 | 38961000 | 18.7656 | 2006--2020 | 2021-11-01
|  | SRV-ELS | Safety Relief Valve (BWR Only) External Leakage (Small) | EPIX/RADS | 0 | 61005550 | h | 519 | Gamma | JNID/IL | 3.22e-11 | 3.73e-09 | 8.2e-09 | 3.15e-08 | 0.5 | 61000000 | 8.4439 | 2006--2020 | 2021-11-01
|  | SRV-ELL | Safety Relief Valve (BWR Only) External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 519 | Gamma | JNID/IL | 6.14e-14 | 1.4e-10 | 5.74e-10 | 2.63e-09 | 0.3 | 522648000 | 18.7656 | 2006--2020 | 2021-11-01
| Safety Valve (SVV) | SVV-SOP | Code Safety Valve Spurious Operation | EPIX/RADS | 1 | 171647800 | h | 1380 | Gamma | JNID/IL | 1.02e-09 | 6.88e-09 | 8.74e-09 | 2.27e-08 | 1.5 | 172000000 | 3.303 | 2006--2020 | 2021-11-01
|  | SVV-ILS | Code Safety Valve Internal Leakage (Small) | EPIX/RADS | 5 | 171647800 | h | 1380 | Gamma | JNID/IL | 1.33e-08 | 3.01e-08 | 3.2e-08 | 5.72e-08 | 5.5 | 172000000 | 1.9026 | 2006--2020 | 2021-11-01
|  | SVV-ILL | Code Safety Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1380 | Gamma | JNID/IL | 6.85e-14 | 1.56e-10 | 6.4e-10 | 2.93e-09 | 0.3 | 468750000 | 18.7656 | 2006--2020 | 2021-11-01
|  | SVV-ELS | Code Safety Valve External Leakage (Small) | EPIX/RADS | 1 | 171647800 | h | 1380 | Gamma | JNID/IL | 1.02e-09 | 6.88e-09 | 8.74e-09 | 2.27e-08 | 1.5 | 172000000 | 3.303 | 2006--2020 | 2021-11-01
|  | SVV-ELL | Code Safety Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1380 | Gamma | JNID/IL | 6.55e-14 | 1.49e-10 | 6.12e-10 | 2.8e-09 | 0.3 | 490356000 | 18.7656 | 2006--2020 | 2021-11-01
|  | SVV-FTO-PWR-MSS | Safety Valve Fails To Open+D174 PWRs) | RV Update, Table 24. | 0 | 745 | d | -- | Beta | CNID | 2.61e-06 | 0.000305 | 0.00067 | 0.00258 | 0.499 | 744.001 | 8.4554 | 1988--2020 | 2021-09-16
|  | SVV-FTC-PWR-MSS | Safety Valve Fails To Close (Main Steam System, PWRs) | RV Update, Table 24. | 4 | 745 | d | -- | Beta | JNID | 0.00223 | 0.0056 | 0.00603 | 0.0113 | 4.5 | 741.5 | 2.0221 | 1988--2020 | 2021-09-16
|  | SVV-SOP-PWR-MSS | Safety Valve Spurious Operation (Main Steam System, PWRs) | EPIX/RADS | 0 | 140068800 | h | 1109 | Gamma | JNID/IL | 1.4e-11 | 1.62e-09 | 3.57e-09 | 1.37e-08 | 0.5 | 140000000 | 8.4439 | 2006--2020 | 2021-11-01
|  | SVV-FTO-PWR-RCS | Safety Valve Fails To Open (Reactor Coolant System, PWRs) | RV Update, Table 25. | 0 | 4 | d | -- | Beta | Bayes | 2.58e-06 | 0.000301 | 0.000663 | 0.00255 | 0.499 | 752.001 | 8.4555 | 1988--2020 | 2021-09-16
|  | SVV-FTC-PWR-RCS | Safety Valve Fails To Close (Reactor Coolant System, PWRs) | RV Update, Table 25. | 2 | 4 | d | -- | Beta | Bayes | 0.00965 | 0.0363 | 0.0413 | 0.0901 | 2.487 | 57.689 | 2.4788 | 1988--2020 | 2021-09-16
|  | SVV-SOP-PWR-RCS | Safety Valve Spurious Operation (Reactor Coolant System, PWRs) | EPIX/RADS | 1 | 23893310 | h | 207 | Gamma | JNID/IL | 7.36e-09 | 4.95e-08 | 6.28e-08 | 1.63e-07 | 1.5 | 23900000 | 3.303 | 2006--2020 | 2021-11-01
| Power-Operated Relief Valve (PORV) | PORV-FTO-RCS | Power-Operated Relief Valve Fails To Open (Reactor Coolant System, PWRs) | RV Update, Table 23. | 4 | 377 | d | -- | Beta | JNID | 0.00442 | 0.0111 | 0.0119 | 0.0223 | 4.5 | 373.5 | 2.0165 | 1988--2020 | 2021-09-16
|  | PORV-FTC-RCS | Power-Operated Relief Valve Fails To Close (Reactor Coolant System, PWRs) | RV Update, Table 23. | 1 | 377 | d | -- | Beta | CNID | 1.47e-05 | 0.00179 | 0.00397 | 0.0153 | 0.494 | 124.006 | 8.5142 | 1988--2020 | 2021-09-16
|  | PORV-FTO-MSS | Power-Operated Relief Valve Fails To Open (Main Steam System, PWRs) | RV Update, Table 22. | 25 | 1580 | d | -- | Beta | JNID | 0.0113 | 0.0159 | 0.0161 | 0.0217 | 25.5 | 1555.5 | 1.3603 | 1988--2020 | 2021-09-16
|  | PORV-FTC-MSS | Power-Operated Relief Fails To Close (Main Steam System, PWRs) | RV Update, Table 22. | 7 | 1580 | d | -- | Beta | EB | 0.000254 | 0.00308 | 0.00435 | 0.0128 | 1.053 | 241.155 | 4.1401 | 1988--2020 | 2021-09-16
|  | PORV-FC-MSS | Power-Operated Relief Fails To Control (Cooldown) (Main Steam System, PWRs) | RV Update, Table 22. | 7 | 278 | d | -- | Beta | JNID | 0.0131 | 0.0258 | 0.0269 | 0.0445 | 7.5 | 271.5 | 1.7265 | 1988--2020 | 2021-09-16
|  | PORV-SOP | Power Operated Relief Spurious Operation | EPIX/RADS | 13 | 57223460 | h | 454 | Gamma | JNID/IL | 1.41e-07 | 2.3e-07 | 2.36e-07 | 3.51e-07 | 13.5 | 57200000 | 1.5231 | 2006--2020 | 2021-11-01
|  | PORV-ILS | Power-Operated Relief Valve Internal Leakage (Small) | EPIX/RADS | 3 | 57223460 | h | 454 | Gamma | JNID/IL | 1.89e-08 | 5.55e-08 | 6.12e-08 | 1.23e-07 | 3.5 | 57200000 | 2.2168 | 2006--2020 | 2021-11-01
|  | PORV-ILL | Power-Operated Relief Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 454 | Gamma | JNID/IL | 1.31e-13 | 2.98e-10 | 1.22e-09 | 5.6e-09 | 0.3 | 245098000 | 18.7656 | 2006--2020 | 2021-11-01
|  | PORV-ELS | Power-Operated Relief Valve External Leakage (Small) | EPIX/RADS | 0 | 57223460 | h | 454 | Gamma | JNID/IL | 3.44e-11 | 3.98e-09 | 8.74e-09 | 3.36e-08 | 0.5 | 57200000 | 8.4439 | 2006--2020 | 2021-11-01
|  | PORV-ELL | Power-Operated Relief Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 454 | Gamma | JNID/IL | 6.55e-14 | 1.49e-10 | 6.12e-10 | 2.8e-09 | 0.3 | 490356000 | 18.7656 | 2006--2020 | 2021-11-01
|  | PORV-LOOP | Power-Operated Relief Valves Open During LOOP (Reactor Coolant System, PWRs) | RV Update, Table 13 | -- | -- | d | -- | Point Estimate | Point Estimate | -- | -- | 0.0923 | -- | -- | -- | -- | 1988--2020 | 2021-09-16
|  | PORV-Transient | Power-Operated Relief Valves Open During Transient (Reactor Coolant System, PWRs) | RV Update, Table 13 | -- | -- | d | -- | Point Estimate | Point Estimate | -- | -- | 0.0228 | -- | -- | -- | -- | 1988--2018 | 2021-09-16
| Low-Capacity Relief Valve (RVL) | RVL-FTO | Low Capacity Relief Valve Fails To Open | EPIX/RADS | 0 | 64.9 | d | 12 | Beta | JNID/IL | 3.02e-05 | 0.00349 | 0.00759 | 0.0291 | 0.5 | 65.4 | 8.3352 | 2006--2020 | 2021-11-01
|  | RVL-FTC | Low Capacity Relief Valve Fails To Close | EPIX/RADS | 0 | 64.9 | d | 12 | Beta | JNID/IL | 3.02e-05 | 0.00349 | 0.00759 | 0.0291 | 0.5 | 65.4 | 8.3352 | 2006--2020 | 2021-11-01
|  | RVL-SOP | Low Capacity Relief Valve Spurious Operation | EPIX/RADS | 0 | 9165162 | h | 79 | Gamma | JNID/IL | 2.14e-10 | 2.48e-08 | 5.46e-08 | 2.09e-07 | 0.5 | 9170000 | 8.4439 | 2006--2020 | 2021-11-01
|  | RVL-ILS | Low Capacity Relief Valve Internal Leakage (Small) | EPIX/RADS | 3 | 9165162 | h | 79 | Gamma | JNID/IL | 1.18e-07 | 3.46e-07 | 3.82e-07 | 7.67e-07 | 3.5 | 9170000 | 2.2168 | 2006--2020 | 2021-11-01
|  | RVL-ILL | Low Capacity Relief Valve Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 79 | Gamma | JNID/IL | 8.18e-13 | 1.86e-09 | 7.64e-09 | 3.49e-08 | 0.3 | 39267000 | 18.7656 | 2006--2020 | 2021-11-01
|  | RVL-ELS | Low Capacity Relief Valve External Leakage (Small) | EPIX/RADS | 3 | 9165162 | h | 79 | Gamma | JNID/IL | 1.18e-07 | 3.46e-07 | 3.82e-07 | 7.67e-07 | 3.5 | 9170000 | 2.2168 | 2006--2020 | 2021-11-01
|  | RVL-ELL | Low Capacity Relief Valve External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 79 | Gamma | JNID/IL | 2.86e-12 | 6.52e-09 | 2.67e-08 | 1.22e-07 | 0.3 | 11219100 | 18.7656 | 2006--2020 | 2021-11-01
Electrical Equipment | Battery Charger (BCH) | BCH-FTOP | Battery Charger Fails To Operate | EPIX/RADS | 161 | 99754050 | h | 781 | Gamma | EB/PL/KS | 1.09e-07 | 1.26e-06 | 1.76e-06 | 5.15e-06 | 1.08 | 612000 | 4.0852 | 2006--2020 | 2021-11-01
| Battery (BAT) | BAT-FTOP | Battery Fails To Operate | EPIX/RADS | 21 | 52018730 | h | 412 | Gamma | EB/PL/KS | 4.79e-09 | 2.21e-07 | 4.05e-07 | 1.42e-06 | 0.634 | 1570000 | 6.4531 | 2006--2020 | 2021-11-01
| Automatic Bus Transfer Switch (ABT) | ABT-FF | Automatic Power Transfer Switch Fails To Transfer | EPIX/RADS | 4 | 3376.8 | d | 27 | Beta | JNID/IL | 0.000493 | 0.00124 | 0.00133 | 0.00251 | 4.5 | 3370 | 2.0267 | 2006--2020 | 2021-11-01
|  | ABT-SOP | Automatic Power Transfer Switch Spurious Operation | EPIX/RADS | 0 | 4010342 | h | 32 | Gamma | JNID/IL | 4.9e-10 | 5.67e-08 | 1.25e-07 | 4.79e-07 | 0.5 | 4010000 | 8.4439 | 2006--2020 | 2021-11-01
| Circuit Breaker (CBK) | CRB-FTOC | Circuit Breaker Fails To Open/Close | EPIX/RADS | 102 | 119026.7 | d | 3461 | Beta | EB/PL/KS | 4.23e-05 | 0.000991 | 0.00159 | 0.00516 | 0.793 | 499 | 5.2053 | 2006--2020 | 2021-11-01
|  | CRB-SOP | Circuit Breaker (All Voltages) Spurious Operation | EPIX/RADS | 57 | 552883300 | h | 4620 | Gamma | EB/PL/KS | 4.58e-10 | 7.38e-08 | 1.73e-07 | 6.84e-07 | 0.465 | 2680000 | 9.2666 | 2006--2020 | 2021-11-01
|  | CRBHV-FTOC | High Voltage (13.8 and 16 kV) Circuit Breaker Fails To Open/Close | EPIX/RADS | 17 | 9198.2 | d | 244 | Beta | JNID/IL | 0.00122 | 0.00187 | 0.0019 | 0.00271 | 17.5 | 9180 | 1.4498 | 2006--2020 | 2021-11-01
|  | CRBHV-SOP | High Voltage (13.8 and 16 Kv) Circuit Breaker Spurious Operation | EPIX/RADS | 14 | 37600840 | h | 300 | Gamma | JNID/IL | 2.35e-07 | 3.77e-07 | 3.86e-07 | 5.66e-07 | 14.5 | 37600000 | 1.5019 | 2006--2020 | 2021-11-01
|  | CRBMV-FTOC | Medium Voltage (4160 V and 6.9 kV) Circuit Breaker Fails To Open/Close | EPIX/RADS | 57 | 50897.2 | d | 1080 | Beta | EB/PL/KS | 7.09e-06 | 0.00113 | 0.00264 | 0.0104 | 0.466 | 176 | 9.1974 | 2006--2020 | 2021-11-01
|  | CRBMV-SOP | Medium Voltage (4160 v and 6.9 Kv) Circuit Breaker Spurious Operation | EPIX/RADS | 15 | 149457800 | h | 1240 | Gamma | JNID/IL | 6.47e-08 | 1.02e-07 | 1.04e-07 | 1.51e-07 | 15.5 | 149000000 | 1.4829 | 2006--2020 | 2021-11-01
|  | CRB-FTOC-480 | Low Voltage (480 V) Circuit Breaker Fails To Open/Close | EPIX/RADS | 25 | 46175.6 | d | 1752 | Beta | EB/PL/KS | 3.27e-06 | 0.000389 | 0.000857 | 0.0033 | 0.497 | 579 | 8.4951 | 2006--2020 | 2021-11-01
|  | CRB-SOP-480 | Low Voltage (480 V) Circuit Breaker Spurious Operation | EPIX/RADS | 27 | 310690800 | h | 2630 | Gamma | JNID/IL | 6.26e-08 | 8.74e-08 | 8.85e-08 | 1.18e-07 | 27.5 | 311000000 | 1.3493 | 2006--2020 | 2021-11-01
|  | CRBDC-FTOC | DC Circuit Breaker Fails To Open/Close | EPIX/RADS | 5 | 17566.3 | d | 602 | Beta | JNID/IL | 0.00013 | 0.000294 | 0.000313 | 0.000559 | 5.5 | 17600 | 1.9024 | 2006--2020 | 2021-11-01
|  | CRBDC-SOP | DC Circuit Breaker Spurious Operation | EPIX/RADS | 0 | 34938600 | h | 270 | Gamma | JNID/IL | 5.63e-11 | 6.52e-09 | 1.43e-08 | 5.5e-08 | 0.5 | 34900000 | 8.4439 | 2006--2020 | 2021-11-01
| Inverter (INV) | INV-FTOP | Inverter Fails To Operate | EPIX/RADS | 52 | 24269470 | h | 199 | Gamma | EB/PL/KS | 1.73e-07 | 2.41e-06 | 3.49e-06 | 1.05e-05 | 0.986 | 282000 | 4.3681 | 2006--2020 | 2021-11-01
| Bus (BUS) | BUS-FTOP-AC | AC Bus Fails To Operate | EPIX/RADS | 76 | 160545900 | h | 1296 | Gamma | EB/PL/KS | 2.91e-08 | 4.05e-07 | 5.88e-07 | 1.77e-06 | 0.986 | 1680000 | 4.3681 | 2006--2020 | 2021-11-01
|  | BUS-FTOP-DC | DC Bus Fails To Operate | EPIX/RADS | 1 | 2103936 | h | 16 | Gamma | JNID/IL | 8.38e-08 | 5.63e-07 | 7.13e-07 | 1.86e-06 | 1.5 | 2100000 | 3.303 | 2006--2020 | 2021-11-01
| Motor Control Center (MCC) | MCC-FTOP | Motor Control Center Fails To Operate | EPIX/RADS | 7 | 28535130 | h | 217 | Gamma | EB/PL/KS | 1.31e-08 | 1.7e-07 | 2.43e-07 | 7.24e-07 | 1.02 | 4190000 | 4.2586 | 2006--2020 | 2021-11-01
| Transformer (TFM) | TFM-FTOP | Transformer Fails To Operate | EPIX/RADS | 110 | 60181620 | h | 512 | Gamma | EB/PL/KS | 2.58e-07 | 1.55e-06 | 1.93e-06 | 4.88e-06 | 1.63 | 847000 | 3.1495 | 2006--2020 | 2021-11-01
| Sequencer (SEQ) | SEQ-FTOP | Sequencer fails To operate (as a Sub Component of the EDG) | EPIX/RADS | 6 | 61362.8 | d | 234 | Beta | JNID/IL | 4.8e-05 | 0.0001 | 0.000106 | 0.000182 | 6.5 | 61400 | 1.8121 | 2006--2020 | 2021-11-01
| Fuse | FUS-SOP | Fuse Spurious Operation | EPIX/RADS | 1 | 169366800 | h | 1288 | Gamma | JNID/IL | 1.04e-09 | 7e-09 | 8.86e-09 | 2.31e-08 | 1.5 | 169000000 | 3.303 | 2006--2020 | 2021-11-01
Strainers/Filters | Filter (FLT) | STR-FLT-PG-RAW | Strainer Plugging (Dirty water systems) | EPIX/RADS | 6 | 7922615 | h | 62 | Gamma | JNID/IL | 3.72e-07 | 7.79e-07 | 8.2e-07 | 1.41e-06 | 6.5 | 7920000 | 1.8122 | 2006--2020 | 2021-11-01
|  | STR-FLT-ELS | Filter External Leakage (Small) All Systems | EPIX/RADS | 1 | 28097240 | h | 223 | Gamma | JNID/IL | 6.26e-09 | 4.21e-08 | 5.34e-08 | 1.39e-07 | 1.5 | 28100000 | 3.303 | 2006--2020 | 2021-11-01
|  | STR-FLT-ELL | Filter External Leakage (Small) All Systems | NUREG/CR-6928 | (note c) | -- | h | 223 | Gamma | JNID/IL | 4e-13 | 9.11e-10 | 3.74e-09 | 1.71e-08 | 0.3 | 80256800 | 18.7656 | 2006--2020 | 2021-11-01
|  | STR-FLT-PG-CLEAN | Filter Plugging, Clean Systems | EPIX/RADS | 1 | 8161140 | h | 68 | Gamma | JNID/IL | 2.16e-08 | 1.45e-07 | 1.84e-07 | 4.79e-07 | 1.5 | 8160000 | 3.303 | 2006--2020 | 2021-11-01
|  | STR-FLT-BYP-CLEAN | Clean Systems Passive Filter Bypass | EPIX/RADS | 0 | 8161140 | h | 68 | Gamma | JNID/IL | 2.41e-10 | 2.79e-08 | 6.13e-08 | 2.35e-07 | 0.5 | 8160000 | 8.4439 | 2006--2020 | 2021-11-01
|  | STR-FLT-PG-IAS | Instrument Air System Filter Plugs | EPIX/RADS | 0 | 210384 | h | 2 | Gamma | JNID/IL | 9.36e-09 | 1.08e-06 | 2.38e-06 | 9.15e-06 | 0.5 | 210000 | 8.4439 | 2006--2020 | 2021-11-01
| Self-Cleaning Strainer (FLTSC) | STR-FLTSC-PG | Self Cleaning Filter Plugging | EPIX/RADS | 32 | 21560060 | h | 167 | Gamma | JNID/IL | 1.1e-06 | 1.49e-06 | 1.51e-06 | 1.96e-06 | 32.5 | 21600000 | 1.3184 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-BYP | Self Cleaning Filter Bypass | EPIX/RADS | 0 | 21560060 | h | 167 | Gamma | JNID/IL | 9.1e-11 | 1.05e-08 | 2.32e-08 | 8.89e-08 | 0.5 | 21600000 | 8.4439 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-FTOP | Self Cleaning Filter Fails To Operate | EPIX/RADS | 53 | 21560060 | h | 167 | Gamma | JNID/IL | 1.95e-06 | 2.46e-06 | 2.48e-06 | 3.06e-06 | 53.5 | 21600000 | 1.2427 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-ELS | Self Cleaning Filter External Leakage (Small) | EPIX/RADS | 2 | 21560060 | h | 167 | Gamma | JNID/IL | 2.65e-08 | 1.01e-07 | 1.16e-07 | 2.56e-07 | 2.5 | 21600000 | 2.5441 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-ELL | Self Cleaning Filter External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 167 | Gamma | JNID/IL | 8.69e-13 | 1.98e-09 | 8.12e-09 | 3.71e-08 | 0.3 | 36945800 | 18.7656 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-PG-SWN | Normally Running Service Water Strainer Plugs | EPIX/RADS | 19 | 13235010 | h | 103 | Gamma | JNID/IL | 9.73e-07 | 1.45e-06 | 1.47e-06 | 2.07e-06 | 19.5 | 13200000 | 1.4235 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-PG-SSW | Standby Service Water Strainer Plugs | EPIX/RADS | 13 | 7799060 | h | 60 | Gamma | JNID/IL | 1.04e-06 | 1.69e-06 | 1.73e-06 | 2.57e-06 | 13.5 | 7800000 | 1.5231 | 2006--2020 | 2021-11-01
|  | STR-FLTSC-PG-EE-SSW | Standby Service Water Strainer Plugging, Environmental | EPIX/RADS | 1 | 7799060 | h | 60 | Gamma | JNID/IL | 2.26e-08 | 1.52e-07 | 1.92e-07 | 5.01e-07 | 1.5 | 7800000 | 3.303 | 2006--2020 | 2021-11-01
| Sump Strainer (SMP) | STR-PG-SUMP-BWR | Containment Sump Plugging (BWRs, suppression pool strainers) | EPIX/RADS | 0 | 5522832 | h | 42 | Gamma | JNID/IL | 3.56e-10 | 4.12e-08 | 9.05e-08 | 3.48e-07 | 0.5 | 5520000 | 8.4439 | 2006--2020 | 2021-11-01
|  | STR-PG-SUMP-PWR | Containment Sump Plugging (PWRs) | EPIX/RADS | 1 | 3528454 | h | 29 | Gamma | JNID/IL | 4.98e-08 | 3.35e-07 | 4.25e-07 | 1.11e-06 | 1.5 | 3530000 | 3.303 | 2006--2020 | 2021-11-01
| Traveling Screen Assembly (TSA) | TSA-PG | Traveling Screen Plugging | EPIX/RADS | 37 | 25155920 | h | 205 | Gamma | JNID/IL | 1.11e-06 | 1.47e-06 | 1.49e-06 | 1.91e-06 | 37.5 | 25200000 | 1.2944 | 2006--2020 | 2021-11-01
|  | TSA-BYP | Traveling Screen Bypass | EPIX/RADS | 2 | 25155920 | h | 205 | Gamma | JNID/IL | 2.27e-08 | 8.63e-08 | 9.94e-08 | 2.2e-07 | 2.5 | 25200000 | 2.5441 | 2006--2020 | 2021-11-01
|  | TSA-FTOP | Traveling Screen Fails To Operate | EPIX/RADS | 45 | 25155920 | h | 205 | Gamma | EB/PL/KS | 1.3e-08 | 1.04e-06 | 2.12e-06 | 7.86e-06 | 0.547 | 259000 | 7.5817 | 2006--2020 | 2021-11-01
|  | TSA-PG-SSW | Standby Service Water Traveling Screen Plugs | EPIX/RADS | 0 | 1972440 | h | 15 | Gamma | JNID/IL | 9.98e-10 | 1.15e-07 | 2.53e-07 | 9.75e-07 | 0.5 | 1970000 | 8.4439 | 2006--2020 | 2021-11-01
| Trash Rack (TRK) | TRK-PG | Trash Rack Plugging | EPIX/RADS | 0 | 1314960 | h | 10 | Gamma | JNID/IL | 1.5e-09 | 1.74e-07 | 3.8e-07 | 1.47e-06 | 0.5 | 1310000 | 8.4439 | 2006--2020 | 2021-11-01
RPS | Bistable (BIS) | BIS-FTOP | Bistable Fails To Operate | RPS SSs | 55 | 102094 | d | -- | Beta | JNID/IL | 2.14e-06 | 0.000247 | 0.000544 | 0.00209 | 0.5 | 919.266 | 8.4362 | -- | 2007-02-01
| Process Logic Components | PLF-FTOP | Process Logic (Flow) Fails To Operate | RPS SSs | (note d) | 6075 | d | -- | Beta | JNID/IL | 2.46e-06 | 0.000285 | 0.000625 | 0.0024 | 0.5 | 798.974 | 8.435 | -- | 2007-02-01
|  | PLL-FTOP | Process Logic (Level) Fails To Operate | RPS SSs | 3 | 6075 | d | -- | Beta | JNID/IL | 2.46e-06 | 0.000285 | 0.000625 | 0.0024 | 0.5 | 798.974 | 8.435 | -- | 2007-02-01
|  | PLP-FTOP | Process Logic (Pressure) Fails To Operate | RPS SSs | 6 | 38115 | d | -- | Beta | JNID/IL | 6.29e-07 | 7.28e-05 | 0.00016 | 0.000615 | 0.5 | 3123.76 | 8.4417 | -- | 2007-02-01
|  | PLDT-FTOP | Process Logic (Delta Temperature) Fails To Operate | RPS SSs | 24 | 4887 | d | -- | Beta | JNID/IL | 2.01e-05 | 0.00232 | 0.00507 | 0.0194 | 0.5 | 98.0484 | 8.3713 | -- | 2007-02-01
| Sensor/Transmitter Components | STF-FTOP-D | Sensor/Transmitter (Flow) Fails To Operate on Demand | RPS SSs | (note d) | 6750 | d | -- | Beta | JNID/IL | 3.21e-06 | 0.000371 | 0.000815 | 0.00313 | 0.5 | 613.227 | 8.4323 | -- | 2007-02-01
|  | STF-FTOP-R | Sensor/Transmitter (Flow) Fails To Operate per Hour | RPS SSs | (note d) | 9831970 | h | -- | Gamma | JNID/IL | 4e-10 | 4.63e-08 | 1.02e-07 | 3.91e-07 | 0.5 | 4915980 | 8.4439 | -- | 2007-02-01
|  | STL-FTOP-D | Sensor/Transmitter (Level) Fails To Operate on Demand | RPS SSs | 5 | 6750 | d | -- | Beta | JNID/IL | 3.21e-06 | 0.000371 | 0.000815 | 0.00313 | 0.5 | 613.227 | 8.4323 | -- | 2007-02-01
|  | STL-FTOP-R | Sensor/Transmitter (Level) Fails To Operate per Hour | RPS SSs | 0 | 9831970 | h | -- | Gamma | JNID/IL | 4e-10 | 4.63e-08 | 1.02e-07 | 3.91e-07 | 0.5 | 4915980 | 8.4439 | -- | 2007-02-01
|  | STP-FTOP-D | Sensor/Transmitter (Pressure) Fails To Operate on Demand | RPS SSs | 2 | 23960 | d | -- | Beta | JNID/IL | 4.6e-07 | 5.32e-05 | 0.000117 | 0.000449 | 0.5 | 4278.25 | 8.4423 | -- | 2007-02-01
|  | STP-FTOP-R | Sensor/Transmitter (Pressure) Fails To Operate per Hour | RPS SSs | 35 | 43430500 | h | -- | Gamma | JNID/IL | 3.23e-09 | 3.74e-07 | 8.22e-07 | 3.16e-06 | 0.5 | 608270 | 8.4439 | -- | 2007-02-01
|  | STT-FTOP-D | Sensor/Transmitter (Temperature) Fails To Operate on Demand | RPS SSs | 17 | 40759 | d | -- | Beta | JNID/IL | 1.7e-06 | 0.000197 | 0.000432 | 0.00166 | 0.5 | 1157.45 | 8.4378 | -- | 2007-02-01
|  | STT-FTOP-R | Sensor/Transmitter (Temperature) Fails To Operate per Hour | RPS SSs | 29 | 35107400 | h | -- | Gamma | JNID/IL | 3.3e-09 | 3.82e-07 | 8.4e-07 | 3.23e-06 | 0.5 | 595041 | 8.4439 | -- | 2007-02-01
| Reactor Trip Breaker (RTB) | RTB-FTOC-BME | RPS Breaker (Mechanical) Fails To Open/Close | RPS SSs | 1 | 97359 | d | -- | Beta | JNID/IL | 6.06e-08 | 7.01e-06 | 1.54e-05 | 5.92e-05 | 0.5 | 32452.5 | 8.4437 | -- | 2007-02-01
|  | RTB-FTOP-BSN | RPS Breaker (Shunt Trip) Fails To Operate | RPS SSs | 14 | 44104 | d | -- | Beta | JNID/IL | 1.29e-06 | 0.00015 | 0.000329 | 0.00126 | 0.5 | 1520.33 | 8.4392 | -- | 2007-02-01
|  | RTB-FTOP-BUV | RPS Breaker (Undervoltage Trip) Fails To Operate | RPS SSs | 23 | 57199 | d | -- | Beta | JNID/IL | 1.62e-06 | 0.000188 | 0.000413 | 0.00158 | 0.5 | 1211.34 | 8.438 | -- | 2007-02-01
|  | RTB-FTOC | RPS Breaker (Combined) Fails To Open/Close | RPS SSs | -- | -- | d | -- | Beta | JNID/IL | 6.11e-08 | 7.07e-06 | 1.55e-05 | 5.97e-05 | 0.5 | 32169.3 | 8.4437 | -- | 2007-02-01
| Manual Switch (MSW) | MSW-FTOC | Manual Switch Fails To Open/Close | RPS SSs | 2 | 19789 | d | -- | Beta | JNID/IL | 4.97e-07 | 5.75e-05 | 0.000126 | 0.000485 | 0.5 | 3957.5 | 8.4421 | -- | 2007-02-01
| Relay (RLY) | RLY-FTOP | Relay Fails To Operate | RPS SSs | 24 | 974417 | d | -- | Beta | JNID/IL | 9.77e-08 | 1.13e-05 | 2.48e-05 | 9.54e-05 | 0.5 | 20132.1 | 8.4436 | -- | 2007-02-01
Control Rods | Control Rod Drive (CRD) | CRD-FTOP | Control Rod Drive Fails To Insert Rod | EPIX/RADS | 19 | 145016900 | d | 1198 | Gamma | EB/PL/KS | 1.16e-09 | 8.38e-08 | 1.68e-07 | 6.18e-07 | 0.56 | 3340000 | 7.3805 | 2006--2020 | 2021-11-01
|  | CRD-SOP | Control Rod Drive Spurious Operation | EPIX/RADS | 23 | 145016900 | h | 1198 | Gamma | JNID/IL | 1.11e-07 | 1.6e-07 | 1.62e-07 | 2.21e-07 | 23.5 | 145000000 | 1.3813 | 2006--2020 | 2021-11-01
| Control Rod (ROD) | ROD-FTOP | Control Rod Fails To Operate/ Insert Rod | EPIX/RADS | 10 | 110389200 | d | 844 | Gamma | JNID/IL | 5.27e-08 | 9.24e-08 | 9.51e-08 | 1.49e-07 | 10.5 | 110000000 | 1.6064 | 2006--2020 | 2021-11-01
|  | ROD-SOP | Control Rod Spurious Operation | EPIX/RADS | 11 | 110389200 | h | 844 | Gamma | JNID/IL | 5.95e-08 | 1.02e-07 | 1.04e-07 | 1.6e-07 | 11.5 | 110000000 | 1.5746 | 2006--2020 | 2021-11-01
| Hydraulic Control Unit (HCU) | HCU-FTI | Hydraulic Control Unit Components Fail | RPS SSs | -- | -- | d | -- | Lognormal | -- | 1.05e-09 | 2.1e-08 | 1.1e-07 | 4.19e-07 | 20 | -- | 20 | -- | 2005-06-23
|  | HCU-FTOP | Hydraulic Control Unit Fails To Operate | EPIX/RADS | 19 | 1347114000 | h | 10425 | Gamma | JNID/IL | 9.52e-09 | 1.42e-08 | 1.45e-08 | 2.02e-08 | 19.5 | 1350000000 | 1.4235 | 2006--2020 | 2021-11-01
|  | HCU-SOP | Hydraulic Control Unit Spurious Operation | EPIX/RADS | 27 | 1347114000 | h | 10425 | Gamma | EB/PL/KS | 7.14e-09 | 1.84e-08 | 1.99e-08 | 3.79e-08 | 4.3 | 216000000 | 2.0593 | 2006--2020 | 2021-11-01
Heating & Ventilation | Air Damper (DMP) | AOD-FTOC | Air-Operated Damper Fails To Open/Close | EPIX/RADS | 0 | 6602.3 | d | 50 | Beta | JNID/IL | 2.98e-07 | 3.45e-05 | 7.57e-05 | 0.000291 | 0.5 | 6600 | 8.4429 | 2006--2020 | 2021-11-01
|  | AOD-SOP | Air-Operated Damper Spurious Operation | EPIX/RADS | 4 | 24287000 | h | 207 | Gamma | EB/PL/KS | 1.29e-09 | 8.25e-08 | 1.61e-07 | 5.86e-07 | 0.579 | 3600000 | 7.1097 | 2006--2020 | 2021-11-01
|  | AOD-ILS | Air-Operated Damper Internal Leakage (Small) | EPIX/RADS | 3 | 24287000 | h | 207 | Gamma | JNID/IL | 4.46e-08 | 1.31e-07 | 1.44e-07 | 2.89e-07 | 3.5 | 24300000 | 2.2168 | 2006--2020 | 2021-11-01
|  | AOD-ILL | Air-Operated Damper Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 207 | Gamma | JNID/IL | 3.08e-13 | 7.02e-10 | 2.88e-09 | 1.32e-08 | 0.3 | 104167000 | 18.7656 | 2006--2020 | 2021-11-01
|  | HOD-FTOC | Hydraulic-Operated Damper Fails To Open/Close | EPIX/RADS | 4 | 6112.8 | d | 42 | Beta | JNID/IL | 0.000272 | 0.000682 | 0.000736 | 0.00138 | 4.5 | 6110 | 2.0273 | 2006--2020 | 2021-11-01
|  | HOD-SOP | Hydraulic-Operated Damper Spurious Operation | EPIX/RADS | 2 | 16454520 | h | 126 | Gamma | JNID/IL | 3.47e-08 | 1.32e-07 | 1.52e-07 | 3.35e-07 | 2.5 | 16500000 | 2.5441 | 2006--2020 | 2021-11-01
|  | HOD-ILS | Hydraulic-Operated Damper Internal Leakage (Small) | EPIX/RADS | 0 | 16454520 | h | 126 | Gamma | JNID/IL | 1.19e-10 | 1.38e-08 | 3.04e-08 | 1.16e-07 | 0.5 | 16500000 | 8.4439 | 2006--2020 | 2021-11-01
|  | HOD-ILL | Hydraulic-Operated Damper Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 126 | Gamma | JNID/IL | 6.51e-14 | 1.48e-10 | 6.08e-10 | 2.78e-09 | 0.3 | 493421000 | 18.7656 | 2006--2020 | 2021-11-01
|  | MOD-FTOC | Motor-Operated Damper Fails To Open | EPIX/RADS | 11 | 28949.4 | d | 52 | Beta | EB/PL/KS | 1.74e-05 | 0.000244 | 0.000356 | 0.00107 | 0.981 | 2760 | 4.3831 | 2006--2020 | 2021-11-01
|  | MOD-SOP | Motor-Operated Damper Spurious Operation | EPIX/RADS | 0 | 14134270 | h | 109 | Gamma | JNID/IL | 1.39e-10 | 1.61e-08 | 3.54e-08 | 1.36e-07 | 0.5 | 14100000 | 8.4439 | 2006--2020 | 2021-11-01
|  | MOD-ILS | Motor-Operated Damper Internal Leakage (Small) | EPIX/RADS | 0 | 14134270 | d | 109 | Gamma | JNID/IL | 1.39e-10 | 1.61e-08 | 3.54e-08 | 1.36e-07 | 0.5 | 14100000 | 8.4439 | 2006--2020 | 2021-11-01
|  | MOD-ILL | Motor-Operated Damper Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 109 | Gamma | JNID/IL | 7.58e-14 | 1.73e-10 | 7.08e-10 | 3.24e-09 | 0.3 | 423729000 | 18.7656 | 2006--2020 | 2021-11-01
| Air Handling | AHU-FTS-NR | Air Handling Unit Fails To Start, Normally Running | EPIX/RADS | 23 | 15981.1 | d | 145 | Beta | JNID/IL | 0.00101 | 0.00145 | 0.00147 | 0.002 | 23.5 | 16000 | 1.3809 | 2006--2020 | 2021-11-01
|  | AHU-FTR-NR | Air Handling Unit Fails To Run, Normally Running | EPIX/RADS | 39 | 15131330 | h | 145 | Gamma | JNID/IL | 1.97e-06 | 2.59e-06 | 2.61e-06 | 3.34e-06 | 39.5 | 15100000 | 1.2861 | 2006--2020 | 2021-11-01
|  | AHU-FTS-NS | Air Handling Unit Fails To Start, Normally Standby | EPIX/RADS | 33 | 158866.1 | d | 403 | Beta | JNID/IL | 0.000155 | 0.000209 | 0.000211 | 0.000274 | 33.5 | 159000 | 1.3131 | 2006--2020 | 2021-11-01
|  | AHU-FTR<1H | Air Handling Unit Fails To Run <1H, Normally Standby | EPIX/RADS | 0 | 147962.7 | h | 395 | Gamma | JNID/IL | 1.33e-08 | 1.54e-06 | 3.38e-06 | 1.3e-05 | 0.5 | 148000 | 8.4439 | 2006--2020 | 2021-11-01
|  | AHU-FTR>1H | Air Handling Unit Fails To Run >1H, Normally Standby | EPIX/RADS | 27 | 9928068 | h | 403 | Gamma | JNID/IL | 1.96e-06 | 2.74e-06 | 2.77e-06 | 3.69e-06 | 27.5 | 9930000 | 1.3493 | 2006--2020 | 2021-11-01
| Chiller (CHL) | CHL-FTS-NR | Chiller Unit Fails To Start, Normally Running | EPIX/RADS | 66 | 21136.7 | d | 92 | Beta | EB/PL/KS | 9.52e-06 | 0.00205 | 0.00509 | 0.0205 | 0.438 | 85.6 | 9.9553 | 2006--2020 | 2021-11-01
|  | CHL-FTR-NR | Chiller Unit Fails To Run, Normally Running | EPIX/RADS | 179 | 7250769 | h | 92 | Gamma | EB/PL/KS | 1.94e-07 | 1.84e-05 | 3.87e-05 | 0.000147 | 0.524 | 13500 | 7.9747 | 2006--2020 | 2021-11-01
|  | CHL-FTS-NS | Chiller Unit Fails To Start, Normally Standby | EPIX/RADS | 0 | 18005.8 | d | 64 | Beta | JNID/IL | 1.09e-07 | 1.26e-05 | 2.78e-05 | 0.000107 | 0.5 | 18000 | 8.4435 | 2006--2020 | 2021-11-01
|  | CHL-FTR<1H | Chiller Unit Fails To Run <1H, Normally Standby | EPIX/RADS | 34 | 233780.6 | h | 64 | Gamma | JNID/IL | 0.000109 | 0.000146 | 0.000148 | 0.000191 | 34.5 | 234000 | 1.3081 | 2006--2020 | 2021-11-01
|  | CHL-FTR>1H | Chiller Unit Fails To Run >1H, Normally Standby | EPIX/RADS | 34 | 233780.6 | h | 64 | Gamma | JNID/IL | 0.000109 | 0.000146 | 0.000148 | 0.000191 | 34.5 | 234000 | 1.3081 | 2006--2020 | 2021-11-01
| Fan (FAN) | FAN-FTS-NS | HVC Fan Fails To Start, Normally Standby | EPIX/RADS | 17 | 63510.5 | d | 154 | Beta | JNID/IL | 0.000177 | 0.00027 | 0.000276 | 0.000392 | 17.5 | 63500 | 1.4504 | 2006--2020 | 2021-11-01
|  | FAN-FTR<1H | HVC Fan FTR<1H, Normally Standby | EPIX/RADS | 17 | 39404.9 | h | 133 | Gamma | JNID/IL | 0.000285 | 0.000436 | 0.000444 | 0.000632 | 17.5 | 39400 | 1.4504 | 2006--2020 | 2021-11-01
|  | FAN-FTR>1H | HVC Fan FTR>1H, Normally Standby | EPIX/RADS | 3 | 120199.9 | h | 154 | Gamma | JNID/IL | 9.03e-06 | 2.64e-05 | 2.91e-05 | 5.86e-05 | 3.5 | 120000 | 2.2168 | 2006--2020 | 2021-11-01
|  | FAN-FTS-NR | HVC Fan Fails To Start, Normally Running | EPIX/RADS | 28 | 87322.6 | d | 233 | Beta | EB/PL/KS | 1.69e-06 | 0.000299 | 0.000715 | 0.00284 | 0.456 | 636 | 9.4987 | 2006--2020 | 2021-11-01
|  | FAN-FTR-NR | HVC Fan Fails To Run, Normally Running | EPIX/RADS | 50 | 16050850 | h | 233 | Gamma | EB/PL/KS | 4.87e-08 | 1.83e-06 | 3.23e-06 | 1.11e-05 | 0.674 | 209000 | 6.0671 | 2006--2020 | 2021-11-01
Miscellaneous Equipment | Air Compressor (CMP) | MDC-FTS-NR | Motor-Driven Compressor Fails To Start, Normally Running | EPIX/RADS | 52 | 7854.7 | d | 65 | Beta | EB/PL/KS | 3.28e-05 | 0.00578 | 0.0136 | 0.0536 | 0.456 | 33.1 | 9.2799 | 2006--2020 | 2021-11-01
|  | MDC-FTR-NR | Motor-Driven Compressor Fails To Run | EPIX/RADS | 173 | 4802083 | h | 65 | Gamma | EB/PL/KS | 9.92e-06 | 3.54e-05 | 4.03e-05 | 8.72e-05 | 2.69 | 66800 | 2.464 | 2006--2020 | 2021-11-01
|  | MDC-FTS-NS | Motor-Driven Compressor Fails To Start, Normally Standby | EPIX/RADS | 34 | 21073.7 | d | 57 | Beta | EB/PL/KS | 9.56e-05 | 0.00189 | 0.00293 | 0.00927 | 0.847 | 289 | 4.9117 | 2006--2020 | 2021-11-01
|  | MDC-FTR<1H | Motor-Driven Compressor Fails To Run (0 To 1 Hour) | EPIX/RADS | 1 | 20247.5 | h | 54 | Gamma | JNID/IL | 8.71e-06 | 5.86e-05 | 7.41e-05 | 0.000193 | 1.5 | 20200 | 3.303 | 2006--2020 | 2021-11-01
|  | MDC-FTR>1H | Motor-Driven Compressor Fails To Run (> 1 Hour) | EPIX/RADS | 90 | 1573366 | h | 57 | Gamma | JNID/IL | 4.81e-05 | 5.74e-05 | 5.75e-05 | 6.8e-05 | 90.5 | 1570000 | 1.1833 | 2006--2020 | 2021-11-01
|  | EDC-FTS-NS | Engine-Driven Compressor Fails To Start, Normally Standby | EPIX/RADS | 14 | 1459.1 | d | 4 | Beta | JNID/IL | 0.00606 | 0.00968 | 0.00993 | 0.0145 | 14.5 | 1450 | 1.4982 | 2006--2020 | 2021-11-01
|  | EDC-FTR<1H | Engine-Driven Compressor Fails To Run <1H, Normally Standby | EPIX/RADS | 1 | 1459.1 | h | 4 | Gamma | JNID/IL | 0.00012 | 0.00081 | 0.00103 | 0.00268 | 1.5 | 1460 | 3.303 | 2006--2020 | 2021-11-01
|  | EDC-FTR>1H | Engine-Driven Compressor Fails To Run >1H, Normally Standby | EPIX/RADS | 12 | 1608.5 | h | 4 | Gamma | JNID/IL | 0.00454 | 0.00756 | 0.00777 | 0.0117 | 12.5 | 1610 | 1.5472 | 2006--2020 | 2021-11-01
|  | EDC-FTR-NR | Engine-Driven Compressor Fails To Run, Normally Running | EPIX/RADS | 10 | 163320.5 | d | 3 | Gamma | JNID/IL | 3.56e-05 | 6.24e-05 | 6.43e-05 | 0.0001 | 10.5 | 163000 | 1.6064 | 2006--2020 | 2021-11-01
|  | MDC-FTR-IAS | Instrument Air System Motor-Driven Compressor Fails To Run | EPIX/RADS | 117 | 2376803 | h | 36 | Gamma | EB/PL/KS | 2.41e-05 | 4.73e-05 | 4.93e-05 | 8.22e-05 | 7.62 | 154000 | 1.736 | 2006--2020 | 2021-11-01
|  | MDC-FTR-CIA | Containment Instrument Air Motor-Driven Compressor Fails To Run | EPIX/RADS | 0 | 98560.8 | h | 2 | Gamma | JNID/IL | 1.99e-08 | 2.31e-06 | 5.07e-06 | 1.95e-05 | 0.5 | 98600 | 8.4439 | 2006--2020 | 2021-11-01
| Air Drier Unit (ADU) | ADU-FTOP | Air dryer unit fails To operate | WSRC | -- | -- | h | 0 | Gamma | JNID/IL | 5.35e-10 | 1.22e-06 | 5e-06 | 2.29e-05 | 0.3 | 60000 | 18.7656 | -- | 2005-06-23
| Accumulator (ACC) | ACC-FTOP | Accumulator Fails To Operate | EPIX/RADS | 11 | 79315180 | h | 617 | Gamma | JNID/IL | 8.25e-08 | 1.41e-07 | 1.45e-07 | 2.22e-07 | 11.5 | 79300000 | 1.5746 | 2006--2020 | 2021-11-01
|  | ACC-ELS | Accumulator External Leakage (Small) | EPIX/RADS | 8 | 79315180 | h | 617 | Gamma | JNID/IL | 5.47e-08 | 1.03e-07 | 1.07e-07 | 1.74e-07 | 8.5 | 79300000 | 1.6885 | 2006--2020 | 2021-11-01
|  | ACC-ELL | Accumulator External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 617 | Gamma | JNID/IL | 8.02e-13 | 1.83e-09 | 7.49e-09 | 3.43e-08 | 0.3 | 40053400 | 18.7656 | 2006--2020 | 2021-11-01
| Cooling Tower Fan (CTF) | CTF-FTS-NS | Cooling Tower Fan Fails To Start (Standby) | EPIX/RADS | 14 | 37306.8 | d | 55 | Beta | JNID/IL | 0.000237 | 0.00038 | 0.000389 | 0.00057 | 14.5 | 37300 | 1.5017 | 2006--2020 | 2021-11-01
|  | CTF-FTR<1H | Cooling Tower Fan Fails To Run <1H (Standby) | EPIX/RADS | 0 | 37231.2 | h | 54 | Gamma | JNID/IL | 5.29e-08 | 6.11e-06 | 1.34e-05 | 5.16e-05 | 0.5 | 37200 | 8.4439 | 2006--2020 | 2021-11-01
|  | CTF--FTR>1H | Cooling Tower Fan Fails To Run >1H (Standby) | EPIX/RADS | 0 | 895323 | h | 55 | Gamma | JNID/IL | 2.2e-09 | 2.54e-07 | 5.58e-07 | 2.15e-06 | 0.5 | 895000 | 8.4439 | 2006--2020 | 2021-11-01
|  | CTF-FTS-NR | Cooling Tower Fan Fails To Start | EPIX/RADS | 1 | 2239.2 | d | 20 | Beta | JNID/IL | 7.85e-05 | 0.000528 | 0.00067 | 0.00174 | 1.5 | 2240 | 3.301 | 2006--2020 | 2021-11-01
|  | CTF-FTR-NR | Cooling Tower Fan Fails To Run | EPIX/RADS | 6 | 1253930 | h | 20 | Gamma | JNID/IL | 2.36e-06 | 4.94e-06 | 5.18e-06 | 8.94e-06 | 6.5 | 1250000 | 1.8122 | 2006--2020 | 2021-11-01
| Tank (TNK) | TNK-FC | Tank Rupture | EPIX/RADS | 16 | 46469300 | h | 383 | Gamma | EB/PL/KS | 5.99e-10 | 1.61e-07 | 4.18e-07 | 1.72e-06 | 0.42 | 1000000 | 10.6625 | 2006--2020 | 2021-11-01
|  | TNK-PRESS-LIQ-ELS | Pressurized Liquid Tank Small Leakage External Leakage (Small) | EPIX/RADS | 5 | 19535510 | h | 156 | Gamma | EB/PL/KS | 8.76e-10 | 1.12e-07 | 2.51e-07 | 9.71e-07 | 0.489 | 1950000 | 8.6829 | 2006--2020 | 2021-11-01
|  | TNK-PRESS-LIQ-ELL | Pressurized Liquid Tank Small Leakage External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 156 | Gamma | EB/PL/KS | 1.88e-12 | 4.28e-09 | 1.76e-08 | 8.04e-08 | 0.3 | 17074600 | 18.7656 | 2006--2020 | 2021-11-01
|  | TNK-UNPRESS-LIQ-ELS | Unpressurized Liquid Tank Small Leakage External Leakage (Small) | EPIX/RADS | 4 | 22725910 | h | 195 | Gamma | JNID/IL | 7.32e-08 | 1.84e-07 | 1.98e-07 | 3.73e-07 | 4.5 | 22700000 | 2.028 | 2006--2020 | 2021-11-01
|  | TNK-UNPRESS-LIQ-ELL | Unpressurized Liquid Tank Small Leakage External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 195 | Gamma | JNID/IL | 1.48e-12 | 3.38e-09 | 1.39e-08 | 6.34e-08 | 0.3 | 21645000 | 18.7656 | 2006--2020 | 2021-11-01
|  | TNK-FC-IAS | Instrument Air System Tank Fails To Control | EPIX/RADS | 0 | 3287400 | h | 25 | Gamma | JNID/IL | 5.98e-10 | 6.91e-08 | 1.52e-07 | 5.84e-07 | 0.5 | 3290000 | 8.4439 | 2006--2020 | 2021-11-01
|  | TNK-FC-SSW | Standby Service Water Tank Fails To Control | EPIX/RADS | 0 | 880966 | h | 7 | Gamma | JNID/IL | 2.23e-09 | 2.58e-07 | 5.68e-07 | 2.18e-06 | 0.5 | 881000 | 8.4439 | 2006--2020 | 2021-11-01
|  | TNK-GAS-ELS | Gas Tank Small Leakage External Leakage (Small) | EPIX/RADS | 0 | 4207872 | h | 32 | Gamma | JNID/IL | 4.67e-10 | 5.4e-08 | 1.19e-07 | 4.56e-07 | 0.5 | 4210000 | 8.4439 | 2006--2020 | 2021-11-01
|  | TNK-GAS-ELL | Gas Tank Small Leakage External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 32 | Gamma | JNID/IL | 8.92e-13 | 2.03e-09 | 8.33e-09 | 3.81e-08 | 0.3 | 36014400 | 18.7656 | 2006--2020 | 2021-11-01
| Orifice (ORF) | ORF-PG | Orifice Plugging | WSRC | -- | -- | h | 0 | Gamma | JNID/IL | 1.07e-10 | 2.44e-07 | 1e-06 | 4.57e-06 | 0.3 | 300000 | 18.7656 | -- | 2005-06-23
| Pipe (PIPE) | PIPE-OTHER-ELS | Piping Non-Service Water System External Leak Small | EPIX | 4.5 | 15830000000 | h-ft | 0 | Gamma | JNID/IL | 9.94e-13 | 1.15e-10 | 2.53e-10 | 9.71e-10 | 0.5 | 1978750000 | 8.4439 | -- | 2007-02-01
|  | PIPE-OTHER-ELL | Piping Non-Service Water System External Leak Large | NUREG/CR-6928 | (note c) | 15830000000 | h-ft | 0 | Gamma | JNID/IL | 2.7e-15 | 6.16e-12 | 2.53e-11 | 1.16e-10 | 0.3 | 11872500000 | 18.7656 | -- | 2007-02-01
|  | PIPE-SWS-ELS | Piping Service Water System External Leak Small | EPIX | 8.5 | 13060000000 | h-ft | 0 | Gamma | JNID/IL | 2.71e-12 | 3.14e-10 | 6.89e-10 | 2.65e-09 | 0.5 | 725556000 | 8.4439 | -- | 2007-02-01
|  | PIPE-SWS-ELL | Piping Service Water System External Leak Large | NUREG/CR-6928 | (note c) | 13060000000 | h-ft | 0 | Gamma | JNID/IL | 1.48e-14 | 3.36e-11 | 1.38e-10 | 6.3e-10 | 0.3 | 2176670000 | 18.7656 | -- | 2007-02-01
| Heat Exchanger (HTX) | HTX-LOHT | Heat Exchanger Plugging/Loss of Heat Transfer | EPIX/RADS | 67 | 222831700 | h | 1750 | Gamma | EB/PL/KS | 1.11e-09 | 1.5e-07 | 3.39e-07 | 1.32e-06 | 0.483 | 1420000 | 8.8204 | 2006--2020 | 2021-11-01
|  | HTX-ILS | Heat Exchanger Internal Leakage (Small) | EPIX/RADS | 61 | 222831700 | h | 1750 | Gamma | JNID/IL | 2.21e-07 | 2.74e-07 | 2.76e-07 | 3.36e-07 | 61.5 | 223000000 | 1.2252 | 2006--2020 | 2021-11-01
|  | HTX-ILL | Heat Exchanger Internal Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1750 | Gamma | JNID/IL | 5.91e-13 | 1.35e-09 | 5.52e-09 | 2.53e-08 | 0.3 | 54347800 | 18.7656 | 2006--2020 | 2021-11-01
|  | HTX-ELS | Heat Exchanger External Leakage (Small) | EPIX/RADS | 38 | 222831700 | h | 1750 | Gamma | EB/PL/KS | 5.71e-09 | 1.21e-07 | 1.9e-07 | 6.08e-07 | 0.825 | 4350000 | 5.0408 | 2006--2020 | 2021-11-01
|  | HTX-ELL | Heat Exchanger External Leakage (Rupture) | NUREG/CR-6928 | (note c) | -- | h | 1750 | Gamma | EB/PL/KS | 3.05e-12 | 6.95e-09 | 2.85e-08 | 1.3e-07 | 0.3 | 10526300 | 18.7656 | 2006--2020 | 2021-11-01
|  | HTX-PG-CCW | Heat Exchanger Plugging Non Standby | EPIX/RADS | 8 | 28273230 | h | 223 | Gamma | JNID/IL | 1.53e-07 | 2.89e-07 | 3.01e-07 | 4.87e-07 | 8.5 | 28300000 | 1.6885 | 2006--2020 | 2021-11-01
|  | HTX-PG-NE-CCW | Component Cooling Water Heat Exchanger Plugging Non-ExEE (hr-1) | EPIX/RADS | 3 | 28273230 | h | 223 | Gamma | JNID/IL | 3.83e-08 | 1.12e-07 | 1.24e-07 | 2.49e-07 | 3.5 | 28300000 | 2.2168 | 2006--2020 | 2021-11-01
| Instrumentation | ICC-FC | Instrumentation and Control Circuit Fails | NUCLARR | 0 | -- | d | 0 | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 | -- | 2.2 | -- | 2005-06-23
|  | ICC-FA | Failure of Instrument and Control for a Turbine Trip | NUCLARR | 0 | -- | d | 0 | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 | -- | 2.2 | -- | 2005-06-23
|  | ACT-FC | Automatic Actuation and Control Circuit Fails | NUCLARR | 0 | -- | d | 0 | Lognormal | NUCLARR | 0.000689 | 0.00152 | 0.0017 | 0.00333 | 2.2 | -- | 2.2 | -- | 2011-12-08
Acronyms - ABT (automatic bus transfer switch), ACC (accumulator), ADU (air dryer unit), AFW (auxiliary feedwater), AHU (air handling unit), AOD (air-operated damper), AOV (air-operated valve), BAT (battery), BCH (battery charger), BFV (butterfly valve), BWR (boiling water reactor), CCW (component cooling water), CHL (chiller), CIA (containment instrument air), CKV (check valve), CMP (air compressor), CRB (circuit breaker), CRD (control rod drive), CTF (cooling Tower fan), CTG (combustion turbine generator), CWS (circulating water system), EB/PL/KS (empirical Bayes/plant level/Kass Steffey), EDC (engine-driven compressor), EDG (diesel generator), EDP (engine-driven pump), ELL (external large leakage), ELS (external small leakage), EOV (explosive-operated valve), EPIX (Equipment Performance and Information Exchange), FC (fail To control), FTC (fail To close), FCV (flow control valve), FRV (feedwater regulating valve), FTLR (fail To load and run), FTO (fail To open), FTOC (fail To open or close), FTOP (fail To operate), FTR (fail To run), FTS (fail To start), HCS (high-pressure core spray), HCU (hydraulic control unit), HOD (hydraulic-operated damper), HOV (hydraulic-operated valve), HTG (hydro turbine generator), HTX (heat exchanger), HVC (heating, ventilating, and air conditioning), IAS (instrument air system), ILL (internal large leakage), ILS (internal small leakage), JNID/IL (Jeffreys noninformative distribution/industry level), LIQ (liquid), LL (lower limit), LOHT (loss of heat transfer), MDC (motor-driven compressor), MDP (motor-driven pump), MFW (main feedwater), MOD (motor-driven damper), MOV (motor-operated valve), MSS (main steam system), MSV (main steam isolation valve), NR (normally running), NS (normally standby), ORF (orifice), PDP (positive displacement pump), PLL (process logic level), PMP (pump volute), PORV (power-operated relief valve), PWR (pressurized water reactor), PZR (pressurizer), RADS (Reliability and Availability Database System), RCS (reactor coolant system), ROD (control rod), RPS (reactor protection system), RVL (low capacity relief valve), SBO (station blackout), SOV (solenoid-operated valve), SRV (safety relief valve), SS (system study), STBY (standby), SVV (code safety valve), SWS (service water system), TDP (turbine-driven pump), TNK (tank), VBV (vacuum breaker valve), WSRC (Westinghouse Savannah River Company), XVM (manual valve) Note a - If these distributions are To be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in ASME/ANS RA-Sa-2009 and outlined in Section 6.2.3.5 of NUREG/CR-6823. Note b - The error factor is from an empirical Bayes analysis at the plant level, with Kass-Steffey adjustment. The error factor is the 95th percentile divided by the median. Note c - External and internal large leakage (ELL and ILL) events are defined as greater than 50 gpm. Because ELL and ILL events are rare, good estimates for ELL and ILL cannot be obtained using data from only one component. The NUREG/CR-6928 study (Table A.1.2-1) shows the mean of ELL is the ELS mean multiplied by 0.07 for pump, valves, tanks, and heat exchanger shells, multiplied by 0.2 for Emergency Service Water (ESW) pipe, multiplied by 0.1 for non-ESW pipe, and multiplied by 0.15 for heat exchanger tubes. The ILL mean is the ILS mean multiplied by 0.02. Note d - The flow process logic (PLF) reliability was estimated by using the level process logic (PLL) data. The flow sensor/transmitter (STF) reliability was estimated by using the level sensor/transmitter (STL) data.

## IE Data
SPAR Initiating Event Data and Results
2020 Parameter Estimation Update
2021-11-01 18:52 |  | Parameter Estimate 2020 V1
Section | Sub Section | Initiating Event | Description | Data |  |  | Industry-average Frequency Distribution (note a) | [8 empty] | Baseline Period | Effective Date
|  |  |  | Source | Number of Events | Critical Years (rcry) | Distribution | Analysis Type | 5th | Median | Mean | 95th | α | β | Error Factor
Primary/Secondary Inventory Control | High Energy Line Breaks | FWLB BWR FI | Feedwater Line Break (BWR) | RADS | 0 | 989.4 | Gamma | JNID/IL | 1.99e-06 | 0.00023 | 0.000505 | 0.00194 | 0.5 | 989 | 8.4439 | 1988--2020 | 2021-11-01
|  | FWLB PWR FI | Feedwater Line Break (PWR) | RADS | 2 | 1962.4 | Gamma | JNID/IL | 0.000292 | 0.00111 | 0.00127 | 0.00282 | 2.5 | 1960 | 2.5441 | 1988--2020 | 2021-11-01
|  | SLBIC PWR FI | Steam Line Break Inside Containment (PWR) | RADS | 0 | 1962.4 | Gamma | JNID/IL | 1e-06 | 0.000116 | 0.000255 | 0.00098 | 0.5 | 1960 | 8.4439 | 1988--2020 | 2021-11-01
|  | SLBOC BWR FI | Steam Line Break Outside Containment (BWR) | RADS | 2 | 989.4 | Gamma | JNID/IL | 0.000579 | 0.0022 | 0.00253 | 0.0056 | 2.5 | 989 | 2.5441 | 1988--2020 | 2021-11-01
|  | SLBOC PWR FI | Steam Line Break Outside Containment (PWR) | RADS | 10 | 1962.4 | Gamma | JNID/IL | 0.00296 | 0.00519 | 0.00535 | 0.00833 | 10.5 | 1960 | 1.6064 | 1988--2020 | 2021-11-01
| Steam Generator Tube Rupture | SGTR | Steam Generator Tube Rupture | RADS | 3 | 1962.4 | Gamma | JNID/IL | 0.000553 | 0.00162 | 0.00178 | 0.00359 | 3.5 | 1960 | 2.2168 | 1988--2020 | 2021-11-01
| Loss of Coolant Accidents | LLOCA BWR | Large Loss-of-Coolant Accident (BWR) | RADS & NUREG-1829 | 0 | 573.8 | Gamma | (note b) | 1.25e-09 | 2.86e-06 | 1.17e-05 | 5.36e-05 | 0.3 | 25600 | 18.7656 | 2003--2020 | 2021-11-01
|  | LLOCA PWR | Large Loss-of-Coolant Accident (PWR) | RADS & NUREG-1829 | 0 | 1096.5 | Gamma | (note b) | 6.28e-10 | 1.43e-06 | 5.87e-06 | 2.69e-05 | 0.3 | 51100 | 18.7656 | 2003--2020 | 2021-11-01
|  | MLOCA BWR | Medium Loss-of-Coolant Accident (BWR) | RADS & NUREG-1829 | 0 | 573.8 | Gamma | (note b) | 9.07e-08 | 3.17e-05 | 8.75e-05 | 0.000364 | 0.4 | 4570 | 11.4556 | 2003--2020 | 2021-11-01
|  | MLOCA PWR | Medium Loss-of-Coolant Accident (PWR) | RADS & NUREG-1829 | 0 | 1096.5 | Gamma | (note b) | 1.4e-08 | 3.18e-05 | 0.000131 | 0.000597 | 0.3 | 2300 | 18.7656 | 2003--2020 | 2021-11-01
|  | SLOCA BWR | Small Loss-of-Coolant Accident (BWR) | RADS & NUREG-1829 | 0 | 573.8 | Gamma | (note b) | 3.34e-07 | 0.000117 | 0.000322 | 0.00134 | 0.4 | 1240 | 11.4556 | 2003--2020 | 2021-11-01
|  | SLOCA PWR | Small Loss-of-Coolant Accident (PWR) | RADS & NUREG-1829 | 0 | 1096.5 | Gamma | (note b) | 3.19e-07 | 0.000112 | 0.000309 | 0.00128 | 0.4 | 1300 | 11.4556 | 2003--2020 | 2021-11-01
|  | VSLOCA BWR FI | Very Small Loss-of-Coolant Accident (BWR) | RADS | 2 | 890.6 | Gamma | JNID/IL | 0.000643 | 0.00244 | 0.00281 | 0.00621 | 2.5 | 891 | 2.5441 | 1992--2020 | 2021-11-01
|  | VSLOCA PWR FI | Very Small Loss-of-Coolant Accident (PWR) | RADS | 0 | 1744.8 | Gamma | JNID/IL | 1.13e-06 | 0.000131 | 0.000287 | 0.0011 | 0.5 | 1740 | 8.4439 | 1992--2020 | 2021-11-01
|  | SORV1 BWR FI | Stuck Open Safety/Relief Valve (BWR) | RADS | 7 | 838.6 | Gamma | EB/PL/KS | 0.0013 | 0.00685 | 0.00832 | 0.0203 | 1.82 | 219 | 2.9666 | 1994--2020 | 2021-11-01
|  | SORV2 BWR FI | Stuck Open Relief Valve >2 (BWR) | RADS | 0 | 838.6 | Gamma | JNID/IL | 2.34e-06 | 0.000271 | 0.000596 | 0.00229 | 0.5 | 839 | 8.4439 | 1994--2020 | 2021-11-01
|  | SORV1 PWR FI | Stuck Open Safety/Relief Valve (PWR) | RADS | 2 | 1962.4 | Gamma | JNID/IL | 0.000292 | 0.00111 | 0.00127 | 0.00282 | 2.5 | 1960 | 2.5441 | 1988--2020 | 2021-11-01
|  | SORV2 PWR FI | Stuck Open Relief Valve >2 (PWR) | RADS | 0 | 1962.4 | Gamma | JNID/IL | 1e-06 | 0.000116 | 0.000255 | 0.00098 | 0.5 | 1960 | 8.4439 | 1988--2020 | 2021-11-01
|  | ISLOCA BWR FI | Interfacing System Loss-of-Coolant Accident (BWR) | RADS | 0 | 989.4 | Gamma | JNID/IL | 1.99e-06 | 0.00023 | 0.000505 | 0.00194 | 0.5 | 989 | 8.4439 | 1988--2020 | 2021-11-01
|  | ISLOCA PWR FI | Interfacing System Loss-of-Coolant Accident (PWR) | RADS | 0 | 1962.4 | Gamma | JNID/IL | 1e-06 | 0.000116 | 0.000255 | 0.00098 | 0.5 | 1960 | 8.4439 | 1988--2020 | 2021-11-01
|  | RCPLOCA | Reactor Coolant Pump Seal Loss-of-Coolant Accident (PWR) | RADS | 0 | 1962.4 | Gamma | JNID/IL | 1e-06 | 0.000116 | 0.000255 | 0.00098 | 0.5 | 1960 | 8.4439 | 1988--2020 | 2021-11-01
|  | XLOCA | Excessive Loss-of-Coolant Accident (Vessel Rupture) | WASH-1285 | -- | -- | Gamma | Geo Mean Aggregate | 1.07e-11 | 2.44e-08 | 1e-07 | 4.57e-07 | 0.3 | 3000000 | 18.7656 | -- | 2005-06-23
Transients | General Transient | TRANS BWR | Transient Initiating Event (BWR) | RADS | 173 | 316.7 | Gamma | EB/PL/KS | 0.0798 | 0.452 | 0.555 | 1.38 | 1.71 | 3.08 | 3.0673 | 2011--2020 | 2021-11-01
|  | TRANS PWR | Transient Initiating Event (PWR) | RADS | 300 | 596.5 | Gamma | EB/PL/KS | 0.139 | 0.46 | 0.518 | 1.09 | 2.94 | 5.68 | 2.3739 | 2011--2020 | 2021-11-01
| Loss of Condenser Heat Sink | LOCHS BWR FI | Loss of Condenser Heat Sink (BWR) | RADS | 16 | 381.9 | Gamma | EB/PL/KS | 0.0177 | 0.0393 | 0.0419 | 0.0741 | 5.68 | 136 | 1.8843 | 2009--2020 | 2021-11-01
|  | LOCHS PWR FI | Loss of Condenser Heat Sink (PWR) | RADS | 23 | 909.8 | Gamma | EB/PL/KS | 0.0104 | 0.0238 | 0.0253 | 0.0457 | 5.35 | 211 | 1.9188 | 2006--2020 | 2021-11-01
| Loss of Feedwater | LOMFW | Loss of Main Feedwater | RADS | 20 | 913.2 | Gamma | EB/PL/KS | 0.00118 | 0.0153 | 0.0219 | 0.0651 | 1.02 | 46.6 | 4.2586 | 2011--2020 | 2021-11-01
Loss of Support Systems | Loss of Safety-Related Cooling Water | LOSWS | Loss of Safety Related Cooling Water (Open System) | RADS | 1 | 2951.7 | Gamma | JNID/IL | 5.96e-05 | 0.000401 | 0.000508 | 0.00132 | 1.5 | 2950 | 3.303 | 1988--2020 | 2021-11-01
|  | PLOSWS FI | Partial Loss of SWS Initiating Event | RADS | 4 | 2951.7 | Gamma | JNID/IL | 0.000564 | 0.00141 | 0.00152 | 0.00287 | 4.5 | 2950 | 2.028 | 1988--2020 | 2021-11-01
|  | LOCCW FI | Loss of Safety Related Cooling Water (Closed System) | RADS | 1 | 2951.7 | Gamma | JNID/IL | 5.96e-05 | 0.000401 | 0.000508 | 0.00132 | 1.5 | 2950 | 3.303 | 1988--2020 | 2021-11-01
|  | PLOCCW FI | Partial Loss of CCW Initiating Event | RADS | 4 | 2951.7 | Gamma | JNID/IL | 0.000564 | 0.00141 | 0.00152 | 0.00287 | 4.5 | 2950 | 2.028 | 1988--2020 | 2021-11-01
| Loss of Instrument Control Air | LOIA BWR | Loss of Instrument Air (BWR) | RADS | 6 | 916.9 | Gamma | EB/PL/KS | 0.000102 | 0.00374 | 0.00655 | 0.0225 | 0.68 | 104 | 6.0145 | 1991--2020 | 2021-11-01
|  | LOIA PWR | Loss of Instrument Air (PWR) | RADS | 10 | 1453.3 | Gamma | JNID/IL | 0.004 | 0.00701 | 0.00723 | 0.0113 | 10.5 | 1450 | 1.6064 | 1997--2020 | 2021-11-01
Loss of Offsite Power | Loss of Offsite Power, Power Operations | PO.LOOP | Loss-of-Offsite-Power, All Categories, Power Operations, per rcry | LOOP | 35 | 1388.9 | Gamma | EB/PL/KS | 0.00239 | 0.0192 | 0.0252 | 0.0683 | 1.33 | 52.8 | 3.5532 | 2006--2020 | 2021-11-01
|  | PO.LOOP-GR | Loss-of-Offsite-Power, Grid-Related, Power Operations, per rcry | LOOP | 7 | 1388.9 | Gamma | JNID/IL | 0.00261 | 0.00516 | 0.0054 | 0.00899 | 7.5 | 1390 | 1.7432 | 2006--2020 | 2021-11-01
|  | PO.LOOP-PC | Loss-of-Offsite-Power, Plant-Centered, Power Operations, per rcry | LOOP | 6 | 1388.9 | Gamma | JNID/IL | 0.00212 | 0.00444 | 0.00468 | 0.00804 | 6.5 | 1390 | 1.8122 | 2006--2020 | 2021-11-01
|  | PO.LOOP-SC | Loss-of-Offsite-Power, Switchyard-Centered, Power Operations, per rcry | LOOP | 12 | 1388.9 | Gamma | JNID/IL | 0.00526 | 0.00875 | 0.009 | 0.0135 | 12.5 | 1390 | 1.5472 | 2006--2020 | 2021-11-01
|  | PO.LOOP-WR | Loss-of-Offsite-Power, Weather-Related, Power Operations, per rcry | LOOP | 10 | 1388.9 | Gamma | EB/PL/KS | 0.000134 | 0.00425 | 0.00721 | 0.0244 | 0.713 | 98.8 | 5.7465 | 2006--2020 | 2021-11-01
| Loss of Offsite Power, Shutdown Operations | SD.LOOP | Loss-of-Offsite-Power, All Categories, Shutdown Operations, per rsy | RADS | 17 | 127.2 | Gamma | JNID/IL | 0.0884 | 0.135 | 0.138 | 0.196 | 17.5 | 127 | 1.4504 | 2006--2020 | 2021-11-01
|  | SD.LOOP-GR | Loss-of-Offsite-Power, Grid-Related, Shutdown Operations, per rsy | RADS | 2 | 127.2 | Gamma | JNID/IL | 0.00451 | 0.0171 | 0.0197 | 0.0436 | 2.5 | 127 | 2.5441 | 2006--2020 | 2021-11-01
|  | SD.LOOP-PC | Loss-of-Offsite-Power, Plant-Centered, Shutdown Operations, per rsy | RADS | 3 | 127.2 | Gamma | JNID/IL | 0.00853 | 0.025 | 0.0275 | 0.0554 | 3.5 | 127 | 2.2168 | 2006--2020 | 2021-11-01
|  | SD.LOOP-SC | Loss-of-Offsite-Power, Switchyard-Centered, Shutdown Operations, per rsy | RADS | 8 | 127.2 | Gamma | JNID/IL | 0.0341 | 0.0643 | 0.0668 | 0.109 | 8.5 | 127 | 1.6885 | 2006--2020 | 2021-11-01
|  | SD.LOOP-WR | Loss-of-Offsite-Power, Weather-Related, Shutdown Operations, per rsy | RADS | 4 | 127.2 | Gamma | JNID/IL | 0.0131 | 0.0328 | 0.0354 | 0.0666 | 4.5 | 127 | 2.028 | 2006--2020 | 2021-11-01
Electrical Power | Loss of AC Electrical Bus | LOAC | Loss of Vital AC Bus | RADS | 16 | 2635.4 | Gamma | JNID/IL | 0.00395 | 0.00612 | 0.00626 | 0.00898 | 16.5 | 2640 | 1.5 | 1992--2020 | 2021-11-01
|  | LOAC 4160V FI | Loss of Vital AC Bus (4160 Volt) | RADS | 11 | 2635.4 | Gamma | EB/PL/KS | 0.000334 | 0.0031 | 0.00416 | 0.0116 | 1.2 | 293 | 3.8 | 1992--2020 | 2021-11-01
|  | LOAC LOWV FI | Loss of Vital AC Bus (Low Voltage) | RADS | 5 | 2635.4 | Gamma | JNID/IL | 0.000866 | 0.00196 | 0.00209 | 0.00373 | 5.5 | 2640 | 1.9026 | 1992--2020 | 2021-11-01
|  | LOACB2 | Loss of Vital AC Bus Event (2 Buses modeled as IEs) | RADS Adjusted | (note c) | -- | Gamma | JNID/IL | 3.15e-07 | 0.000717 | 0.00294 | 0.0134 | 0.3 | 102.041 | 18.7656 | 1992--2020 | 2021-11-01
| Loss of DC Electrical Bus | LODC | Loss of Vital DC Bus | RADS | 2 | 2951.7 | Gamma | JNID/IL | 0.000194 | 0.000738 | 0.000847 | 0.00188 | 2.5 | 2950 | 2.5441 | 1988--2020 | 2021-11-01
|  | LODCB2 | Loss of Vital DC Bus Event (2 Buses modeled as IEs) | RADS Adjusted | (note c) | -- | Gamma | JNID/IL | 4.53e-08 | 0.000103 | 0.000424 | 0.00194 | 0.3 | 708.383 | 18.7656 | 1988--2020 | 2021-11-01
Acronyms - BWR (boiling water reactor), CCW (component cooling water), EB (empirical Bayes), EE (expert elicitation), FI (functional impact), FWLB (feedwater line break), GR (grid-related), IE (initiating event), IEDB (initiating events database - http://nrcoe.inl.gov), IL (industry level), ISLOCA (interfacing system loss-of-coolant accident), KS (Kass-Steffey), JNID (Jeffreys noninformative distribution), LOCCW (loss of component cooling water), LLOCA (large loss-of-coolant event), LOAC (loss of vital ac bus), LOCHS (loss of condenser heat sink), LODC (loss of vital dc bus), LOIA (loss of instrument air), LOMFW (loss of main feedwater), LOOP (loss-of-offsite-power), LOSWS (loss of emergency service water), MLOCA (medium loss-of-accident accident), PC (plant-centered), PL (plant level), PLOCCW (partial loss of component cooling water), PLOSWS (partial loss of emergency service water), PO (power operations), PWR (pressurized water reactor), RADS (Reliability and Availability Database System), rcry (reactor critical year), RCPLOCA (reactor coolant pump seal loss-of-coolant accident), rsy (reactor shutdown year), SC (switchyard-centered), SD (shutdown operations), SGTR (steam generator tube rupture), SLBIC (steam line break inside containment), SLBOC (steam line break outside containment), SLOCA (small loss-of-coolant accident), SORV (stuck open safety/relief valve), TRANS (transient), VSLOCA (very small loss-of-coolant accident), WR (weather-related), XLOCA (excessive loss-of-coolant accident) Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in ASME/ANS RA-Sa-2009 and outlined in Section 6.2.3.5 of NUREG/CR-6823. Note b - The NUREG-1829 results are used as the prior to Bayesian update the newer observed data. Note c – The mean value of the loss of two AC (or DC) buses frequency are calculated by dividing the mean value of the loss of one vital AC (or DC) bus.

## Train UA
SPAR Basic Event Unavailability Data and Results
2020 Parameter Estimation Update
2021-11-01 18:53 |  | Parameter Estimate 2020 V1
Section | Sub Section | Train Unavailability Event | Train Description | Data Source | Analysis | Data | Industry-average Probability Distribution (note a) | [8 empty] | Date Range | Comments | Effective Date
[6 empty] | MSPI Trains | Distribution (note b) | 5th | Median | Mean | 95th | α | β | Std Dev | Error Factor
Generators | 1E EDG | EDG-EPS | Diesel Generator Test or Maintenance | EPIX/RADS | CurveFit/Train | 258 | Normal | 0.00348 | 0.0151 | 0.0151 | 0.0267 | -- | -- | 0.00704 | 1.7692 | 2006--2020 |  | 2021-11-01
| Combustion Turbine | CTG | Combustion Turbine Generator Test or Maintenance | IPEs | SCNID (IPEs/2) | -- | Beta | 0.000212 | 0.0243 | 0.05 | 0.187 | 0.5 | 9.5 | -- | 7.7165 | -- | (Note c) | 2005-06-23
| HPCS | EDG-HCS | HPCS Diesel Generator Test or Maintenance | EPIX/RADS | CurveFit/Train | 8 | Normal | 0.00713 | 0.0133 | 0.0133 | 0.0194 | -- | -- | 0.00374 | 1.4634 | 2006--2020 |  | 2021-11-01
| Generator Service Water | EDG-SW | Service Water for Emergency Diesel Generator Test or Maintenance | EPIX/RADS | CurveFit/Train | 6 | Normal | -0.000449 | 0.0111 | 0.0111 | 0.0227 | -- | -- | 0.00704 | 2.0404 | 2006--2020 |  | 2021-11-01
|  | HCS-SW | Service Water for High Pressure Core Spray Generator Test or Maintenance | EPIX/RADS | CurveFit/Train | 7 | Normal | 0.00491 | 0.00732 | 0.00732 | 0.00972 | -- | -- | 0.00146 | 1.3286 | 2006--2020 |  | 2021-11-01
Pumps | Motor Driven | MDP-ALL | Motor-Driven Pump Test or Maintenance (All Clean Systems) | EPIX/RADS | CurveFit/Train | 1061 | Normal | -0.00839 | 0.00656 | 0.00656 | 0.0215 | -- | -- | 0.00909 | 3.2774 | 2006--2020 |  | 2021-11-01
|  | MDP-AFW | Motor-Driven Pump Test or Maintenance (AFW) | EPIX/RADS | CurveFit/Train | 124 | Normal | -0.000201 | 0.00314 | 0.00314 | 0.00649 | -- | -- | 0.00203 | 2.064 | 2006--2020 |  | 2021-11-01
|  | MDP-CCW | Motor-Driven Pump Test or Maintenance (CCW) | EPIX/RADS | CurveFit/Train | 142 | Normal | -0.00558 | 0.00482 | 0.00482 | 0.0152 | -- | -- | 0.00632 | 3.1573 | 2006--2020 |  | 2021-11-01
|  | MDP-ESW | Motor-Driven Pump Test or Maintenance (ESW) | EPIX/RADS | CurveFit/Train | 305 | Normal | -0.0112 | 0.0124 | 0.0124 | 0.0361 | -- | -- | 0.0144 | 2.8993 | 2006--2020 |  | 2021-11-01
|  | MDP-FWS | Feed Water System Motor-Driven Pumps Test or Maintenance | EPIX/RADS | CurveFit/Train | 4 | Normal | 0.00643 | 0.00768 | 0.00768 | 0.00893 | -- | -- | 0.000761 | 1.163 | 2006--2020 |  | 2021-11-01
|  | MDP-HCS | Motor-Driven Pump Test or Maintenance (HCS) | EPIX/RADS | CurveFit/Train | 8 | Normal | 0.00422 | 0.00768 | 0.00768 | 0.0111 | -- | -- | 0.0021 | 1.4506 | 2006--2020 |  | 2021-11-01
|  | MDP-HPI | Motor-Driven Pump Test or Maintenance (HPI) | EPIX/RADS | CurveFit/Train | 199 | Normal | -0.000432 | 0.00299 | 0.00299 | 0.0064 | -- | -- | 0.00208 | 2.1447 | 2006--2020 |  | 2021-11-01
|  | MDP-RHR | Motor-Driven Pump Test or Maintenance (RHR) | EPIX/RADS | CurveFit/Train | 225 | Normal | 0.000391 | 0.00509 | 0.00509 | 0.00979 | -- | -- | 0.00286 | 1.9233 | 2006--2020 |  | 2021-11-01
|  | MDP-RHR-BWR | Motor-Driven Pump Test or Maintenance (RHR-BWR) | EPIX/RADS | CurveFit/Train | 80 | Normal | 0.00184 | 0.00592 | 0.00592 | 0.01 | -- | -- | 0.00248 | 1.689 | 2006--2020 |  | 2021-11-01
|  | MDP-RHR-PWR | Motor-Driven Pump Test or Maintenance (RHR-PWR) | EPIX/RADS | CurveFit/Train | 145 | Normal | -0.000228 | 0.00463 | 0.00463 | 0.0095 | -- | -- | 0.00296 | 2.0492 | 2006--2020 |  | 2021-11-01
|  | MDP-RHRSW | Motor-Driven Pump Test or Maintenance (RHR Service Water) | EPIX/RADS | CurveFit/Train | 54 | Normal | 0.000443 | 0.00491 | 0.00491 | 0.00938 | -- | -- | 0.00272 | 1.9097 | 2006--2020 |  | 2021-11-01
|  | PDP | Positive Displacement Pump Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 1.26e-05 | 0.00146 | 0.00319 | 0.0123 | 0.5 | 156 | -- | 8.3982 | -- | (Note c) | 2005-06-23
|  | MDP-CLEAN | Motor-Driven Pump Test or Maintenance (Clean System) | EPIX/RADS | CurveFit/Train | 702 | Normal | -0.00197 | 0.00414 | 0.00414 | 0.0102 | -- | -- | 0.00371 | 2.4756 | 2006--2020 |  | 2021-11-01
|  | MDP-NR-CLEAN | Motor-Driven Pump Test & Maintenance (Normally Running System, Clean) | EPIX/RADS | CurveFit/Train | 146 | Normal | -0.00539 | 0.0049 | 0.0049 | 0.0152 | -- | -- | 0.00625 | 3.0995 | 2006--2020 |  | 2021-11-01
|  | MDP-NS-CLEAN | Motor-Driven Pump Test or Maintenance (Normally Standby System, Clean) | EPIX/RADS | CurveFit/Train | 556 | Normal | -0.000417 | 0.00394 | 0.00394 | 0.0083 | -- | -- | 0.00265 | 2.1058 | 2006--2020 |  | 2021-11-01
|  | MDP-NR-DIRTY | Motor-Driven Pump Test or Maintenance (Normally Running System, Dirty) | EPIX/RADS | CurveFit/Train | 305 | Normal | -0.0112 | 0.0124 | 0.0124 | 0.0361 | -- | -- | 0.0144 | 2.8993 | 2006--2020 |  | 2021-11-01
|  | MDP-NS-DIRTY | Motor-Driven Pump Test or Maintenance (Normally Standby System, Dirty) | EPIX/RADS | CurveFit/Train | 359 | Normal | -0.011 | 0.0113 | 0.0113 | 0.0336 | -- | -- | 0.0135 | 2.9709 | 2006--2020 |  | 2021-11-01
| Turbine Driven | TDP-ALL | Turbine-Driven Pump Test or Maintenance (AFW, HPCI, and RCIC combined) | EPIX/RADS | CurveFit/Train | 120 | Normal | 1.16e-05 | 0.0073 | 0.0073 | 0.0146 | -- | -- | 0.00443 | 1.9984 | 2006--2020 |  | 2021-11-01
|  | TDP-AFW | Turbine-Driven Pump Test or Maintenance (AFW) | EPIX/RADS | CurveFit/Train | 66 | Normal | -0.000271 | 0.00464 | 0.00464 | 0.00955 | -- | -- | 0.00299 | 2.0585 | 2006--2020 |  | 2021-11-01
|  | TDP-HCI | Turbine-Driven Pump Test or Maintenance (HPCI) | EPIX/RADS | CurveFit/Train | 24 | Normal | 0.00657 | 0.0111 | 0.0111 | 0.0157 | -- | -- | 0.00277 | 1.4098 | 2006--2020 |  | 2021-11-01
|  | TDP-RCI | Turbine-Driven Pump Test or Maintenance (RCIC) | EPIX/RADS | CurveFit/Train | 30 | Normal | 0.00307 | 0.0101 | 0.0101 | 0.0171 | -- | -- | 0.00426 | 1.6956 | 2006--2020 |  | 2021-11-01
|  | TDP-HCI-RCI | Turbine-Driven Pump Test or Maintenance (HPCI and RCIC combined) | EPIX/RADS | CurveFit/Train | 24 | Normal | 0.00657 | 0.0111 | 0.0111 | 0.0157 | -- | -- | 0.00277 | 1.4098 | 2006--2020 |  | 2021-11-01
| Engine Driven | EDP | Engine-Driven Pump Test or Maintenance | EPIX/RADS | CurveFit/Train | 15 | Normal | -0.00287 | 0.0227 | 0.0227 | 0.0483 | -- | -- | 0.0156 | 2.1261 | 2006--2020 |  | 2021-11-01
|  | EDP-AFW | Engine-Driven Pump Test or Maintenance | EPIX/RADS | CurveFit/Train | 5 | Normal | 0.0021 | 0.00547 | 0.00547 | 0.00885 | -- | -- | 0.00205 | 1.6161 | 2006--2020 |  | 2021-11-01
|  | EDP-ESW | Engine-Driven Pump Test or Maintenance | EPIX/RADS | CurveFit/Train | 10 | Normal | 0.0129 | 0.0314 | 0.0314 | 0.0499 | -- | -- | 0.0113 | 1.5902 | 2006--2020 |  | 2021-11-01
Heat Exchangers | Pooled | HTX | Heat Exchanger Test or Maintenance | EPIX/RADS | CurveFit/Train | 98 | Normal | -0.00713 | 0.00763 | 0.00763 | 0.0224 | -- | -- | 0.00897 | 2.934 | 2006--2020 |  | 2021-11-01
| CCW | HTX-CCW | Heat Exchanger Test or Maintenance (CCW) | EPIX/RADS | CurveFit/Train | 86 | Normal | -0.00743 | 0.00773 | 0.00773 | 0.0229 | -- | -- | 0.00922 | 2.961 | 2006--2020 |  | 2021-11-01
| Service Water | HTX-ESW | Heat Exchanger Test or Maintenance (ESW) | EPIX/RADS | CurveFit/Train | 4 | Normal | 0.00974 | 0.0161 | 0.0161 | 0.0224 | -- | -- | 0.00384 | 1.3931 | 2006--2020 |  | 2021-11-01
| Residual Heat Removal | HTX-RHR-BWR | Heat Exchanger and Pump Train Test or Maintenance (RHR-BWR) | EPIX/RADS | CurveFit/Train | 6 | Normal | -0.000447 | 0.00305 | 0.00305 | 0.00655 | -- | -- | 0.00213 | 2.1464 | 2006--2020 |  | 2021-11-01
|  | HTX-RHR-PWR | Heat Exchanger and Pump Train Test or Maintenance (RHR-BWR) | EPIX/RADS | CurveFit/Year | 15 | Normal | -0.000497 | 0.000209 | 0.000209 | 0.000915 | -- | -- | 0.000429 | 4.3737 | 2006--2020 |  | 2021-11-01
Electrical | Breaker | CRB | Circuit Breaker Test or Maintenance | Unknown | CurveFit | -- | Beta | -- | -- | 0.5 | -- | 0.5 | -- | -- | -- | -- |  | 2005-06-23
| Bus | BDC | Bus (DC) Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 7.87e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2499.5 | -- | 8.4411 | -- | (Note c) | 2005-06-23
|  | BAC | Bus (AC) Test or Maintenance | IPEs | IPEs | -- | Beta | 7.87e-07 | 9.1e-05 | 0.0002 | 0.000768 | 0.5 | 2499.5 | -- | 8.4411 | -- | (Note c) | 2005-06-23
| Battery | BAT | Battery Test or Maintenance | Letter | CurveFit | -- | Lognormal | 2.8e-06 | 0.000148 | 0.00272 | 0.00784 | -- |  | -- | 52.9 | -- |  | 2005-06-23
|  | BCH | Battery Charger Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | -- | 8.4153 | -- | (Note c) | 2005-06-23
| Transformer | TFM | Startup Transformer Test or Maintenance | Letter | CurveFit | -- | Lognormal | 4.55e-07 | 4.11e-05 | 0.00175 | 0.00372 | -- | -- | -- | 90.5 | -- | (Note d) | 2005-06-23
| RPS | CCP-RPS | RPS Channel A Test or Maintenance | RPS SS | NUREG/CR-5500 | -- | Beta | 4.14e-05 | 0.00478 | 0.005 | 0.0396 | 0.5 | 47.76 | -- | 8.2952 | -- | (Note e) | 2005-06-23
Other | Ventilation | AHU | Air Handling Unit Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 9.87e-06 | 0.00114 | 0.0025 | 0.00959 | 0.5 | 199.5 | -- | 8.4082 | -- | (Note c) | 2005-06-23
|  | CHL | Chiller Test or Maintenance | IPEs | SCNID (IPEs/2) | -- | Beta | 8.11e-05 | 0.00934 | 0.02 | 0.0761 | 0.5 | 24.5 | -- | 8.1559 | -- | (Note c) | 2005-06-23
| Compressor | MDC | Motor-Driven Compressor Test or Maintenance | IPEs | SCNID (IPEs/2) | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | -- | 8.2716 | -- | (Note c) | 2005-06-23
|  | DDC | Diesel-Driven Compressor Test or Maintenance | Existing SPAR | JNID/IL | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | -- | 8.2716 | -- | From MDC | 2005-06-23
|  | EDC | Engine-Driven Compressor Test or Maintenance | IPEs | SCNID (IPEs/2) | -- | Beta | 4.8e-05 | 0.00554 | 0.012 | 0.0459 | 0.5 | 41.1667 | -- | 8.2716 | -- | (Note c) | 2005-06-23
| Fan | FAN | Fan Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | -- | 8.4153 | -- | (Note c) | 2005-06-23
|  | CTF | Cooling Tower Fan Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 7.89e-06 | 0.000912 | 0.002 | 0.00768 | 0.5 | 249.5 | -- | 8.4153 | -- | (Note c) | 2005-06-23
| Explosive Valve | EPV | Explosive-Operated (SQUIBB) Valve Test or Maintenance | IPEs | SCNID (IPEs) | -- | Beta | 2.36e-06 | 0.000273 | 0.0006 | 0.0023 | 0.5 | 832.833 | -- | 8.4354 | -- | (Note c) | 2005-06-23
Headers | Clean Water | HDR-AFW | AFW Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 16 | Normal | -0.00107 | 0.00077 | 0.00077 | 0.00261 | -- | -- | 0.00112 | 3.3951 | 2006--2020 |  | 2021-11-01
|  | HDR-CCW | CCW Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 6 | Normal | -0.000416 | 0.000242 | 0.000242 | 0.0009 | -- | -- | 0.0004 | 3.716 | 2006--2020 |  | 2021-11-01
|  | HDR-HPI | HPSI Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 45 | Normal | -0.000268 | 0.000136 | 0.000136 | 0.000541 | -- | -- | 0.000246 | 3.9672 | 2006--2020 |  | 2021-11-01
|  | HDR-ISO | ISO Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 6 | Normal | 0.000724 | 0.00262 | 0.00262 | 0.00452 | -- | -- | 0.00115 | 1.724 | 2006--2020 |  | 2021-11-01
|  | HDR-RHR | RHR Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 16 | Normal | -0.00139 | 0.000721 | 0.000721 | 0.00283 | -- | -- | 0.00128 | 3.9246 | 2006--2020 |  | 2021-11-01
| Service Water | HDR-ESW | ESW Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 123 | Normal | -0.0234 | 0.00461 | 0.00461 | 0.0326 | -- | -- | 0.017 | 7.065 | 2006--2020 |  | 2021-11-01
|  | HDR-RHRSW | RHRSW Header Test or Maintenance | EPIX/RADS | CurveFit/Train | 8 | Normal | -0.00296 | 0.00281 | 0.00281 | 0.00857 | -- | -- | 0.0035 | 3.0549 | 2006--2020 |  | 2021-11-01
Acronyms - ACX or AHU (air handling unit), AFW (auxiliary feedwater system), BAC (ac bus), BAT (battery), BCH (battery charger), BDC (dc bus), BWR (boiling water reactor), CCP (channel calculator for pressure), CCW (component cooling water), CHL (chiller), CRB (circuit breaker), CTF (cooling tower fan), CTG (combustion turbine generator), DDC (diesel-driven compressor), EDG (emergency diesel generator), EDP (engine-driven pump), EPIX (Equipment Performance and Information Exchange), EPS (emergency power system), EPV (explosive-operated valve), ESW (emergency or essential service water), FWS (feed water system), HDR (header), HPCI or HCI (high-pressure coolant injection), HPCS or HCS (high-pressure core spray), HPSI or HPI (high pressure safety injection), HTX (heat exchanger), IPE (individual plant examination), ISO (isolation condenser), MDC (motor-driven compressor), MDP (motor-driven pump), MOV (motor-operated valve), NR(normally running), NS (normally standby), PDP (positive displacement pump), PWR (pressurized water reactor), RADS (Reliability and Availability Database System), RCIC or RCI (reactor core isolation cooling), RHR (residual heat removal), RPS (reactor protection system), SCNID (simplified constrained noninformative distribution), SS (system study), SW (service water), TDP (turbine-driven pump), TFM (transformer), YL (year level) Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in ASME/ANS RA-Sa-2009 and outlined in Section 6.2.3.5 of NUREG/CR-6823. Note b - For the ROP UAs using the MSPI data and assessed through RADS, the mean is the average of individual train UAs. Each train UA is the total number of planned and unplanned outage hours divided by total number of plant critical hours. The percentiles were obtained from the ordered set of train UAs. The error factor is the 95th percentile divided by the median. Note c - The UA results are from NUREG/CR-6928 and supported by IPE data. For IPE data with UA estimates > 0.005, the IPE mean was divided by two. For IPE data with UA estimates <0.005, the IPE result was used directly. See Appendix B in NUREG/CR-6928 for details. Note d - The UA results are from the INL Letter: Generic Test and Maintenance Unavailability Values, JCN W6467 - MBS-02-99. Note e - The UA results are supported by the RPS system study (NUREG/CR-5500, Vol 2,3,10, and 11).

## Special Events
SPAR Special Event Data and Results
2020 Parameter Estimation Update
Special Event Name | System Study Name | Description | Existing SPAR Value |  | Data Source | Data | [6 empty] | Industry-average Probability or Rate Distribution (note a) |  |  |  |  | Comments | [5 empty] | Effective Date
|  |  | Mean | Units |  | Failures | Demands or Hours | MLE | Jeffreys Mean | Error Factor | Data Source | d or h | Distribution (note b) | Mean | α | β | Error Factor |  | Recommended Improvement | 95% | Median | 95% | Median
TDP-PRST (RCIC) | IFRS | RCIC TDP probability of restart | 0.26 | D | SS | 6 | 47 | 0.12766 | 0.13542 | ? | System Study (1996 - 2002) | d | Beta (Jeffreys, Jeffreys) | 0.13542 | 6.5 | 41.5 | 1.7163 |  |  | #REF! | #REF! | 0.22371 | 0.13034 | 2007-02-01
TDP-FRST (RCIC) | LNRS | RCIC TDP restart failure per event | 0.24 | D | SS | 1 | 17 | 0.058824 | 0.083333 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.083333 | 0.5 | 5.5 | 7.2198 |  |  | #REF! | #REF! | 0.30575 | 0.042348 | 2007-02-01
TDP-FRFRST (RCIC) | FRFTRS | RCIC failure to recover TDP restart failure | 0.5 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1991 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | #REF! | #REF! | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (RCIC) | PMI | RCIC injection valve probability of multiple injections | ? | D | SS | 14 | 28 | 0.5 | 0.5 | ? | System Study (1998 - 2002) | d | Beta (EB/YL/KS, EB/YL/KS) | 0.503 | 4.18 | 4.1301 | 1.5354 |  |  | #REF! | #REF! | 0.77267 | 0.50325 | 2007-02-01
MOV-FTRO (RCIC) | FRO | RCIC injection valve fails to reopen | ? | D | SS | 1 | 38 | 0.026316 | 0.038462 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.038462 | 0.5 | 12.5 | 7.8865 |  |  | #REF! | #REF! | 0.14506 | 0.018393 | 2007-02-01
MOV-FRFTRO (RCIC) | FRFRO | RCIC failure to recover injection valve failure to reopen | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 |  |  | #REF! | #REF! | 1 | 0.95096 | 2007-02-01
SUC-FTFRI (RCIC) | LNRC | RCIC failure to transfer back to injection mode (pump recirculation valve) | 0.034 | D | SS | 1 | 197.95 | 0.0050518 | 0.0075777 | ? | System Study (1988 - 2002) | h | Gamma (Jeffreys, SCNID) | 0.0075777 | 0.5 | 65.9833 | 8.4439 | (note c) |  | #REF! | #REF! | 126.7361 | 15.0091 | 2007-02-01
SUC-FRFTFR (RCIC) | FRFTRC | RCIC failure to recover transfer failure | 0.17 | D | SS | 0 | 1 | 0 | 0.25 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.25 | 0.5 | 1.5 | 4.7274 |  |  | #REF! | #REF! | 0.77148 | 0.16319 | 2007-02-01
MOV-PMINJ (HPCI) | PMI | HPCI injection valve probability of multiple injections | 0.13 | D | SS | 2 | 17 | 0.11765 | 0.13889 | ? | System Study (1995 - 2002) | d | Beta (Jeffreys, SCNID) | 0.13889 | 0.5 | 3.1 | 6.38 |  |  | #REF! | #REF! | 0.48738 | 0.076392 | 2007-02-01
MOV-FTRO (HPCI) | FRO | HPCI injection valve fails to reopen | 0.192 | D | SS | 1 | 8 | 0.125 | 0.16667 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.16667 | 0.5 | 2.5 | 5.9592 |  |  | #REF! | #REF! | 0.56926 | 0.095526 | 2007-02-01
MOV-FRFTRO (HPCI) | FRFRO | HPCI failure to recover injection valve failure to reopen | 0.833 | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 |  |  | #REF! | #REF! | 1 | 0.95096 | 2007-02-01
SUC-FTFR (HPCI) | FTRT | HPCI failure to transfer | ? | D | SS | 0 | 1270 | 0 | 0.00039339 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.00039339 | 0.5 | 1270.5 | 8.4383 |  |  | #REF! | #REF! | 0.0015109 | 0.00017906 | 2007-02-01
SUC-FRFTFR (HPCI) | FRFTRT | HPCI failure to recover transfer failure | ? | D | SS | 0 | 0 | #DIV/0! | 0.5 | ? | System Study (1989 - 2002) | d | Beta (Jeffreys, SCNID) | 0.5 | 0.5 | 0.5 | 1.9877 |  |  | #REF! | #REF! | 0.99384 | 0.5 | 2007-02-01
SUC-FTFR (HPCS) | FTRT | HPCS failure to transfer | ? | D | SS | 1 | 478 | 0.0020921 | 0.0031315 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.0031315 | 0.5 | 159.1667 | 8.3991 |  |  | #REF! | #REF! | 0.012014 | 0.0014303 | 2007-02-01
SUC-FRFTFR (HPCS) | FRFTRT | HPCS failure to recover transfer failure | ? | D | SS | 1 | 1 | 1 | 0.75 | ? | System Study (1988 - 2002) | d | Beta (Jeffreys, SCNID) | 0.75 | 0.5 | 0.16667 | 1.0516 |  |  | #REF! | #REF! | 1 | 0.95096 | 2007-02-01
Acronyms - EB (empirical Bayes), HPCI (high-pressure coolant injection), HPCS (high-pressure core spray), KS (Kass-Steffey), MOV (motor-operated valve), RCIC (reactor core isolation cooling), SCNID (simplified constrained noninformative distribution), SUC (suction), SS (updated system study), TDP (turbine-driven pump), YL (year level) Note a - If these distributions are to be used as priors in Bayesian updates using plant-specific data, then a check for consistency between the prior and the data should be performed first, as suggested in supporting requirement DA-D4c in ASME/ANS RA-Sa-2009 and outlined in Section 6.2.3.5 of NUREG/CR-6823. Note b - The format for the distributions is the following: distribution type (source for mean, source for α factor). Note c - Note that this is per hour. Failure occurred 8 min after RCIC initiation.