410 | 4101988026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101988026R00.pdf | 1988-06-28 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 9 | POWER LEVEL - 009%. ON JUNE 28, 1988 AT 2012 HOURS NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN ACTUATION OF AN ENGINEERED SAFETY FEATURE, SPECIFICALLY, A REACTOR SCRAM. AT THE TIME OF THE EVENT, THE PLANT WAS IN A STARTUP CONDITION WITH THE REACTOR MODE SWITCH IN THE 'STARTUP/HOT STANDBY' POSITION. REACTOR PRESSURE AND COOLANT TEMPERATURE WERE APPROXIMATELY 850 POUNDS PER SQUARE INCH GAUGE (PSIG) AND 527F, RESPECTIVELY. THE REACTOR WAS OPERATING AT APPROXIMATELY 9% OF RATED THERMAL POWER. THE SCRAM OCCURRED DUE TO AN AVERAGE POWER RANGE MONITOR (APRM) UPSCALE TRIP. THE IMMEDIATE CAUSE OF THE SCRAM HAS BEEN ATTRIBUTED TO FLOW 'CHANGES' IN THE REHEAT SYSTEM AND SUBSEQUENT CHANGES IN REACTOR STEAM LOADS. THE ROOT CAUSE OF THIS EVENT HAS BEEN DETERMINED TO BE OPERATOR ERROR. SECONDARY CAUSES OF THIS EVENT HAVE BEEN DETERMINED TO BE PROCEDURAL DEFICIENCY AND TRAINING DEFICIENCY. FOLLOWING THE REACTOR SCRAM, THE TECH SPEC MAXIMUM ALLOWABLE COOLDOWN RATE OF 100F/ HOUR WAS EXCEEDED. ALL APPLICABLE ACTION REQUIREMENTS WERE MET. INITIAL ACTION WAS TO ENTER INTO OPERATING PROCEDURE N2-OP-101C, 'SCRAM RECOVERY'. CORRECTIVE ACTION HAS BEEN TO MODIFY PROCEDURE N2-OP-2, 'MOISTURE SEPARATOR REHEATER SYSTEM', AND TO ISSUE A LESSONS LEARNED TRANSMITTAL TO THE OPERATIONS DEPARTMENT, AND ISSUE A TRAINING MODIFICATION RECOMMENDATION TO THE TRAINING DEPARTMENT.
410 | 4101988028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101988028R00.pdf | 1988-07-11 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 45 | POWER LEVEL - 045%. ON JULY 11, 1988 AT 0305 HOURS NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN ACTUATION OF AN ENGINEERED SAFETY FEATURE, SPECIFICALLY A MANUAL REACTOR SCRAM. AT THE TIME OF THE EVENT THE REACTOR MODE SWITCH WAS IN THE 'RUN' POSITION WITH THE REACTOR AT APPROXIMATELY 45% OF RATED THERMAL POWER. AT APPROXIMATELY 0037 HOURS ON JULY 11, 1988 AN ELECTROHYDRAULIC CONTROL (EHC) FLUID LEAK WAS DISCOVERED ON A TURBINE CONTROL VALVE. ATTEMPTS TO ISOLATE THE LEAK WERE UNSUCCESSFUL. UPON REACHING THE LOW LEVEL POINT IN THE EHC RESERVOIR, THE DECISION WAS MADE TO MANUALLY SCRAM THE REACTOR. THE SCRAM WAS INITIATED AT 0305 HOURS. THE IMMEDIATE CAUSE OF THE EVENT WAS A LOOSE FITTING CAUSING AN EHC FLUID LEAK. THE MOST PROBABLE ROOT CAUSE IS INSTALLATION DEFICIENCY BY CONTRACTOR PERSONNEL. IMMEDIATE ACTION WAS TO ENTER INTO OPERATING PROCEDURE N2-OP-101C, 'SCRAM RECOVERY'. CORRECTIVE ACTIONS INCLUDE THE ISSUANCE OF A WORK REQUEST TO REPAIR THE EHC FITTING LEAK AND ISSUANCE OF A PROBLEM REPORT TO INITIATE CORRECTIVE ACTIONS, AS REQUIRED, TO PREVENT SIMILAR OCCURRENCES.
410 | 4101988039 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101988039R01.pdf | 1988-08-06 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 53 | POWER LEVEL - 053%. ON AUGUST 6, 1988 AT 2101 HOURS NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN ACTUATION OF AN ENGINEERED SAFETY FEATURE, SPECIFICALLY A REACTOR SCRAM. AT THE TIME OF THE EVENT THE REACTOR MODE SWITCH WAS IN THE 'RUN' POSITION WITH THE REACTOR AT APPROXIMATELY 53% OF RATED THERMAL POWER. AT APPROXIMATELY 2053 HOURS OPERATIONS PERSONNEL OBSERVED THAT TURBINE ELECTROHYDRAULIC CONTROL SYSTEM (EHC) PRESSURE WAS DECREASING RAPIDLY. THE EHC PRESSURE DECREASE WAS DUE TO AN EHC OIL LEAK. THE LOW EHC OIL PRESSURE INITIATED A TRIP OF THE TURBINE RESULTING IN AN AUTOMATIC REACTOR SCRAM. REACTOR PRESSURE CONTROL WAS MAINTAINED DURING THE EVENT. THE EHC OIL LEAK WAS DUE TO THE FAILURE OF AN EHC FLUID PIPE NIPPLE. THE IMMEDIATE CAUSE OF THE PIPE FAILURE HAS BEEN ATTRIBUTED TO EXCESSIVE VIBRATION. VIBRATION CAUSED THE CLAMP USED TO SUPPORT THE FAILED PIPE TO ITS SUPPORT FRAME TO FAIL. THE PIPE THEN VIBRATED EXCESSIVELY CAUSING BENDING AT THE PUMP DISCHARGE PIPING. THIS RESULTED IN FATIGUE STRESS AND EVENTUAL FAILURE. OPERATOR ACTIONS WERE TO SECURE THE EHC PUMPS AND ISSUE A WORK REQUEST (WR 136781) TO REPLACE THE FAILED PIPE AND SECURE THE CLAMP. A WORK REQUEST (WR 135422) WAS ALSO ISSUED TO DETERMINE THE CAUSE OF THE VIBRATION.
410 | 4101988051 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101988051R00.pdf | 1988-09-22 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 64 | POWER LEVEL - 064%. ON SEPTEMBER 22, 1988 AT 1339 HOURS, WITH THE REACTOR AT APPROXIMATELY 64% OF RATED THERMAL POWER AND THE MODE SWITCH IN 'RUN', NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN ACTUATION OF AN ENGINEERED SAFETY FEATURE (ESF). SPECIFICALLY, THE ESF CONSISTED OF A MANUAL REACTOR SCRAM. AS A RESULT OF A POST MAINTENANCE VALVE STROKE ON SERVICE WATER VALVE 2SWP*MOV18B, THE SERVICE WATER SYSTEM (SWP) WAS CROSS CONNECTED TO THE REACTOR BUILDING CLOSED LOOP COOLING SYSTEM (CCP). THIS CROSS CONNECTION CAUSED LOSS OF CCP INVENTORY TO THE SERVICE WATER DISCHARGE HEADER, WHICH EVENTUALLY RESULTED IN THE TRIP OF CCP BOOSTER PUMPS ON LOW SUCTION PRESSURE. UPON LOSS OF CCP, THE STATION SHIFT SUPERVISOR ORDERED A MANUAL SCRAM IN ACCORDANCE WITH N2-OP-13, 'REACTOR BUILDING CLOSED LOOP COOLING'. THE CAUSE OF THIS EVENT WAS PERSONNEL ERROR DUE TO INATTENTION TO DETAIL. OPERATIONS PERSONNEL FAILED TO ASSESS THE IMPACT OF OPENING 2SWP*MOV18B WITH THE EXISTING SYSTEM CONFIGURATION. CORRECTIVE ACTIONS ARE AS FOLLOWS: 1) CCP WAS RETURNED TO NORMAL AND HOLD OUT TAGS WERE PLACED ON THE CCP AND SWP VALVE CONTROLS; 2) AN OPERATOR AID HAS BEEN ADDED TO THE CONTROL ROOM PANELS WARNING OF THE IMPACT OF OPENING THE SERVICE WATER CROSSTIE VALVES; 3) A LESSONS LEARNED HAS BEEN ISSUED STRESSING THE IMPORTANCE OF ASSESSING PLANT IMPACT.
410 | 4101989014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989014R00.pdf | 1989-04-13 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | POWER LEVEL - 100%. ON APRIL 13, 1989 AT 1101 HOURS WITH THE REACTOR MODE SWITCH IN RUN, AND THE REACTOR AT 100% RATED THERMAL POWER, NINE MILE POINT UNIT 2 EXPERIENCED A REACTOR SCRAM. THIS EVENT WAS A RESULT OF A TURBINE TRIP DUE TO THE ACTUATION OF THE GENERATOR PROTECTION CIRCUITRY. THE GENERATOR PROTECTION CIRCUITRY INITIATED A FAST TRANSFER OF HOUSE SERVICE LOADS TO THE STATION RESERVE TRANSFORMERS. ONE OF THE 13.8KV ELECTRICAL BUSES FAILED TO TRANSFER WHICH CAUSED A LOSS OF FEEDWATER. REACTOR WATER LEVEL DECREASED AS THE TURBINE CONTROL BYPASS VALVES MODULATED TO CONTROL REACTOR PRESSURE, WHICH CAUSED THE AUTOMATIC ACTUATION OF THE HIGH PRESSURE CORE SPRAY (CSH) AND REACTOR CORE ISOLATION COOLING (ICS) SYSTEMS. THE CAUSE FOR THE TURBINE TRIP WAS DETERMINED TO BE A DISCONNECTED WIRE LOCATED IN THE MAIN GENERATOR POTENTIAL TRANSFORMER CUBICAL. THIS CREATED A SIGNAL TO THE TRIPPING AND ALARM RELAYS CAUSING A TURBINE TRIP. THE CAUSE FOR THE 13.8KV BUS FAST TRANSFER FAILURE WAS DETERMINED TO BE THE POSITIVE INTERLOCKING ROLLER FOR THE BREAKER NOT FULLY ENGAGED. CORRECTIVE ACTIONS INCLUDE: (1) RELANDED THE DISCONNECTED WIRE AND TIGHTENED OTHER POTENTIAL TRANSFORMER CONNECTIONS; (2) REVISING THE ELECTRICAL MAINTENANCE PROCEDURE (N2-EPM-GMS-R693) TO CHECK CONNECTION INTEGRITY IN HIGH VIBRATION AREAS.
410 | 4101989009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989009R00.pdf | 1989-04-22 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | POWER LEVEL - 100%. ON APRIL 22, 1989 AT 1941 HOURS, NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED A REACTOR SCRAM AS A RESULT OF A NEUTRON MONITORING SYSTEM TRIP. SPECIFICALLY, WHEN PREPARING TO PERFORM WEEKLY TURBINE BACKUP OVERSPEED TRIP TESTING AN OPERATOR KEYED A RADIO WITHIN THE VICINITY OF THE ELECTRO HYDRAULIC CONTROL (EHC) CABINET. THIS ACTION CAUSED EHC SYSTEM DISTURBANCES RESULTING IN INADVERTENT MOVEMENTS OF THE TURBINE CONTROL AND BYPASS VALVES. THIS MALFUNCTION CREATED A PRESSURE SPIKE WHICH CAUSED ALL SIX AVERAGE POWER RANGE MONITORS (APRMS) TO EXCEED THEIR UPSCALE TRIP SETPOINT. AT THE TIME OF THE EVENT REACTOR POWER WAS AT 100% RATED THERMAL POWER. THE ROOT CAUSE FOR THIS EVENT WAS HUMAN PERFORMANCE PROBLEMS. CORRECTIVE ACTIONS TAKEN FOR THIS EVENT WERE: (1) ISSUANCE OF A TRAINING MODIFICATION REQUEST TO ENSURE APPROPRIATE PERSONNEL ARE AWARE OF POTENTIAL PROBLEMS WITH RADIO USE; (2) INSTALLATION OF PERMANENT CAUTION SIGNS AT EACH ENTRANCE TO THE RELAY ROOM; AND (3) ISSUANCE OF A MEMORANDUM FROM THE STATION SUPERINTENDENT TO ALL STATION PERSONNEL CONCERNING USE OF RADIOS/BEEPERS. IN ADDITION, OTHER AREAS OF THE STATION WHICH HAVE BEEN IDENTIFIED AS RADIO TRANSMISSION SENSITIVE HAVE BEEN POSTED.
410 | 4101989024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989024R00.pdf | 1989-09-08 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 88 | POWER LEVEL - 088%. AT 18:00:45 HOURS ON SEPTEMBER 8, 1989, WITH THE REACTOR MODE SWITCH IN 'RUN' AND THE REACTOR AT 88% RATED THERMAL POWER (930 MWE), NINE MILE POINT #2 EXPERIENCED A DOWNSHIFT OF REACTOR RECIRCULATION PUMPS TO SLOW SPEED. THIS PLACED THE UNIT ABOVE THE 100% ROD LINE WITH CORE FLOW <45% (RESTRICTED AREA OF OPERATION). THE CONTROL ROOM ANNUNCIATORS NOTIFIED THE OPERATIONS PERSONNEL OF THE DOWNSHIFT. OPERATIONS PERSONNEL IMMEDIATELY PERFORMED THE REQUIRED ACTIONS PER N2-OP-29, REACTOR RECIRCULATION SYSTEM, BY PLACING THE REACTOR MODE SWITCH TO 'SHUTDOWN', INITIATING A REACTOR SCRAM. OPERATIONS PERSONNEL PROCEEDED WITH SCRAM RECOVERY PER N2-OP-101C, PLANT SHUTDOWN. 10CFR50.72 NOTIFICATION WAS MADE ON SEPTEMBER 8, 1989, AT 2013. THE ROOT CAUSE FOR RECIRCULATION PUMP TRIP IS A FAILURE OF A 24 VOLT DC POWER SUPPLY (C33A-K613) WITHIN THE FEEDWATER CONTROL SYSTEM. CORRECTIVE ACTION WAS TO REPLACE THE FAULTY POWER SUPPLY.
410 | 4101989035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989035R00.pdf | 1989-10-13 | QL7 | Degraded condenser vacuum | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 54 | POWER LEVEL - 054%. ON OCTOBER 13, 1989, AT 0949 HOURS NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN ACTUATION OF AN ENGINEERED SAFETY FEATURE (ESF), SPECIFICALLY AN AUTOMATIC REACTOR SCRAM AS A RESULT OF A MAIN TURBINE TRIP. AT THE TIME OF THE EVENT, THE REACTOR WAS OPERATING AT 54% RATED POWER WITH THE MODE SWITCH IN 'RUN' (OPERATIONAL CONDITION 1). THE ROOT CAUSE WAS DETERMINED TO BE PERSONNEL ERROR IN THAT AN ADEQUATE EVALUATION OF PLANT IMPACT WAS NOT PERFORMED. A CONTRIBUTING CAUSE WAS FAILURE OF ADMINISTRATIVE PROCEDURES TO ADDRESS A COMPREHENSIVE PLANT IMPACT REVIEW. CONTROL ROOM OPERATORS CARRIED OUT IMMEDIATE CORRECTIVE ACTIONS. OTHER CORRECTIVE ACTIONS INCLUDE REVISION OF PLANT IMPACT EVALUATION FORM AND REPAIR OF MOTOR GENERATOR LOGIC CIRCUIT. THE RESPONSIBLE CHIEF SHIFT OPERATOR (CSO) WAS DIRECTED TO WRITE A SPECIAL REPORT CONCERNING THIS EVENT. MEETINGS WERE HELD TO STRESS THE IMPORTANCE OF PLANT IMPACT EVALUATIONS. ADMINISTRATIVE PROCEDURES WILL BE REVISED. A LESSONS LEARNED TRANSMITTAL WILL BE ISSUED.
410 | 4101989036 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989036R00.pdf | 1989-10-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 1 | POWER LEVEL - 001%. ON OCTOBER 18, 1989, AT 06:15:41 HOURS, NINE MILE POINT UNIT 2 (NMP2) EXPERIENCED AN UPSCALE TRIP OF THE INTERMEDIATE RANGE MONITORS (IRMS) RESULTING IN AN AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM (RPS) AND A FULL REACTOR SCRAM. AT THE TIME OF THE EVENT, THE REACTOR MODE SWITCH WAS IN THE START/HOT STANDBY POSITION WITH REACTOR POWER IN THE INTERMEDIATE RANGE (1%). THE ROOT CAUSE FOR THIS EVENT WAS DETERMINED TO BE INADEQUATE CONTROL OF ACTIVITIES ASSOCIATED WITH THE PLANT SHUTDOWN ON THE PART OF CONTROL ROOM PERSONNEL. A CONTRIBUTING FACTOR WAS A PROCEDURAL DEFICIENCY. CORRECTIVE ACTIONS INCLUDE (1) INSTRUCTING OPERATING SHIFT PERSONNEL ON THIS EVENT, (2) REVISING THE OPERATIONS TRAINING PROGRAM, AND (3) REVISING PLANT SHUTDOWN PROCEDURE N2-OP-101C.
410 | 4101989040 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101989040R00.pdf | 1989-12-01 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 97 | POWER LEVEL - 097%. ON 12/1/89, NINE MILE POINT UNIT 2 (NMP2) WAS OPERATING AT APPROX. 97% RATED THERMAL POWER WITH THE MODE SWITCH IN THE 'RUN' POSITION (OPERATIONAL CONDITION 1). AT 1310 HOURS, NMP2 EXPERIENCED AN AUTOMATIC REACTOR SCRAM CAUSED BY AVERAGE POWER RANGE MONITOR (APRM) HIGH NEUTRON FLUX SIGNALS ON BOTH DIVISIONS OF THE REACTOR PROTECTION SYSTEM (RPS). AT 1313 HOURS, THE TURBINE WAS TRIPPED ON REVERSE POWER BY THE MAIN GENERATOR ANTIMOTORING DEVICE. IMMEDIATE CORRECTIVE ACTIONS WERE TAKEN BY OPERATIONS TO CARRY OUT ALL SCRAM RECOVERY ACTIONS AND TO PLACE THE PLANT IN A STABLE 'HOT SHUTDOWN' MODE (OPERATIONAL CONDITION 3). OPERATIONS THEN INITIATED AN INVESTIGATION OF THE EVENT. THE IMMEDIATE CAUSE WAS A MALFUNCTION OF THE ELECTROHYDRAULIC CONTROL SYSTEM (EHC) WHICH RESULTED IN THE POWER TRANSIENT THAT CAUSED THE SCRAM. CORRECTIVE ACTION WAS TO REPLACE 3 RELAY BOARDS IN THE EHC CONTROL CIRCUIT AND CORRECT A GROUND LOOP IN THE TURBINE SPEED SENSING CIRCUIT.
410 | 4101990009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101990009R00.pdf | 1990-05-14 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Nine Mile Pt. 2 | B | GE | PO | 45 | On May 14, 1990, at approximately 2052 hours, with the reactor mode switch in the "RUN" position and the reactor operating at 100% rated thermal power, Nine Mile Point Unit 2 (NMP2) was experiencing numerous off-normal plant conditions. Operations personnel were responding to several abnormal Offgas System (OFG) indications and alarms, and Main Condenser vacuum was decreasing. At approximately 2058 hours, operators initiated reactor power reduction in response to decreasing condenser vacuum. At 2119 hours with reactor power at approximately 45% rated thermal power, the reactor mode switch was placed in the "SHUTDOWN" position, initiating a reactor scram. <br /><br /> The cause of this event was the partial loss of the Instrument Air System (IAS) due to pipe failure induced by stress-corrosion cracking. Immediate corrective actions included: performing a walkdown of the suspected branch of the IAS to locate source of air loss; generating a Work Request to replace the failed air line; and requesting a failure analysis be performed to identify cause of pipe failure.
410 | 4101990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101990013R00.pdf | 1990-09-05 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 64 | On September 5, 1990, at 0400 hours, with the Reactor Mode Switch in "RUN" and at approximately 64% rated thermal power (645 MWE), Nine Mile Point Unit 2 experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram caused by a Turbine Generator trip which was initiated by a Generator field ground. <br /><br /> The root cause investigation determined that the most probable cause of the generator field ground was leakage current through the insulating teflon tubes in the power rectifier cubicles. <br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant procedures. A Work Request was issued to investigate the Turbine Generator field ground. A plant change request to install a meter to monitor ground leakage current is being evaluated. In the interim, the resistance across the rectifier tube banks will be measured during each forced and planned outage.
410 | 4101991017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101991017R01.pdf | 1991-08-13 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | At 0548 hours on August 13, 1991, Nine Mile Point Unit 2 (NMP2) experienced a turbine trip and reactor scram when the 'B' Phase Main Transformer developed an internal fault. The transformer fault created an electrical disturbance throughout the normal electrical distribution system, resulting in the loss of five non-safety related Uninterruptible Power Supplies (UPS). As a result, the Control Room lost annunciation and most Balance of Plant (BOP) instrumentation. The conditions described in this report mandated entry into a Site Area Emergency as specified by the Site Emergency Plan. Prior to the event, NMP2 was in operational condition 1 (RUN) at 100% rated thermal power. <br /><br /> The cause of the transformer fault was a failure of the coil insulation. Due to the magnitude of the failure, the root cause could not be positively determined, however, the proximate cause was a manufacturer's defect. <br /><br /> Control Room operators verified the reactor scram, identified and re-energized the failed UPS's, identified the cause of the reactor scram, and cooled down the reactor to terminate the emergency event. Other corrective actions included: 1) replacing the 'B' phase transformer with the installed spare; 2) modifying the UPS's; 3) replacement of back-up batteries in the UPS's; 4) developing a back-up battery replacement schedule; and 5) revision of the Reactor Water Cleanup Operating Procedure.
410 | 4101991022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101991022R00.pdf | 1991-12-07 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 90 | On December 7, 1991, at 0935 hours, with the reactor mode switch in the "RUN" position (Mode 1), and the plant operating at approximately 90 percent rated thermal power (905 MWE), Nine Mile Point Unit 2 experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram occurred caused by a Turbine Generator stop valve closure, which was initiated by (most probable cause) an Electrohydraulic Control (EHC) System malfunction. <br /><br /> The root cause investigation is still underway and has not yet determined the exact cause; however, the most probable cause is a defective relay actuation.<br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant procedures. A Work Request was issued to investigate the EHC malfunction, which led to the replacement of the relay board containing the suspected faulty relay.
410 | 4101991023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101991023R00.pdf | 1991-12-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Nine Mile Pt. 2 | B | GE | PO | 55 | On December 12, 1991, at 0322 hours, with the reactor mode switch in the "RUN" position and the plant operating at approximately 55 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram on a reactor vessel low water level (Level 3) signal. Specifically, following the startup of Feedwater System pump 2FWS-P1A in support of raising plant power, a Condensate System (CNM) and Feedwater System (FWS) transient occurred, resulting in the loss of both FWS pumps. Reactor vessel water level lowered to 159.3 inches (Level 3 trip setpoint), initiating an automatic reactor scram signal. On December 12, 1991, at 1023 hours, while operators were attempting to return the Reactor Water Cleanup (WCS) System to an operable status following the scram, WCS isolated on a high differential flow signal (Engineered Safety Feature actuation).<br /><br /> The root cause for the reactor scram was determined to be poor work practices. The preliminary cause for the WCS isolation is inadequate system design.<br /><br /> Immediate actions included restoring reactor vessel inventory and commencing a controlled plant shutdown. Additional corrective actions include: 1) administering disciplinary action for individuals involved in the scram; 2) evaluating and revising Operating Procedure N2-OP-3, "Condensate and Feedwater System"; 3) troubleshooting electrical circuitry for Condensate pump 2CNM-P1C; and 4) completing the WCS isolation root cause analysis.
410 | 4101992017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101992017R00.pdf | 1992-08-22 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Nine Mile Pt. 2 | B | GE | PO | 55 | On August 22, 1992 at 0333 hours, with the reactor mode switch in the 'RUN' position and the plant operating at approximately 55 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram on a reactor vessel low water level (Level 3) signal. Specifically, while a planned shift of Feedwater System (FWS) pumps was in progress to allow maintenance activities on the FWS, a degraded condition on the Condensate System (CNM) occurred, resulting in a loss of feedwater flow to the reactor. Reactor vessel water level lowered to 159.3 inches (Level 3 trip setpoint), initiating an automatic reactor scram signal, and a Group 4 Primary Containment isolation (Residual Heat Removal sample and discharge isolation valves). <br /><br /> The root cause for the reactor scram was personnel error. <br /><br /> Immediate actions included restoring reactor vessel inventory and commencing a controlled plant shutdown. Additional corrective actions include: 1) Short term training of operators; 2) long term changes to the operator training program; 3) issuing a Lessons Learned Transmittal; 4) counseling on-shift personnel; 5) evaluating FWS operation; and 6) revising Operating Procedures.
410 | 4101992022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101992022R00.pdf | 1992-11-04 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On November 4, 1992, at 1011 hours, Nine Mile Point Unit 2 (NMP2) experienced actuation of an Engineered Safety Feature (ESF). One-quarter of the Control Rods scrammed when a Reactor Protection System (RPS) K14K relay failed, after a 'half scram' was inserted in the other RPS channel in an attempt to de-energize this failing relay. The resultant down power transient caused reactor water level to drop below the low level scram setpoint causing the full scram. The mode switch was in the 'RUN' position (Operational Condition 1), and the plant was operating at 100 percent rated thermal power. A second reactor scram signal occurred when a Safety/Relief Valve was cycled shut causing reactor water level to drop again below the low level scram setpoint.<br /><br /> The root cause of the initial scram signal was failure of an RPS relay. The cause of the second scram signal was a level transient during SRV cycling. <br /><br /> The Operators immediately took all the actions to complete the plant shutdown. Additional corrective actions included replacing the faulty relay and placing identification placards to identify the K14 relays.
410 | 4101993012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101993012R00.pdf | 1993-12-04 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | At 2018 hours on December 4, 1993, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram occurred caused by a turbine generator trip. At the time of the event, the reactor mode switch was in the "RUN" position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power.<br /><br /> The root cause of this event was equipment failure, which caused a generator runback and turbine trip. <br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant operating procedures. Follow up corrective actions included: 1) determining the cause for the turbine trip; 2) replacing the faulty flow switch; 3) checking flow switch calibration every 18 months; 4) attempting to isolate the source of the foreign material in the failed component; and 5) sampling Stator Water for filterable impurities periodically. <br /> ?
410 | 4101994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101994001R01.pdf | 1994-03-12 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On March 12, 1994 at 1923 hours, Nine Mile Point Unit 2 (NMP2) experienced several Engineered Safety Feature actuations. Specifically, an automatic reactor scram caused by turbine control valve fast closure and primary containment and reactor vessel isolations caused by low (Level 3) reactor vessel water level. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power. <br /><br /> The cause of the event was a faulty pushbutton test switch in the power/load unbalance trip circuit of the Turbine Electrohydraulic Control (EHC) system. This caused the power/load unbalance trip circuit to become energized and subsequently, the turbine control valves to fast close on a power/load unbalance trip signal initiating this event. The root cause of this event is poor equipment design. <br /><br /> Corrective actions include replacement of the faulty test switch, a review of similar switches used in similar applications and a review of all safety related control circuitry for the impact of a similar failure. Changes to the power/load unbalance and the backup overspeed test circuit designs and test frequencies will be evaluated. Additional corrective actions identified will be implemented by the completion of the next refueling outage.
410 | 4101994007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101994007R00.pdf | 1994-12-09 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Nine Mile Pt. 2 | B | GE | PO | 22 | On December 9, 1994 at 1418 hours, while Nine Mile Point Unit 2 (NMP2) was performing a normal reactor shutdown required by Technical Specifications, actuations of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System occurred. Specifically, operators initiated a manual reactor scram, from approximately 22 percent rated core thermal power, after the offgas system isolated and condenser vacuum started to decrease. After the scram, reactor vessel water level decreased to level 3, as expected, initiating a Group 4 (Residual Heat Removal) and Group 5 (Shutdown Cooling) isolation signal. Additionally, a violation of Technical Specification Surveillance Requirements occurred when the drywell and suppression chamber atmospheres were purged without first performing required sampling of the suppression chamber. At the time these events occurred, NMP2 was in an Unusual Event due to increased unidentified reactor coolant system leakage in the drywell. <br /><br /> The root cause of the Technical Specification required shutdown, due to reactor coolant system leakage, is poor managerial methods. During the drywell inspection following shutdown, valve 2CSH*HCV120 was found to have a packing leak. This valve was previously scheduled to be repacked during the third refuel outage (Fall 1993), but was removed from the outage work schedule without the risks and consequences being adequately assessed. The root cause of the Technical Specification violation has been determined to be inadequate written communications. The packing leak on valve 2CSH*HCV120 was repaired.
410 | 4101995003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101995003R00.pdf | 1995-02-14 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On February 14, 1995 at 2112 hours, Nine Mile Point Unit 2 (NMP2) experienced a momentary loss of Division I Emergency 125VDC power. This resulted in a trip of both Reactor Recirculation pumps, causing control room operators to initiate a manual reactor scram per plant operating procedures. The momentary loss of Division I Emergency 125VDC power also caused isolation of Primary Containment Isolation System groups 8 and 9 and the normal Reactor Building (Secondary Containment) ventilation system. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power.<br /><br /> The cause of this event was personnel error caused by inadequate self-verification when the operator transferring battery chargers supplying the Emergency 125VDC bus opened the wrong breaker. <br /><br /> Immediate corrective actions included restoring the DC bus, completing reactor scram immediate actions, and stabilizing the plant in a hot shutdown condition. counseling and disciplining the operator involved; 2) redefining and training operators on self-verification techniques; 3) modifying the operator training program; 4) reinforcing performance monitoring expectations with shift supervision; and 5) adding cubicle numbers to cubicle labels and revising procedural descriptions to agree with the new labels.
410 | 4101995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101995005R01.pdf | 1995-05-30 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 15 | On May 30, 1995 at 1403 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in order to break condenser vacuum, thereby quickly slowing the turbine generator which was experiencing excessive vibration during a turbine coastdown. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 15 percent of rated thermal power with a turbine generator coastdown in progress. <br /><br /> The proximate cause of the event was turbine bearing vibration beyond allowable in connection with the startup of new low pressure turbine rotors. A thorough technical evaluation performed by an outside contractor determined that the root cause of the high vibrations which led to the reactor scram was the result of the clearances established by the new low pressure turbine design. A contributing cause was the operational approach followed in startup of the new turbine.<br /><br /> Immediate operator actions included commencing scram recovery activities and placing the plant in a stable condition. Systems which could have been affected by the high turbine vibration were inspected and found acceptable. The process of bringing the turbine on-line during a subsequent plant startup was handled as a special evolution, using a Special Test Procedure with revised vibration limits and other restrictions. Additional corrective actions established as a result of the technical review performed by an outside contractor include: disseminating the design experience of this modification throughout Design Engineering, and revising the Turbine Operating Procedure (N2-OP-21) and Preventive Maintenance Procedure (N2-PM-RC@003) to include specific steps to more effectively avoid and mitigate future rubs.
410 | 4101995007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101995007R00.pdf | 1995-06-05 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 77 | On June 5, 1995 at 2253 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in anticipation of an automatic scram on high reactor pressure resulting from a generator runback caused by high temperature in the Generator Stator Cooling Water System. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 77 percent of rated thermal power. <br /><br /> The immediate cause of the high temperature in the Generator Stator Cooling Water System, which resulted in the generator runback and subsequent scram, was an inappropriate reduction in the cooling water flow to the stator cooler heat exchanger. The root cause of the flow reduction was inadequate performance and coordination of a design review which resulted in the failure to identify incorrect information used in a design change. <br /><br /> The immediate corrective actions were to perform the scram recovery actions and place the plant in a stable condition. Other corrective actions included correction of design documents, appropriate field adjustments and calibrations, revision of the design control procedure, disciplining of involved personnel, and re-emphasizing management expectations concerning interdiscipline design reviews.
410 | 4101995008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101995008R00.pdf | 1995-09-01 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 26 | On September 1, 1995 at 0504 hours, Nine Mile Point Unit 2 (NMP2) initiated a manual scram signal resulting in a full reactor scram. The manual scram was initiated in anticipation of an automatic scram resulting from an automatic turbine trip on high Turbine-Generator vibration. At the time of the scram, the reactor mode switch was in the 'RUN' position and the plant was operating at 26% of rated thermal power with a plant shutdown in progress.<br /><br /> The cause of the turbine vibration was a radial packing rub resulting from the tight clearances within the low pressure turbine.<br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. <br /><br /> In addition, the Turbine Operating Procedure N2-OP-21, Plant Shutdown Procedure N2-OP-101C, and Power Change Procedure N2-OP-101D, are being revised to provide additional guidance for turbine shutdown and power reductions in the event of high turbine vibrations.
410 | 4101999005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101999005R01.pdf | 1999-04-24 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Nine Mile Pt. 2 | B | GE | PO | 100 | On April 24, 1999, Nine Mile Point Unit 2 experienced an automatic reactor scram from 100 percent power. The cause of the reactor scram was a fast closure of the main turbine stop and control valves. Operators responding to the event were challenged by several equipment concerns including: failure of the reactor core isolation cooling system to achieve rated flow, the trip of two electrical protection assemblies, an air leak on an auxiliary boiler valve, and the need to restart numerous pieces of plant equipment due to the loss of electrical power during the residual (slow) transfer of the non-vital 13.8 kV buses.The cause of the fast closure of the turbine stop and control valves was determined to be a failure of a main generator protection volts/hertz relay.Corrective actions included: stabilizing the plant, determining and correcting the cause of the equipment failures, revising procedures, training personnel and establishing longer term corrective actions.Technical Specification 3.5.1.f requires a special report when an emergency core cooling system injects water into the reactor coolant system. During this event the high pressure core spray system injected water into the reactor vessel.
410 | 4101999010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4101999010R01.pdf | 1999-06-24 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Nine Mile Pt. 2 | B | GE | PO | 100 | On June 24, 1999, at 3 :41 p.m., Nine Mile Point Unit 2 automatically tripped from 100 percent power. The cause of the transient was a low reactor water level due to a failure of the feedwater master controller. Additionally, there was an unexpected partial loss of offsite power (Line 5) and the reactor core isolation cooling system failed to perform correctly in the automatic mode of operation. The cause of the reactor trip was failure of a manual-tracking card in the feedwater master controller due to aging. The cause of the loss of Line 5 was failure of one of the main generator output breaker individual fault relays. The primary cause of the reactor core isolation cooling system flow oscillations was air found in the flow transmitter, with a contributing cause of a miscalibrated flow controller. Corrective actions included: stabilizing the plant, replacing the feedwater manual-tracking card, replacing the main generator output breaker individual fault relay, calibrating the flow controller, and venting the reactor core isolation cooling system transmitter.
410 | 4102000002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102000002R01.pdf | 2000-03-03 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 28 | On March 3, 2000, at 1417 hours, while performing a normal plant shutdown, Nine Mile Point Unit 2 (NMP2) was manually tripped from 28 percent power. The plant was manually tripped due to a potential loss of the operating reactor feedwater pump 2FWS-P1B. The operators manually initiated the reactor core isolation cooling (RCIC) system in anticipation of losing the feedwater pump. The RCIC system automatically tripped on low suction pressure due to a partial void present in the discharge piping and the resultant water hammer.IOperators were concerned about losing the feedwater pump due to outboard seal injection low flow and high pressure indications and a steam leak. The cause of the incorrect flow and pressure indications was due to inservice wear. The cause of the steam leak was due to inadequate torquing of the discharge cover.The cause of the RCIC system failure was that the design analysis assumed that steam leakage past the inboard testable check valve would condense and maintain the discharge piping downstream of the injection valve full of water. Contrary to this design assumption, there was no minimum leakage requirement or method of ensuring this assumption was met. The RCIC system piping and snubbers were inspected, the injection valve leak was fixed, and a keep-fill modification for the RCIC discharge piping is being implemented.
410 | 4102000014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102000014R00.pdf | 2000-09-17 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 70 | On September 17, 2000, at 1520 hours, while starting up from a planned outage for Noble Metal Chemical Addition, Nine Mile Point Unit 2 experienced a turbine trip and subsequent reactor trip from approximately 70% power as a result of high vibration sensed by turbine bearing number 8 instrumentation. The cause of the high vibration was oil whip/whirl. Oil whip/whirl is the movement of the oil wedge that is present between the turbine shaft and bearing sleeve. This oil movement caused high vibration. The corrective action was to revise procedures to direct operating the turbine oil system at a higher temperature. Additional turbine instrumentation was installed to monitor turbine vibration while placing the plant back into service.
410 | 4102001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102001001R01.pdf | 2001-05-18 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 90 | On May 16, 2001, at 1019 hours, Nine Mile Point Unit 2 automatically scrammed from 90 percent core thermal power due to Turbine Stop Valve closure.This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System that resulted in a reactor scram.The cause of the reactor scram was high resistance in a normally closed contact of relay KT106. A contributing cause was inadequate preventative actions associated with GE TIL 1212-2 recommendations for relay KT106.The immediate corrective action was to replace the KT106 relay. Preventive actions are establishing a replacement frequency for the KTI 06 relay, and evaluating methods for reducing the susceptibility to reactor scrams as a result of KT106 relay failure.
410 | 4102001004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102001004R00.pdf | 2001-10-15 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On October 15, 2001 at approximately 0959, Nine Mile Point Unit 2 (NMP2) scrammed from approximately 100 percent power due to closure of the Main Steam Isolation Valves (MSIVs). Post scram the Safety Relief Valves (SRVs) were used for reactor pressure control until the MSIVs were re-opened. The scram occurred while restoring a steam flow transmitter after surveillance testing.Post scram two high reactor water level conditions occurred that resulted in level 8 conditions. The first level 8 condition caused the "A" and "B" feedwater pumps to trip, as designed. The "A" feedwater pump was later re-started. The second level 8 condition resulted in the operating "A" feedwater pump tripping, as designed. Reactor pressure was then reduced so that the condensate booster pumps could be used for inventory control. While reducing pressure, a low reactor water level condition occurred. A level 2 condition occurred that resulted in actuation of the Reactor Core Isolation Cooling (RCIC ) System and the High Pressure Core Spray (HPCS) System and closure signals to Primary Containment Isolation Valve groups 2,3,6,7,8 and 9. Reactor water level was recovered using RCIC and HPCS. Reactor pressure was reduced and the condensate booster pumps were used to provide inventory control. RCIC and HPCS were then returned to standby. Reactor pressure was reduced to approximately 150 pounds per square inch; the MSIVs were re-opened and reactor pressure control was shifted to the Turbine Bypass valves.The cause of the reactor scram was an inadequate surveillance procedure. The causes of the low reactor water level condition were training issues relative to transient operation of RCIC and selection of a less than optimum event mitigation strategy. Corrective actions include benchmarking methods of restoration of similar transmitters, reviewing activities performed at power that are classified as trip sensitive, reviewing the event with operating crews and developing training on the effect of SRV opening on reactor water level.
410 | 4102001006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102001006R01.pdf | 2001-12-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 75 | On December 2, 2001, at approximately 1449 hours, operators manually scrammed Nine Mile Point Unit 2 (NMP2) from approximately 75 percent power after the "A" Feedwater Pump tripped due to a motor failure.Prior to the Feedwater Pump motor failure a power reduction was in progress for rodline adjustments. The motor failure created a voltage transient that resulted in the loss of hydraulic power to the "A" Recirculation Flow Control Valve (FCV), which prevented its runback operation. The runback of the "B" Recirculation FCV was not sufficient to reduce power to within the capacity of the "B" Feedwater Pump. A manual scram was inserted to preclude an automatic scram because of decreasing reactor vessel water level.After the scram, none of the Emergency Core Cooling System equipment started or should have started. During the post scram recovery the "B" Feedwater pump tripped due to high reactor water level. Approximately 2.5 hours after the manual scram, a low reactor water level scram signal occurred with no rod motion, due to level shrink as operators were closing a Turbine Bypass Valve to control cooldown rate.An inspection of the motor concluded that it had experienced a phase-to-phase fault and phase-to-ground fault. This resulted in a voltage transient and the tripping of the motor breaker.The causes of the motor failure were failure to effectively implement the Corrective Action Program and a faulty motor design that led I to corona induced damage. Contributing causes include inadequate communication and insufficient motor monitoring.Corrective actions include revising the Corrective Action program, disseminating lessons learned to site management and appropriate staff, correcting the motor design flaw, rewinding pump motors and establishing a motor testing program.
410 | 4102001007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102001007R01.pdf | 2001-12-15 | QG9 | Primary System Leak | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 60 | On December 15, 2001, with Nine Mile Point Unit 2 (NMP2) at approximately 100 percent power, Nine Mile Point Nuclear Station, LLC (NMPNS) identified drywell floor drain leakage approaching the maximum limits of Technical Specification (TS) 3.4.5 for unidentified drywell leakage. Plant shutdown was commenced before reaching any of the limits of TS 3.4.5. Additionally, a strategy was developed to manually scram the reactor if leakage increased to 4 gallons per minute (gpm). With leakage continuing to rise above TS 3.4.5 limits, the applicable limiting conditions for operation (LCOs) were entered. At 2046 hours, with reactor core thermal power at approximately 60 percent, a manual reactor scram was initiated after the leak rate exceeded 4 gpm.The cause of the drywell leakage was determined to be failed packing in a gate valve in the reactor coolant (recirculation) system (RCS). The primary purpose of this valve is to isolate the RCS pump for maintenance. The immediate corrective actions included repacking the valve to stop the leakage and retorquing the remaining similar valves in the RCS to protect against leakage. Plant restart and reactor criticality occurred on December 17, 2001.The primary cause of the packing failure was that management direction was inadequate to ensure a sufficient commitment to implementation of the valve packing program. Consequently, the knowledge level of personnel implementing the program was deficient. A contributing cause was inadequate management follow-up of equipment deficiencies, in that, the need for timely repair was not identified. Opportunities to repair the valve were therefore not utilized. Corrective actions include clarifying ownership of the valve packing program, developing a site valve packing procedure, and reviewing previous valve repacking activities to identify and correct instances that are unacceptable.
410 | 4102002004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102002004R00.pdf | 2002-11-11 | QL5 | Partial Closure of MSIVs | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On November 11, 2002, at approximately 0515 hours, with Nine Mile Point Unit 2 (NMP2) at 100 percent power, an outboard main steam isolation valve (MSIV) disc separated from its stem allowing the disc/piston assembly to drop into the valve seat. This led to the rapid loss of flow in the "B" Main Steam Line resulting in a steam pressure transient. As result of increasing reactor pressure, the reactor scrammed due to a "Reactor Pressure High" trip signal. After the reactor scram, all MSIVS received closure signals and closed. The cause of the closure signals to the MSIVs was a "Main Steam Line High Flow" MSIV auto-isolation signal. The high main steam line flow was caused by the increased reactor pressure and flow being restricted to three of the four main steam lines.The reactor scram and MSIV closure are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). This report also constitutes a Part 21 Notification.The cause was a deficient MSIV design that did not ensure the proper stem-to-disc thread loading. Contributors to the failure were marginal thread dimensions and inadequate torque specifications during assembly. Five of eight MSIVs had been modified incorporating an improved design. The failed MSIV had not been modified.The corrective action was the incorporation of a modified stem-to-disc connection on the three remaining unmodified valves.
410 | 4102002006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102002006R00.pdf | 2002-12-16 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On December 16, 2002, at 1545 hours, with Nine Mile Point Unit 2 (NMP2) operating at 100 percent power, an automatic turbine generator runback was experienced as a result of high temperature in the Generator Stator Cooling Water System. As a result of increasing reactor pressure, the reactor automatically scrammed at 1548 hours due to a "High Reactor Pressure" trip signal. At the time of the scram, reactor power was approximately 71 percent of rated power.This event is reportable in accordance with 10 CFR 50 73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System that resulted in a reactor scramThe cause of the high temperature in the Generator Stator Cooling Water System was failure of a mechanical linkage connection within stator water temperature controller 2GMC-TIC101. The cause for this failure was installation of the controller in a manner that exposed it to high vibration, which, over time, caused the linkage to fail. Recognition of past industry operating experience (OE) could have prevented occurrence of the NMP2 event.The corrective actions include replacement of temperature controller 2GMC-TIC101, inspection of other pneumatic controllers, initiation of engineering activities to increase the long-term reliability of 2GMC-TIC101, and changes to the industry OE review program.
410 | 4102003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102003001R00.pdf | 2003-07-24 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On July 24, 2003, at approximately 0550 hours, Nine Mile Point Unit 2 (NMP2) experienced a power supply failure resulting in power and flow perturbations that lead to an automatic reactor scram at approximately 0557 hours. NMP2 was at approximately 100 percent power when the power supply failed, and was at approximately 45 percent power at the time of the scram. The failed power supply affected main steam flow instrumentation, feedwater level control and reactor recirculation flow control. Oscillation Power Range Monitor (OPRM) channels 1 and 4 generated the scram signal when detected power oscillations met trip criteria.The cause of the power and flow perturbations was the failure of non-safety related power supply C33-K611 (Lambda Model LRS-54-24). The power supply failed because of the age related failure of internal components and no preventive maintenance activity to refurbish or replace the power supply. Corrective actions included replacing the failed power supply, and two similar non-safety related power supplies, with auctioneer style power supplies (Lambda Model LZS-250-3), and adding power supply C33-K611 to the preventive maintenance program. Additionally, activities were initiated to replace non-safety related power supplies whose failure could result in a reactor scram, impact mission critical equipment, or cause a significant plant transient. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a critical reactor scram.
410 | 4102003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102003002R00.pdf | 2003-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On August 14, 2003 at approximately 1611 hours, Nine Mile Point Unit 2 automatically scrammed from 100% rated thermal power. The scram resulted from a turbine control valve fast closure signal that was generated as the electrohydraulic system (EHC) attempted to control turbine speed and reactor pressure in response to a severe disturbance in the electric grid. All three (Divisions 1, 2, and 3) emergency diesel generators (EDG) started as a result of the grid disturbance and each EDG powered its associated emergency bus. At 1700 hours an Unusual Event (UE) was declared because of grid instability. The UE was terminated at 0734 hours on August 15, 2003 after grid stability had been established and off-site power had been restored to all three emergency buses.After the scram, the turbine tripped as a result of high reactor vessel water level. The high water level occurred because the electrical transient had caused the feedwater flow control valves to lock up at approximately 55% open. Because the feedwater flow control valves had locked up, operators used reactor core isolation cooling (RCIC) to maintain reactor water level. Reactor pressure was initially controlled using the turbine bypass valves. The cause of the event was the severe disturbance in the electric grid.This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) because of the reactor scram while critical, and because the automatic starting of the EDGs.
410 | 4102006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102006001R00.pdf | 2006-03-09 | QL7 | Degraded condenser vacuum | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 86 | On March 9, 2006, at 22:14 hours, Nine Mile Point Unit 2 reactor automatically scrammed from approximately 86 percent power. Nine Mile Point Unit 2 was coasting down in power for the upcoming refueling outage. The scram was caused by main Turbine Trip due to low condenser vacuum. The Turbine Generator Gland Seal and Exhaust System (TME) failed resulting in a loss of condenser vacuum. A Clean Steam Reboiler, which supplies steam to the TME, isolated on high water level and the TME Emergency Main Steam Backup System (EMS) failed to supply steam as designed. The EMS failed when the mechanical linkage for the pressure indicating controller became disconnected causing the associated pressure regulating valve to fail closed, isolating main steam from the TME. The mechanical linkage became disconnected due to either not being properly reassembled during previous maintenance, or due to the pressure transient within the EMS resulting from its automatic actuation.Corrective actions to prevent recurrence have been developed, including procedure revisions to emphasize performance, of maintenance on critical components, a design change of the EMS and enhanced training for operations and engineering.
410 | 4102010001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102010001R01.pdf | 2010-01-07 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | At 0100 on January 7, 2010, Nine Mile Point Unit 2 scrammed from full power following receipt of an invalid Low-Low Reactor Pressure Vessel (RPV) level signal (Level 2). The Level 2 signal caused a Division II Redundant Reactivity Control System (RRCS) initiation signal that caused an Alternate Rod Insertion (ARI) scram initiation and a trip of the reactor recirculation pumps. The Level 2 signal also initiated Reactor Core Isolation Cooling (RCIC). The invalid RPV Level 2 signal was caused by maintenance technicians performing fill and vent activities on Residual Heat Removal (RHS) instrumentation as part of a planned maintenance window for Division II RHS. The direct cause of this event was venting of RHS instrumentation during planned maintenance. The root cause of this event is, Operations Management has not sufficiently monitored and reinforced standards associated with plant impact assessment during work planning. To address this issue, additional training will be provided to personnel performing the Operations planning functions. In addition, quarterly Management Review Meetings will be implemented for Operations planning personnel to provide continual reinforcement of the standards and provide for monitoring and feedback. The operating procedure involved in this event will be revised to provide precautions and limitations when venting.
410 | 4102011003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102011003R00.pdf | 2011-08-11 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 15 | On August 10, 2011 at 2200, during power ascension from an outage with the reactor operating at approximately 15% of rated thermal power, a leak was identified on a vent pipe connected to the minimum flow line for the "A" feedwater pump. At 0016 on August 11, the reactor was manually shut down due to the unisolatable leak on the feedwater pump minimum flow line.The leak was the result of a failed weld on the feedwater minimum flow line vent pipe due to vibration induced fatigue failure. The vibration increased due to two recent design modifications that affected the "A" feedwater pump minimum flow line. The potential for these design changes to increase vibration and adversely impact system operation had been identified, but was not anticipated to result in a failure of this type. Although the minimum flow piping had been evaluated and was being monitored, the small bore vent line had not been equally modeled or evaluated.The vent pipe was rewelded to the minimum flow line using an improved 2:1 weld profile and a pipe-to-pipe support was installed to make the pipe more robust and less susceptible to vibration.
410 | 4102012004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102012004R00.pdf | 2012-07-12 | QL7 | Degraded condenser vacuum | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 85 | On July 12, 2012, at 02:20, Nine Mile Point Unit 2 was manually scrammed from approximately 85 percent of rated power due to indications of rising offgas system inlet pressure and lowering main condenser vacuum. These conditions occurred due to a loss of the in-service 'B' clean steam reboiler and a low backup sealing steam supply initiation setpoint that resulted in an inadequate sealing steam supply pressure. The reboiler tripped on a low water level condition due to excess steam demand caused by an incorrectly installed gag on relief valve 2TME-RV135. The relief valve gag implementation plan did not contain an adequate level of detail for installation and testing.This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the reactor protection system.The root cause of this event is attributed to inadequate management guidance to ensure that changes in scope during engineering change package development are adequately reviewed and assessed.Corrective actions include adjusting the gag installed on relief valve 2TME-RV135, changing the initiation setpoint for the backup sealing steam supply, revising the turbine gland sealing system operating procedure, and revising the engineering change management procedure.
410 | 4102013004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102013004R00.pdf | 2013-12-02 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 25 | On December 2, 2013, at 0903, Nine Mile Point Unit 2 (NMP2) was lowering reactor power level to remove the main turbine from service to support maintenance. During the power reduction, the Low Frequency Motor Generators (LFMGs) did not start automatically. Attempts to manually start the recirculation system pumps in slow speed were unsuccessful and a manual reactor scram was inserted due to the sudden reduction in core flow. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The Reactor Protection System is listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The root cause of this event is a failure to identify that the switches in the auto transfer circuits for the reactor recirculation pumps to shift from high speed to low speed are single point vulnerable (SPV) components because they were exempted from the AP-913 classification process. Since the switches were not classified as SPV components, no mitigation strategies were developed. <br /><br /> Corrective actions include revision of the operating procedures to manually start the LFMG sets and not rely on the auto transfer circuitry. <br /><br /> There are no similar Licensee Event Reports for NMP2.
410 | 4102014003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102014003R00.pdf | 2014-03-04 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On March 4, 2014, at approximately 0143, Nine Mile Point Unit 2 (NMP2) was manually scrammed because of rising reactor recirculation pump (RRP) seal and motor temperatures. Prior to the scram, a failure of the Uninterruptible Power Supply, 2VBB-UPS3B, to provide uninterruptible power occurred. The malfunction of the Uninterruptible Power Supply (UPS) resulted in the inboard Primary Containment cooling water isolation valves closing and a Reactor Protection System (RPS) half scram. The closing of the inboard isolation valves resulted in the loss of cooling flow to the RRP seals and motors. The cause of the UPS malfunction was a degraded subcomponent associated with the UPS. The causal analysis for this event identified that it resulted from inadequate vendor and industry guidance/operating experience associated with the maintenance of a UPS related subcomponent. Corrective actions planned or taken include replacing degraded UPS subcomponents, revising preventative maintenance strategy, and working with the vendor to identify a list of single point of vulnerability (SPV) components that can prohibit the UPS from transferring to its alternate source when needed. The reportable condition described in this LER is documented in the plant's corrective action program as CR-2014-001725.
410 | 4102014004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102014004R00.pdf | 2014-03-10 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 99 | On Monday March 10, 2014 at 1628 hours, Nine Mile Point Unit 2 (NMP2) experienced an actuation of the Alternate Rod Insertion (ARI) system which resulted in an automatic reactor scram from 99.2% thermal power. An inadvertent Reactor Water Low-Low Level 2 signal from transmitters 2ISC*LT8A and 2ISC*LT8B initiated the Division I ARI which resulted in a Reactor Recirculation Pump trip and a full reactor scram. The event was caused by instrument perturbation while Maintenance I&C technicians were performing minor maintenance associated with changing labels on instrument drain valves in the vicinity of trip sensitive equipment. Safety related and other important equipment functioned properly during and after the scram. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A). The causal analysis identified that station personnel have not adequately internalized the risk and implemented rigorous process and behavioral barriers to mitigate the vulnerabilities associated with work on or near trip sensitive equipment. Corrective actions taken or planned include: 1) Protect the trip sensitive equipment and 2) Implementing new fleet procedures/processes for work around trip sensitive equipment. A similar event was documented in NMP2 LER 2010-001.
410 | 4102015002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102015002R00.pdf | 2015-02-18 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On February 18, 2015, at 1406, Nine Mile Point Unit 2 inserted a manual reactor scram due to rapidly rising reactor water level. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The Reactor Protection System (RPS) was manually actuated, resulting in a reactor scram. The rapidly increasing reactor water level was due to the lifting and separating of two leads on a level recorder being replaced. The root cause of the event was the technical human performance verification tools were not adequately used during the Fix-It-Now (FIN) planning process to validate plant impact since there was a bias towards a level recorder replacement not impacting the control circuit. Corrective actions taken include replacing the failed level recorder and establishing a compensatory action to require FIN Team work packages staged by the FIN team to be peer reviewed by a same-discipline technician.<br /><br /> The event described in this LER is documented in the plant's corrective action program as IR2454892. NMP2 LER 2014-004 reported a similar event.
410 | 4102017001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102017001R00.pdf | 2017-08-05 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 84 | On August 5, 2017, at approximately 2235, the Nine Mile Point Unit 2 (NMP2) reactor scrammed on an automatic scram signal during performance of quarterly turbine stop valve surveillance testing. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.73(a)(2)(iv)(A). The definitive root cause of the equipment failure was not located but was bound to spurious actuation of load limit relays KL186 and KL187. The spurious action was caused by an intermittent ground and/or an induced voltage within the load limit circuit. This is a result of the non-fault tolerant original design of the Electro-hydraulic Control (EHC) system. The corrective action planned is replacement of the current single point vulnerable NMP2 Turbine EHC system with a fault tolerant Digital EHC system. Interim actions have also been developed to mitigate risk associated with testing of the current system until replacement can be accomplished during the 2018 refueling outage.
410 | 4102018002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4102018002R00.pdf | 2018-08-27 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | At 0033 on August 27, 2018, Nine Mile Unit 2 (NMP2) experienced an automatic reactor scram on turbine control valve fast closure due to a turbine trip. All control rods inserted. There were no safety system actuations. In response to the turbine trip and reactor scram all systems responded per design. The station responded in accordance with appropriate procedures and restored impacted systems. The condition was reported in Event Notification #53565 as an event or condition that results in a valid RPS actuation (scram) pursuant to 10CFR.50.72(b)(2)(iv)(B). This event is being reported as an event or condition that results in a valid RPS actuation pursuant to 10CFR50.73(a)(2)(iv)(A). <br /><br /> The direct cause of this event is an actuation of the 'A' phase Unit Differential Relay, 87-2SPUY02(1) due to a grid disturbance on the 'A' phase of the 2-15 Clay - Edic transmission line. The root cause of the event is a failure of Relay & Control technicians to hold themselves accountable for use of the HU tools in preventing errors while removing grounding screws from the Unit Differential Relaying Circuitry. Corrective actions included: removal of the identified shorting screws and qualifications for those involved with the event.
412 | 4121987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987012R00.pdf | 1987-08-07 | QR3 | Reactivity Control Imbalance | [45 empty] | Beaver Valley 2 | P | WE | SU | 2 | POWER LEVEL - 002%. ON 8/7/87, DURING LOW POWER PHYSICS TESTING, FOUR (4) CONTROL RODS FELL INTO THE CORE. THE OPERATORS, AS PER THE PROCEDURE FOR A DROPPED ROD, MANUALLY TRIPPED THE REACTOR AND STABILIZED THE PLANT. AN INVESTIGATION BASED ON UNIT 1 EXPERIENCE AND SOME TROUBLESHOOTING IDENTIFIED A FAULT IN THE MOVABLE FIRING CIRCUIT CARD IN THE 2BD POWER CABINET AS THE CAUSE OF THE FAILURE. THIS CARD WAS REPLACED. RODS WERE WITHDRAWN TO CONTINUE LOW POWER PHYSICS TESTING. ON 8/10/87 THE SAME FOUR (4) RODS AGAIN FELL INTO THE CORE. AGAIN, THE OPERATOR MANUALLY TRIPPED THE REACTOR. FURTHER INVESTIGATION DISCOVERED A FAILED THYRISTOR IN THE 'B' MOVABLE GRIPPER CIRCUIT CARD (WESTINGHOUSE MODEL #6050D12G01) IN THE 2BD POWER CABINET. THIS FAILED THYRISTOR WAS IDENTIFIED TO BE THE CAUSE OF BOTH EVENTS. THERE WERE NO SAFETY IMPLICATIONS DUE TO THESE EVENTS. TRIPPING THE REACTOR WAS A CONSERVATIVE ACTION FOR THESE EVENTS, AS THE PLANT'S SAFETY ANALYSIS ALLOWS SUCH ROD MISALIGNMENT AT LOW POWER LEVELS.
412 | 4121987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987012R00.pdf | 1987-08-10 | QR3 | Reactivity Control Imbalance | [45 empty] | Beaver Valley 2 | P | WE | SU | 1 | POWER LEVEL - 002%. ON 8/7/87, DURING LOW POWER PHYSICS TESTING, FOUR (4) CONTROL RODS FELL INTO THE CORE. THE OPERATORS, AS PER THE PROCEDURE FOR A DROPPED ROD, MANUALLY TRIPPED THE REACTOR AND STABILIZED THE PLANT. AN INVESTIGATION BASED ON UNIT 1 EXPERIENCE AND SOME TROUBLESHOOTING IDENTIFIED A FAULT IN THE MOVABLE FIRING CIRCUIT CARD IN THE 2BD POWER CABINET AS THE CAUSE OF THE FAILURE. THIS CARD WAS REPLACED. RODS WERE WITHDRAWN TO CONTINUE LOW POWER PHYSICS TESTING. ON 8/10/87 THE SAME FOUR (4) RODS AGAIN FELL INTO THE CORE. AGAIN, THE OPERATOR MANUALLY TRIPPED THE REACTOR. FURTHER INVESTIGATION DISCOVERED A FAILED THYRISTOR IN THE 'B' MOVABLE GRIPPER CIRCUIT CARD (WESTINGHOUSE MODEL #6050D12G01) IN THE 2BD POWER CABINET. THIS FAILED THYRISTOR WAS IDENTIFIED TO BE THE CAUSE OF BOTH EVENTS. THERE WERE NO SAFETY IMPLICATIONS DUE TO THESE EVENTS. TRIPPING THE REACTOR WAS A CONSERVATIVE ACTION FOR THESE EVENTS, AS THE PLANT'S SAFETY ANALYSIS ALLOWS SUCH ROD MISALIGNMENT AT LOW POWER LEVELS.
412 | 4121987015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987015R00.pdf | 1987-08-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Beaver Valley 2 | P | WE | PO | 20 | POWER LEVEL - 020%. ON 8/15/87, REACTOR POWER LEVEL WAS BEING INCREASED TO SUPPORT NUCLEAR INSTRUMENTATION CALIBRATION. AS POWER APPROACHED 20%, THE LEVELS OF ALL THREE (3) STEAM GENERATORS BEGAN TO DECREASE RAPIDLY. OPERATORS INCREASED FEED FLOW AND ISOLATED STEAM GENERATOR BLOWDOWN, BUT WERE UNABLE TO PREVENT LEVEL FROM DROPPING TO THE LO-LO STEAM GENERATOR LEVEL SETPOINT. THIS INITIATED AN AUTOMATIC REACTOR TRIP, AS PER DESIGN. THE OPERATORS STABILIZED THE PLANT USING THE REACTOR TRIP RESPONSE PROCEDURE. POST-TRIP EVALUATION DETERMINED THE EVENT HAD OCCURRED DUE TO OPERATOR ERROR, RESULTING FROM INITIAL CORE PARAMETER RESPONSES. DURING THE POWER INCREASE, OPERATORS HAD BEEN WITHDRAWING RODS AS REQUIRED. HOWEVER, DUE TO HIGH ROD WORTHS AND A NEAR ZERO MODERATOR TEMPERATURE COEFFICIENT, THIS RESULTED IN A GREATER THAN EXPECTED RCS HEATUP, WHICH CAUSED THE STEAM GENERATOR LEVELS TO SWELL. CORRECTIVE ACTION THROUGH ROD INSERTION AND FEEDWATER ADDITION RESULTED IN A COOLDOWN AND STEAM GENERATOR SHRINK. THE SHRINK RESULTED IN A LO-LO STEAM GENERATOR REACTOR TRIP. OPERATIONS HAS BEEN PROVIDED WITH ADMINISTRATIVE GUIDANCE CONCERNING PROPER OPERATING TECHNIQUES UNDER THESE CONDITIONS. THESE CONDITIONS ARE THE RESULT OF THE INITIAL CORE, AND WILL IMPROVE WITH CORE AGE. THERE WERE NO SAFETY IMPLICATIONS DUE TO THIS EVENT AS ALL ESF SYSTEMS/COMPONENTS FUNCTIONED AS DESIGNED.
412 | 4121987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987018R01.pdf | 1987-08-18 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Beaver Valley 2 | P | WE | PO | 20 | POWER LEVEL - 020%. ON 8/18/87, MAINTENANCE INSTRUMENT TECHNICIANS WERE REPLACING THE #1 POWER SUPPLY OVERVOLTAGE LIMITER IN THE ROD CONTROL SYSTEM 1AC POWER CABINET. (THE POWER CABINETS USE TWO POWER SUPPLIES IN AN AUCTIONEERED ARRANGEMENT, ALLOWING EITHER, BUT NOT BOTH, OF THE SUPPLIES TO BE REMOVED FROM SERVICE FOR MAINTENANCE WITHOUT AFFECTING THE OPERATION OF THE POWER CABINET.) WHILE MOUNTING THE OVERVOLTAGE PROTECTOR MODULE IN THE CABINET, THE MODULE WAS INADVERTENTLY ALLOWED TO COME IN CONTACT WITH THE ADJACENT TERMINAL BOARD. THIS SHORTED OUT THE #2 POWER SUPPLY FOR THE 1AC POWER CABINET. WITH THE #1 POWER SUPPLY ALREADY REMOVED FOR MAINTENANCE, THIS RESULTED IN DE-ENERGIZING THE 1AC POWER CABINET, CAUSING THE GROUP 1 'A' SHUTDOWN BANK AND THE GROUP 1 'A' AND 'C' CONTROL BANKS OF RODS TO FALL INTO THE CORE. THIS, IN TURN CAUSED A NEGATIVE RATE REACTOR TRIP. TRIP RESPONSE PROCEDURE. BOTH POWER SUPPLIES WERE REPAIRED AND RETURNED TO SERVICE. ALL MAINTENANCE INSTRUMENT TECHNICIANS ARE RECEIVING TRAINING ON THIS EVENT AND THE NECESSITY FOR MORE IN-DEPTH JOB PREPLANNING AND ATTENTION TO DETAIL. THERE WERE NO SAFETY IMPLICATIONS DUE TO THIS EVENT AS ALL ESF/RPS EQUIPMENT FUNCTIONED AS PER DESIGN.
412 | 4121987019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987019R00.pdf | 1987-08-25 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 30 | POWER LEVEL - 030%. ON 8/25/87, WITH THE UNIT IN POWER OPERATION AT 30% REACTOR POWER, TROUBLESHOOTING OF THE TURBINE ELECTRONIC OVERSPEED TRANSDUCER WAS IN PROGRESS. FEEDWATER FLOW TRANSMITTER 2FWS*FT496 WAS OUT-OF-SERVICE (ASSOCIATED BISTABLES WERE IN THE TRIPPED CONDITION). AT 1357 HOURS, A SPURIOUS TURBINE OVERSPEED SIGNAL CAUSED A TURBINE TRIP. A REACTOR TRIP DID NOT IMMEDIATELY OCCUR BECAUSE REACTOR POWER WAS BELOW THE TURBINE TRIP REACTOR TRIP (P-9) SETPOINT. THE STEAM GENERATOR (SG) LEVELS ALL SHRANK BELOW THE LOW LEVEL TRIP SETPOINT. FOLLOWING THE TURBINE TRIP, THE REACTOR TRIPPED ON 21C SG LOW LEVEL COINCIDENT WITH A STEAM FLOW/FEED FLOW MISMATCH SINCE THE 2FWS*FT496 BISTABLES WERE ALREADY TRIPPED. THE OPERATORS INITIATED EMERGENCY OPERATING PROCEDURE E-O TO STABLIIZE THE PLANT. DURING THE 4KV AUTO BUS TRANSFER, THE REACTOR COOLANT PUMPS (RCP) TRIPPED ON A 2/3 RCP BUS UNDERFREQUENCY SIGNAL. THE PLANT WAS STABILIZED ON NATURAL CIRCULATION. THE RCPS WERE RESTARTED AT 1447 HOURS. THE CAUSE FOR THIS EVENT WAS A SPURIOUS TURBINE OVERSPEED SIGNAL. THE RCP TRIPS WERE DUE TO MALFUNCTIONING RELAYS. THE TURBINE OVERSPEED TRANSDUCER WAS REPLACED WITH AN INSTALLED SPARE AND THE UNDERFREQUENCY RELAYS WERE REPLACED WITH A DIFFERENT STYLE RELAY. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC.
412 | 4121987020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987020R01.pdf | 1987-09-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [30 empty] | X |  |  |  | Beaver Valley 2 | P | WE | PO | 30 | POWER LEVEL - 030%. ON 9/9/87, WITH THE UNIT AT 30% REACTOR POWER, THE MAIN STEAM ISOLATION VALVES (MSIVS; 2MSS*A0V101A, B, C) WERE CLOSED BY INITIATING A STEAM LINE ISOLATION IN ACCORDANCE WITH THE PROVISIONS OF A STARTUP PROGRAM TEST. THIS TEST METHOD RENDERED THE CONDENSER UNAVAILABLE. THEREFORE, THE LEVEL IN ALL THREE STEAM GENERATORS (2RCS*SG21A, B, C) SHRUNK AS A RESULT OF THE RAPID SECONDARY SIDE PRESSURE RISE INDUCED BY THE SUDDEN MSIV CLOSURE. A REACTOR TRIP OCCURRED AT 0131 HOURS ON 9/9/87 DUE TO SG21A LOW-LOW LEVEL. THE REACTOR PROTECTION SYSTEM AND ENGINEERED SAFETY FEATURES (AUXILIARY FEEDWATER PUMPS) OPERATED PROPERLY, WHILE THE ATMOSPHERIC STEAM DUMPS (2SVS*PCV101A, B, C) OPENED TO REMOVE HEAT. THEREFORE, THE CONSEQUENCES OF THE ACCIDENT WERE MITIGATED IN ACCORDANCE WITH THE ANALYSIS PROVIDED IN SECTIONS 15.2.3 AND 15.2.5 OF THE UNIT II FINAL SAFETY ANALYSIS REPORT, AND NO SAFETY IMPLICATIONS RESULTED FROM THE EVENT. THE OPERATORS FOLLOWED THE UNIT EMERGENCY PROCEDURE FOR A REACTOR TRIP AND STABILIZED THE PLANT IN HOT STANDBY. THE NRC WAS NOTIFIED AT 0230 HOURS, WITHIN THE FOUR HOUR PROVISION OF 10 CFR 50.72.B.2.II. THE REACTOR WAS TAKEN CRITICAL AT 0855 HOURS ON 9/9/87. SINCE THE MSIV CLOSURE TEST WAS A UNIQUE TEST REQUIRED AS PART OF THE STARTUP PROGRAM, A SIMILAR TRIP SHOULD NOT OCCUR IN THE FUTURE.
412 | 4121987023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987023R00.pdf | 1987-09-28 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 73 | POWER LEVEL - 073%. ON 9/28/87, UNIT 2 WAS OPERATING AT 73% POWER WITH ONLY ONE MAIN FEEDWATER PUMP (MFP) RUNNING, AS REQUIRED BY A STARTUP PROGRAM TEST. THE 'B' AND 'C' MAIN FEEDWATER REGULATING VALVES (MFRVS) WERE IN MANUAL CONTROL DUE TO ERRATIC AUTOMATIC OPERATION. UPON TEST COMPLETION, THE SECOND MFP WAS STARTED AND PLANT CONDITIONS WERE STABILIZED. THE 'B' MFRV WAS THEN PLACED IN AUTOMATIC TO DETERMINE IF IT WOULD NOW CONTROL PROPERLY. IMMEDIATELY UPON TRANSFER TO AUTOMATIC, THE 'B' MFRV FAILED OPEN. IT WAS RETURNED TO MANUAL CONTROL, AND SHUT, WHICH RESULTED IN INCREASED FLOW IN THE OTHER FEEDWATER LINES. THE 'A' MFRV (IN AUTOMATIC) STARTED SHUTTING IN RESPONSE TO THE INCREASED FLOW, WHICH RESULTED IN A RAPID FLOW DECREASE AND IN A STEAM FLOW/FEED FLOW MISMATCH BISTABLE ACTUATION. SINCE A LEVEL CHANNEL FOR THE 'A' STEAM GENERATOR (SG) HAD PREVIOUSLY BEEN DECLARED INOPERABLE AND HAD ITS BISTABLE TRIPPED, THE MISMATCH RESULTED IN A 1/2 STEAMFLOW/FEEDFLOW MISMATCH COINCIDENT WITH A 1/2 LOW SG LEVEL REACTOR TRIP AT 0156 HOURS. THE PLANT WAS QUICKLY STABILIZED IN ACCORDANCE WITH EMERGENCY PROCEDURES. THERE WERE NO SAFETY IMPLICATIONS BECAUSE ALL TRIP AND SAFETY FEATURES ACTUATED AS REQUIRED TO MITIGATE THE ACCIDENT. THE CAUSE OF THE 'B' MFRV FAILURE WAS A FAULTY CONTROLLER CARD IN THE AUTOMATIC CIRCUIT, WHICH WAS REPLACED. THE REACTOR WAS TAKEN CRITICAL AT 1047 HOURS ON 9/28/87.
412 | 4121987024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987024R00.pdf | 1987-09-29 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Beaver Valley 2 | P | WE | PO | 15 | POWER LEVEL - 015%. ON 9/29/87 AT APPROXIMATELY 0200 HOURS, WITH THE UNIT IN POWER OPERATION, A TURBINE STARTUP WAS IN PROGRESS IN ACCORDANCE WITH OPERATING MANUAL 2.52.4A. THE OPERATORS WERE PERFORMING THE OVERSPEED PROTECTION CONTROLLER (OPC) TRIP CHECK. THE OPC SWITCH WAS PLACED IN THE TEST POSITION CAUSING GOVERNOR AND INTERCEPTOR VALVE CLOSURE. THE OPC SWITCH WAS THEN PLACED IN THE IN-SERVICE POSITION. SINCE THE PROCEDURE DID NOT ADDRESS THE VALVE POSITION LIMITER IT WAS STILL IN THE 100% POSITION. THE GOVERNOR AND INTERCEPTOR VALVES IMMEDIATELY OPENED, CAUSING A SAFETY INJECTION AT 0219 HOURS, ON THE RATE SENSITIVE LOW STEAMLINE PRESSURE SIGNAL. A RESULTANT REACTOR TRIP IMMEDIATELY FOLLOWED. THE OPERATORS UTILIZED THE EMERGENCY OPERATING PROCEDURES TO STABILIZE THE PLANT IN HOT STANDBY. AS A RESULT OF THE SAFETY INJECTION, APPROXIMATELY 3500 GALLONS OF BORATED WATER WERE INJECTED INTO THE REACTOR COOLANT SYSTEM. THE CAUSE FOR THIS EVENT WAS A DEFICIENT PROCEDURE. THE PROCEDURE WAS RECENTLY REVISED AND DID NOT INCLUDE INSTRUCTIONS REGARDING THE VALVE POSITION LIMITER. INSTRUCTIONS REGARDING THE VALVE POSITION LIMITER. AS A RESULT OF THIS EVENT.
412 | 4121987026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987026R00.pdf | 1987-10-08 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Beaver Valley 2 | P | WE | PO | 55 | POWER LEVEL - 055%. ON 10/8/87, WITH THE UNIT AT 55% REACTOR POWER, THE 'A' MAIN FEED PUMP WAS REMOVED FROM SERVICE TO PERMIT TESTING GROUP TO OBTAIN SINGLE PUMP OPERATION DATA ON THE 'B' MAIN FEED PUMP. APPROXIMATELY 5 SECONDS LATER, STEAM GENERATOR (SG) FEED PUMP RECIRCULATION VALVE (2FWR-FCV150B) OPENED FOLLOWED BY THE SG FEED PUMP RECIRCULATION VALVE (2FWR-FCV150A). THE 'A' MAIN FEED PUMP WAS RESTARTED AND SUBSEQUENTLY BOTH SG RECIRCULATION VALVES CLOSED. SG 'A' AND 'C' MAIN FEED REGULATING VALVES BEGAN TO OSCILLATE. SINCE THE NARROW RANGE SG 'A' WATER LEVEL CHANNEL (2FWS-L475) HAD BEEN DECLARED OUT OF SERVICE AND ITS BISTABLES TRIPPED, THE FEED FLOW SWING ON THE 'A' SG RESULTED IN A FEED FLOW/STEAM FLOW MISMATCH WITH SG 'A' LOW LEVEL REACTOR TRIP. MAINTENANCE DISCOVERED THE PIPING TO THE 'B' MAIN FEED PUMP SUCTION FLOW INDICATING SWITCHES WAS REVERSED. THIS CAUSED BOTH MAIN FEED PUMPS RECIRCULATION VALVES TO OPEN WHEN THE 'A' MAIN FEED PUMP WAS SECURED. THE MAIN FEED REGULATION VALVES OVER RESPONDED CAUSING THEM TO SWING FULL RANGE. THE PIPING ERROR WAS CORRECTED AND THE GAIN ON THE MAIN FEED REG. VALVES ADJUSTED. THERE WERE NO SAFETY IMPLICATIONS. THE REACTOR TRIPPED AS DESIGNED AND THE AUXILIARY FEED PUMPS STARTED.
412 | 4121987028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987028R00.pdf | 1987-10-14 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 99 | POWER LEVEL - 099%. AT APPROXIMATELY 1000 HOURS ON 10/14/87, AN OPERATOR IN THE UNIT 2 CONTROL ROOM RECEIVED AN ALARM INDICATING A LOSS OF TURBINE ELECTROHYDRAULIC (EH) FLUID PRESSURE. A NON-LICENSED NUCLEAR OPERATOR (NO) WAS DIRECTED TO OPEN THE MANUAL ISOLATION VALVES FOR THE EH FLUID PRESSURE SWITCHES IN ORDER TO RESTORE PRESSURE. THESE SWITCHES HAD BEEN ISOLATED PREVIOUSLY DUE TO ERRATIC OPERATION THAT HAD LED TO A TURBINE TRIP. BEFORE THE SUO COULD REACH THE VALVES, HOWEVER, THE TURBINE TRIPPED ON A LOW EH FLUID PRESSURE SIGNAL. SINCE REACTOR POWER WAS 99%, WHICH IS GREATER THAN THE TURBINE TRIP INTERLOCK SETPOINT (P-9) OF 49%, THE TURBINE TRIP RESULTED IN A REACTOR TRIP AT 1010 HOURS. OPERATORS FOLLOWED EMERGENCY PROCEDURES TO STABILIZE THE PLANT BY 1025 HOURS. NO SAFETY IMPLICATIONS RESULTED BECAUSE THE REACTOR PROTECTION SYSTEM AND ALL APPROPRIATE ENGINEERED SAFETY FEATURES OPERATED PROPERLY TO MITIGATE THE CONSEQUENCES OF THE TRANSIENT. THE CAUSE OF THE EVENT WAS DETERMINED TO BE LEAKAGE PAST THE EH PRESSURE SWITCH ISOLATION VALVES. TO CORRECT THE PROBLEM, THE VALVES WERE OPENED AND THE EH LOW PRESSURE CIRCUITS BYPASSED. THE REACTOR WAS TAKEN CRITICAL AT 2115 HOURS, 10/14/87. WESTINGHOUSE WILL MODIFY THE CIRCUITS DURING THE FIRST REFUELING OUTAGE.
412 | 4121987029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987029R00.pdf | 1987-10-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 65 | POWER LEVEL - 065%. ON 10/15/87 AT APPROXIMATELY 1514 HOURS, WITH THE UNIT AT 65% REACTOR POWER, ERRATIC OPERATION OF ALL THREE MAIN FEEDWATER REGULATING VALVES (MFRV) WAS EXPERIENCED. THE OPERATORS TOOK MANUAL CONTROL OF THE 'A' AND 'B' MFRVS TO ATTEMPT TO RESTORE CONTROL. LEVEL STABILITY COULD NOT BE ACHIEVED BECAUSE ADJUSTMENT OF ONE MFRV CAUSED ADVERSE RESPONSES ON THE OTHER FEEDWATER LINES. AT 1515 HOURS, THE LEVEL IN THE 21A STEAM GENERATOR INCREASED TO 75%, CAUSING A TURBINE TRIP. SINCE REACTOR POWER WAS ABOVE THE P-9 PROTECTION INTERLOCK (49%), THE TURBINE TRIP INITIATED A REACTOR TRIP. THE OPERATORS STABLIIZED THE PLANT IN HOT SHUTDOWN UTILIZING THE EMERGENCY OPERATING PROCEDURES. THE CAUSE FOR THIS EVENT WAS THE OVER-RESPONSIVENESS OF THE MFRVS TO SMALL LEVEL CHANGES IN THE STEAM GENERATORS. INSTRUMENT AND CONTROL PERSONNEL WERE CALLED IN TO ADJUST THE ELECTRONIC GAINS WITHIN THE MFRV CONTROLLERS. AS A PERMANENT CORRECTIVE ACTION, THE RESPONSE TIMES OF THE MFRVS WILL BE ADJUSTED TO ALLOW STABLE LEVEL CONTROL OF THE STEAM GENERATORS. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS EVENT. THIS EVENT HAS BEEN PREVIOUSLY ANALYZED IN FSAR SECTION 15.1.2, 'FEEDWATER SYSTEM MALFUNCTIONS CAUSING AN INCREASE IN FEEDWATER FLOW'. THIS EVENT IS BEING REPORTED IN ACCORDANCE WITH 10 CFR 50.73.A.2.IV AS AN EVENT INVOLVING AN AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
412 | 4121987030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987030R01.pdf | 1987-10-16 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Beaver Valley 2 | P | WE | PO | 97 | POWER LEVEL - 097%. ON 10/16/87 AT 2215 HOURS, MECHANICS NOTIFIED THE CONTROL ROOM THAT SMOKE WAS ISSUING FROM THE HIGH PRESSURE TURBINE ENCLOSURE. OPERATORS DISPATCHED THE EMERGENCY SQUAD TO INVESTIGATE. AT 2217 HOURS, THE EMERGENCY SQUAD CONFIRMED A FIRE IN THE VICINITY OF THE #2 TURBINE BEARING. OPERATORS IMMEDIATELY TRIPPED THE REACTOR AND TURBINE WHILE THE EMERGENCY SQUAD INITIATED FIRE SUPPRESSION ACTIONS. THE FIRE WAS EXTINGUISHED BY 2223 HOURS. INVESTIGATION DETERMINED THAT THE FIRE RESULTED FROM OIL SOAKED INSULATION ON THE TURBINE #2 GLAND PACKING. ADMINISTRATIVE CONTROLS WERE INITIATED TO PREVENT OIL LEAKAGE DURING OPERATION. DURING THE UNIT'S FIRST REFUELING OUTAGE, THE #2 BEARING SEAL WAS REPLACED AND AN OIL DEFLECTOR WAS INSTALLED INTERNAL TO THE #2 BEARING OIL SEAL. THIS PREVENTS OIL SPRAY FROM THE #2 BEARING FROM REACHING THE BEARING OIL SEAL. NO SEAL LEAKAGE HAS BEEN DETECTED SINCE THIS ACTION WAS COMPLETED. EVENT. THE FIRE CAUSED NO PERSONNEL INJURY OR DAMAGE TO SAFETY RELATED EQUIPMENT.
412 | 4121987032 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987032R01.pdf | 1987-10-24 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | POWER LEVEL - 000%. ON 10/24/87, THE 100% LOAD REJECTION TEST (IST 2.04.06) WAS PERFORMED. THE OPERATORS, AS PER PROCEDURE, MANUALLY OPENED THE MAIN OUTPUT BREAKERS TO INITIATE A LOSS OF LOAD TRANSIENT. CONDENSER STEAM DUMPS AUTOMATICALLY OPENED IN RESPONSE TO THE LOSS OF LOAD. THE RESULTANT STEAM FLOW TRANSIENT CAUSED ALL THREE STEAM GENERATOR LEVELS TO DROP RAPIDLY. A REACTOR TRIP OCCURRED ON LO-LO STEAM GENERATOR LEVEL. ALL AUXILIARY FEED PUMPS AUTO-STARTED TO RECOVER STEAM GENERATOR LEVELS. DUE TO TURBINE SPEED FLUCTUATIONS, ALL THREE REACTOR COOLANT PUMPS (RCPS) TRIPPED ON UNDERFREQUENCY. THIRTY SECONDS AFTER THE REACTOR TRIP, STATION LOADS WERE (AS DESIGNED) AUTOMATICALLY TRANSFERRED FROM ON-SITE TO OFF-SITE POWER. HOWEVER, THE 'A', 'B' AND 'AE' 4KV BUSSES DID NOT SUCCESSFULLY TRANSFER DUE TO PHASE DIFFERENTIAL BETWEEN ON-SITE AND OFF-SITE POWER. THE #1 EMERGENCY DIESEL GENERATOR AUTO-STARTED AND REENERGIZED THE 'AE' BUS. THE 'A' AND 'B' BUSSES WERE MANUALLY REALIGNED TO OFF-SITE POWER. THE 'A' RCP WAS RESTARTED. OPERATORS STABILIZED THE PLANT USING THE REACTOR TRIP RESPONSE PROCEDURE. THERE WERE NO SAFETY IMPLICATIONS DUE TO THIS EVENT. THIS EVENT WAS BOUNDED BY FSAR SECTION 15.2.6 (REACTOR TRIP FROM 100%, COINCIDENT WITH LOSS OF OFF-SITE POWER).
412 | 4121987034 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987034R00.pdf | 1987-10-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 98 | POWER LEVEL - 098%. ON 10/29/87 AT 0135 HOURS, WITH THE PLANT AT 98% REACTOR POWER, ERRATIC LEVEL SWINGS IN THE 'B' 5TH POINT HEATER WERE OBSERVED. OPERATIONS AND INSTRUMENT & CONTROL (I&C) PERSONNEL WERE DISPATCHED TO INVESTIGATE. AT 0142 HOURS, EXTRACTION STEAM TO THE 'B' 5TH POINT HEATER ISOLATED ON EXTREME HIGH LEVEL. HEATER DRAIN PUMP AND MAIN FEEDWATER PUMP (MFP) PERTURBATIONS WERE ALSO NOTED. AT 0145 HOURS, CONDENSATE POLISHING WAS BYPASSED TO IMPROVE MFP FLOW. A START ATTEMPT ON THE 21C CONDENSATE PUMP WAS UNSUCCESSFUL. THE 'B' 5TH POINT HEATER ISOLATION CAUSED LEVEL INCREASES AND HEATER ISOLATIONS IN THE ENTIRE 'B' HEATER TRAIN. AT 0145 HOURS, THE 21A MFP TRIPPED ON LOW SUCTION PRESSURE. AN EMERGENCY SHUTDOWN WAS COMMENCED, HOWEVER AT 0147 HOURS, A REACTOR TRIP ON LO-LO LEVEL IN THE 21B STEAM GENERATOR OCCURRED. THE OPERATORS STABILIZED THE PLANT IN HOT STANDBY USING THE EMERGENCY OPERATING PROCEDURES. THE CAUSE FOR THIS EVENT WAS IMPROPER RESPONSE OF THE 'B' 5TH POINT HEATER LEVEL CONTROL VALVES (LCV). I&C PERSONNEL ADJUSTED THE RESPONSE OF THE 'B' 5TH POINT HEATER LCVS. THE OTHER LCVS IN THE HEATER TRAIN WERE ALSO CHECKED FOR PROPER OPERATION. ADMINISTRATIVE GUIDANCE HAS BEEN PROVIDED TO OPERATIONS PERSONNEL AS A RESULT OF THIS EVENT. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS EVENT.
412 | 4121987035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987035R00.pdf | 1987-11-10 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Beaver Valley 2 | P | WE | PO | 11 | POWER LEVEL - 011%. ON 11/10/87, AT 2220 HOURS, WITH THE REACTOR AT 11% POWER FOLLOWING A STARTUP, AN ALARM INDICATING LOW CONDENSATE PUMP DISCHARGE PRESSURE WAS RECEIVED. AN ATTEMPT WAS MADE TO CORRECT THE PROBLEM BY OPENING THE CONDENSATE POLISHING BYPASS FLOW VALVE (2CNM-DCV100) FULL, WHILE REDUCING FLOW THROUGH THE CONDENSATE POLISHING DEMINERALIZERS. HOWEVER, THE PROBLEM PERSISTED, LEADING AT 2223 HOURS TO A TRIP OF THE RUNNING MAIN FEEDWATER PUMP (MFP) ON LOW SUCTION PRESSURE. A SUCCESSFUL RESTART OF THE PUMP WAS RETURNED, HOWEVER, TRIPPING THE MFP AGAIN AND PREVENTING THE START OF THE OTHER PUMP. ALTHOUGH BOTH MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS STARTED ON THE MFP TRIP, LOW-LOW LEVEL IN THE 'C' STEAM GENERATOR CAUSED A REACTOR TRIP AT 2226 HOURS. THERE WERE NO SAFETY IMPLICATIONS AS ALL REACTOR PROTECTION AND ENGINEERED SAFEGUARDS ACTIVATED AS REQUIRED TO MITIGATE THE CONSEQUENCES OF THE EVENT. THE CAUSE OF THE LOW PRESSURE WAS FOUND TO BE A BENT DISC AND STEM ON 2CNM-DCV100, WHICH PREVENTED THE NEARLY CLOSED VALVE FROM OPENING FURTHER IN RESPONSE TO ITS DEMAND SINGLE. THE VALVE WAS REPLACED BY A MODEL WITH AN INCREASED DIFFERENTIAL PRESSURE RATING. THE REACTOR WAS TAKEN CRITICAL AT 0345 HOURS ON 11/12/87.
412 | 4121987036 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121987036R00.pdf | 1987-11-17 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Beaver Valley 2 | P | WE | PO | 98 | POWER LEVEL - 098%. ON 11/17/87 AT 1406 HOURS, AN I&C TECHNICIAN WORKING IN THE CONTROL ROOM BUMPED AND TRIPPED THE POWER SUPPLY SWITCH TO THE TURBINE THRUST BEARING CIRCUIT SUPERVISORY INSTRUMENT. THE RESULTANT SIGNAL SPIKE INITIATED A THRUST BEARING FAILURE SIGNAL WHICH CAUSED A TURBINE TRIP/REACTOR TRIP. THE 4KV BUS USST BREAKERS TRIPPED PROPERLY ON A FAST TRANSFER AND THE SSST BREAKERS CLOSED PROPERLY, HOWEVER, THE USST BREAKERS RECLOSED CAUSING THE TRIPPED GENERATOR TO BE PARALLED WITH THE SYSTEM GRID. THE USST'S WERE ALLOWED TO RECLOSE DUE TO A TRIP SIGNAL THAT DOES NOT SEAL IN. OVERCURRENT ON THE 'D' USST CAUSED ALL FOUR USSTS TO RETRIP AND LOCK OPEN. WHILE THE SYSTEM GRID AND GENERATOR WERE PARALLED, THE (138KV) SYSTEM SUPPLY BREAKERS (OCB-94 & 85) TO THE 'A,B,C & D' 4KV BUSSES TRIPPED OPEN. THIS RESULTED IN A TOTAL LOSS OF AC POWER WHICH PLACED THE RCS IN NATURAL CIRCULATION. BOTH EMERGENCY DIESEL GENERATORS STARTED ON AN UNDERVOLTAGE SIGNAL AND REENERGIZED THE 'AE' AND 'DF' EMERGENCY BUSSES. THE (138KV) SYSTEM SUPPLY BREAKER (OCB-85) RECLOSED RESTORING POWER TO THE 'A & B' 4KV BUSSES. THE 'A & B' REACTOR COOLANT PUMPS (RCP) WERE RESTARTED. FOLLOWING TESTING OF THE 'B' SYSTEM STATION SERVICE TRANSFORMER, THE 'C & D' 4KV BUSSES WERE REENERGIZED AND THE 'C' RCP RESTARTED. THERE WERE NO SAFETY IMPLICATIONS RESULTING FROM THIS INCIDENT.
412 | 4121988002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121988002R01.pdf | 1988-01-27 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | POWER LEVEL - 100%. DURING NORMAL PLANT TESTING THE 21C SERVICE WATER PUMP WAS SHUTDOWN. AT THIS TIME THE 21A SERVICE WATER PUMP DISCHARGE PRESSURE TRANSMITTER FAILED DOWNSCALE RESULTING IN THE AUTO START OF THE 21A EMERGENCY SERVICE WATER PUMP. AT 0152 HOURS, THE 21A EMERGENCY SERVICE WATER PUMP WAS SHUTDOWN AND 62 MILLISECONDS LATER, THE 4KV BUS 2A SUPPLY BREAKER (ACB-42C) TRIPPED ON PHASE OVERCURRENT. THE LOSS OF THE 2A BUS CAUSED THE 21A REACTOR COOLANT PUMP TO TRIP ON UNDERVOLTAGE RESULTING IN A PLANT TRIP. THE AUTO-TRANSFER OF THE 2A BUS DID NOT OCCUR DUE TO THE OVERCURRENT TRIP. DE-ENERGIZING THE 2AE BUS CAUSED THE NO. 1 EMERGENCY DIESEL GENERATOR TO AUTOMATICALLY START AND ENERGIZE THE 4KV EMERGENCY BUS 2AE. DURING THIS TRANSIENT, THE RADIATION MONITORS FOR THE UNIT 2 CONTROL ROOM DE-ENERGIZED MOMENTARILY RESULTING IN ACTUATION OF THE CONTROL ROOM EMERGENCY BOTTLED AIR PRESSURIZATION SYSTEM (CREBAPS). THE SERVICE WATER PUMP DISCHARGE PRESSURE TRANSMITTER WAS CALIBRATED SATISFACTORILY AND IS SCHEDULED FOR REPLACEMENT. A MODIFICATION TO PREVENT A CREBAPS ACTUATION ON A LOSS OF POWER TO THE UNIT 2 CONTROL ROOM RADIATION MONITORS IS BEING EVALUATED. THE CAUSE OF THE ACB-42C TRIP IS UNDER INVESTIGATION. THE RESULTS OF THE INVESTIGATION IS PROVIDED IN THIS REPORT. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS EVENT AS ALL PROTECTIVE SYSTEMS ACTUATION AS DESIGNED.
412 | 4121988007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121988007R01.pdf | 1988-04-04 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 4/4/88 AT 0800 HOURS, WITH THE UNIT IN POWER OPERATION AT 100% REACTOR POWER, A SURVEILLANCE TEST OF THE 4KV AND 480VAC NORMAL 1 BUS UNDERVOLTAGE (UV) PROTECTION WAS INITIATED. THIS TESTING INVOLVES USING A BLOCKING RELAY IN THE UV CIRCUITRY WHILE TESTING THE UV PROTECTION RELAYS. DURING TESTING OF THE 2A 4KV BUS, ACTUATION OF THE UNDERVOLTAGE RELAYS OCCURRED CAUSING A LOSS OF 2A 4KV BUS MOTOR LOADS. THIS CAUSED THE 'A' REACTOR COOLANT PUMP TO TRIP INITIATING A REACTOR TRIP, AT 0847 HOURS, DUE TO THE LOW FLOW IN THAT COOLANT LOOP. THE OPERATORS STABILIZED THE PLANT IN HOT STANDBY USING THE EMERGENCY OPERATING PROCEDURES. THE CAUSE FOR THE UV PROTECTION RELAY ACTUATIONS WAS DETERMINED TO BE A MALFUNCTIONING BLOCKING RELAY. THE CONTACT SPACING WAS FOUND TO BE OUT OF ADJUSTMENT CAUSING IMPROPER OPERATION. THIS RELAY WAS ADJUSTED AND CALIBRATED USING A RELAY CALIBRATION PROCEDURE. THE UNDERVOLTAGE PROTECTION SURVEILLANCE TEST WAS PERFORMED SATISFACTORILY AND THE RELAY WAS RETURNED TO SERVICE. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS INCIDENT. THE UNDERVOLTAGE PROTECTION IS DESIGNED TO SHED THE LOADS ON THE RESPECTIVE BUS BEFORE ANY DAMAGE TO THE LOADS ARE RECEIVED DUE TO THE OPERATION AT A REDUCED VOLTAGE. THIS TYPE OF EVENT IS DISCUSSED IN THE FINAL SAFETY ANALYSIS REPORT, SECTION 8.3.1.1.11.
412 | 4121988009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121988009R00.pdf | 1988-07-27 | QR3 | Reactivity Control Imbalance | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 7/27/88, OPERATIONS PERSONNEL WERE PERFORMING A SURVEILLANCE TEST TO VERIFY CONTROL ROD MOVEMENT. DURING THE TEST, SHUTDOWN BANK 'A' (SBA) WOULD NOT MOVE. NO ROD CONTROL URGENT ALARM WAS RECEIVED. THE OPERATORS VERIFIED ALL DISCONNECT SWITCHES WERE CONNECTED AND AGAIN ATTEMPTED TO MOVE SBA RODS, WITH THE SAME RESULT. THE OTHER SHUTDOWN AND CONTROL ROD BANKS WERE VERIFIED OPERABLE. AT 1415 HOURS, SBA WAS DECLARED INOPERABLE AND THE UNIT ENTERED THE ACTION STATEMENT OF TECHNICAL SPECIFICATION 3.1.3.1. INSTRUMENT AND CONTROL (I&C) PERSONNEL SUSPECTED A FAULTY STATIONARY GRIPPER COIL FIRING CIRCUIT CARD AND PROCEEDED TO THE 1AC POWER CABINET. NO VISIBLE PROBLEMS WERE IDENTIFIED. I&C PERSONNEL REMOVED THE SUSPECT CARD AND UPON REMOVAL, A GROUP OF RODS CONTROLLED BY THE 1AC POWER CABINET FELL INTO THE REACTOR, INITIATING A POWER RANGE NEGATIVE RATE NEUTRON FLUX REACTOR TRIP AT 1441 HOURS. THE OPERATORS USED THE EMERGENCY OPERATING PROCEDURES TO STABILIZE THE PLANT. THE PROBLEM WAS DETERMINED TO BE A FAILED BUFFER CARD AND WAS SENT TO THE VENDOR FOR ANALYSIS. THERE WERE MINIMAL SAFETY IMPLICATIONS AS A RESULT OF THIS EVENT. THIS EVENT IS BOUNDED BY THE UPDATED FINAL SAFETY ANALYSIS REPORT, SECTION 15.
412 | 4121988013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121988013R00.pdf | 1988-09-20 | QR8 | Spurious Reactor Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 9/20/88 AT 0140 HOURS, WITH THE UNIT AT 100% REACTOR POWER, A MAINTENANCE SURVEILLANCE PROCEDURE (MSP) WAS COMPLETED ON LOOP 2A OVERPOWER DELTA-T (OPDT) CHANNEL. AT 0200 HOURS, ANOTHER SURVEILLANCE PROCEDURE WAS INITIATED TO VERIFY OPERABILITY OF THE NEUTRON FLUX POWER RANGE CHANNELS. THIS PROCEDURE REQUIRES THE BISTABLES FOR THE OPDT REACTOR TRIP AND ROD STOP BLOCKS TO BE PLACED IN THE TRIPPED CONDITION. TWO OF FOUR POWER RANGE CHANNELS WERE COMPLETED BY 0254 HOURS. THE BISTABLES FOR THE THIRD CHANNEL, ASSOCIATED WITH THE 2C REACTOR COOLANT LOOP, WERE TRIPPED AT 0301 HOURS. AT 0306 HOURS, AN ELECTRONIC SPIKE WAS RECEIVED ON LOOP 2A OPDT, COMPLETING THE REQUIRED LOGIC AND GENERATING AN OPDT REACTOR TRIP SIGNAL. THE OPERATORS STABILIZED THE PLANT USING THE EMERGENCY OPERATING PROCEDURES. INSTRUMENT AND CONTROL PERSONNEL WERE CALLED IN TO TROUBLESHOOT/CORRECT THE PROBLEM. THE CAUSE OF THE TRIP WAS DETERMINED TO BE A FAULTY ELECTRONIC CIRCUIT CARD. THIS CARD WAS REPLACED. ADMINISTRATIVE GUIDELINES HAVE BEEN PROVIDED TO OPERATIONS PERSONNEL, TO ENHANCE THE POST-TEST/MAINTENANCE PRACTICE. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS INCIDENT. THIS TYPE OF PROTECTIVE SYSTEM ACTUATION HAS BEEN PREVIOUSLY ANALYZED IN SECTION 15.6 OF THE UPDATED FINAL SAFETY ANALYSIS REPORT.
412 | 4121989003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121989003R00.pdf | 1989-02-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 55 | POWER LEVEL - 055%. ON 2/12/89, WITH THE UNIT IN POWER OPERATION, A POWER REDUCTION FROM 90% REACTOR POWER TO 50% REACTOR POWER WAS IN PROGRESS AS PART OF END OF CORE LIFE PROGRAMS. AT 0048 HOURS, OPERATORS NOTICED ERRATIC OPERATION OF THE 'C' MAIN FEEDWATER REGULATING VALVE (MFRV). THE OPERATORS PLACED THE 'C' MFRV IN MANUAL TO CONTROL STEAM GENERATOR LEVEL. AT 0108 HOURS AT APPROX. 55% REACTOR POWER, THE 'A' MAIN FEEDWATER PUMP WAS SHUTDOWN TO REDUCE THE PRESSURE DIFFERENTIAL ACROSS THE VALVE ALLOWING EASIER VALVE MOVEMENT AND CONTROL. AT 0120 HOURS, A TURBINE TRIP/REACTOR TRIP OCCURRED DUE TO A HIGH WATER LEVEL IN THE 'C' STEAM GENERATOR. THE OPERATORS STABILIZED THE PLANT IN HOT SHUTDOWN UTILIZING THE EMERGENCY OPERATING PROCEDURES. THE 'C' MFRV WAS FOUND TO HAVE SHEARED ANTI-ROTATION PINS AND THE STEM DETACHED FROM THE VALVE PLUG. THE CAUSE FOR THE VALVE FAILURE WAS ATTRIBUTED TO HYDRAULIC FORCES AND VIBRATION ACTING OVER TIME. THE MFRVS WERE ALL DISASSEMBLED, INSPECTED AND REPAIRED AS NECESSARY. THIS EVENT WAS REPORTED TO THE NUCLEAR REGULATORY COMMISSION AT 0300 HOURS, IN ACCORDANCE WITH 10CFR50.72.B.2.II. THERE WERE NO SAFETY IMPLICATIONS TO THE PUBLIC AS A RESULT OF THIS EVENT. THIS TYPE OF EVENT HAS PREVIOUSLY BEEN ANALYZED AS STATED IN THE UPDATED FINAL SAFETY ANALYSIS REPORT, SECTION 15.1.2, 'FEEDWATER SYSTEM MALFUNCTIONS CAUSING AN INCREASE IN FEEDWATER FLOW'.
412 | 4121990008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121990008R00.pdf | 1990-07-02 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 90 | On 7/02/90 at 0700 hours, with the Unit in Power Operation at 87% reactor power, a power increase to 90% was initiated. At approximately 0800 hours, Relay personnel began clearing the 345 KV Bus Backup Timer Protection associated with the main transformer to perform a calibration of Primary 345 KV Leads Secondary Backup Fault Unit (SBFU) Protection Relay, 50-J3202. Relay 50-J3202 is within a current loop inputting a signal to Differential Protection Relay 87-204. Relay 87-204 compares signals from the 345 KV distribution lines and the output of the main transformer. At 0915 hours, with the Unit at 90% reactor power, a reactor trip occurred. The reactor trip was the result of an immediate turbine/generator trip. Operations personnel utilized the Emergency Operating Procedures to stabilize the Unit in Hot Standby. The cause for the turbine/generator trip was actuation of Relay 87-204. This relay actuated as a result of a personnel error during the calibration of relay 50-J3202. The relay technician opened a four-pole shorting switch, de-energizing one input to relay 87-204, causing actuation. The four-pole shorting switch has been identified with warning placards and mechanically prevented from opening. There were no safety implications as a result of this event. The turbine/generator immediately tripped as designed upon a loss of the main output breakers, as discussed in the Updated Final Safety Analysis Report, Section 8.0.
412 | 4121991005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121991005R00.pdf | 1991-11-26 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On 11/26/91, with the Unit in Power Operation at 100 percent reactor power, a load rejection (closure of the governor and interceptor valves) occurred at 1143 hours. The closure of the governor and interceptor valves was the result of a signal from the Overspeed Protection Control (OPC) circuit. The load rejection caused a rapid reactor coolant system (RCS) heatup of three degrees. The control rods, in automatic, began to step into the core, however, a reactor trip on power range neutron flux negative rate occurred at 1143 hours. This trip was the result of the combined effects of the reactor fuel (doppler) and moderator temperature coefficients due to the RCS heatup resulting from the load rejection. Operations personnel stabilized the plant in Hot Shutdown. An investigation revealed that a solid state relay in the OPC circuit inadvertently actuated causing the load rejection. The failed relay was replaced. There were no safety implications as a result of this event. The reactor control system and the auxiliary feedwater system actuated as designed upon receipt of the reactor trip signal and low-low steam generator level signals.
412 | 4121993002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121993002R01.pdf | 1993-01-30 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Beaver Valley 2 | P | WE | PO | 92 | On 1/30/93, with the Unit at 92 percent power, the bistables for Loop 'A' Channel II main steam pressure were in a tripped condition for transmitter replacement. At 0124 hours, the Loop 'A' Channel III main steam pressure transmitter experienced a fuse failure which tripped the bistables for that channel, generating a Low Steamline Pressure Safety Injection (SI) signal. The SI signal caused a reactor trip and SI flow to the reactor coolant system. Operations personnel entered Emergency operating Procedure E-0 and the plant was stabilized in Hot Shutdown. The emergency diesel generators started as designed, but did not load due to the availability of offsite power. The auxiliary feedwater pumps automatically started and supplied feedwater to the steam generators. All other SI equipment operated as designed. The cause for this event was a comparator card power supply failure in the 'A' Channel III main steam pressure circuit. This tripped the bistables for that channel, which in conjunction with the tripped bistables for Loop 'A' Channel II, resulted in a SI and reactor trip signal. There were no safety implications as a result of this event. The SI equipment including the emergency diesel generators, standby high head charging pump, auxiliary feedwater pumps, standby service water pump and the associated valves all actuated to their design positions.
412 | 3341994005 | https://lersearch.inl.gov/PDFView.ashx?DOC::3341994005R00.pdf | 1994-06-01 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On 6/01/94 at 1455 hours, an insulating bushing failure on the Unit 1 Main Unit Transformer initiated an immediate generator/turbine trip followed by a subsequent reactor trip. The transformer fault initiated a voltage disturbance on the electrical grid which caused an inadvertent protective relay actuation on a circuit monitoring the 138 kilovolt (KV) AC line supplying the Unit 2 System Station Service Transformer (SSST)2A. Unit 2 4KV AC busses were being supplied by the offsite electrical grid. The loss of the 2A SSST resulted in the actuation of two reactor coolant pump underfrequency protective relays on two of the 4KV AC busses. This initiated a Unit 2 reactor trip. Both Units were stabilized in Hot Standby. The cause for this event was a single-phase insulating bushing failure on the Unit 1 Main Unit Transformer, which initiated a voltage disturbance on the electrical grid which affected Unit 2. Corrective actions have been initiated at both Units to address identified concerns. There were no safety implications as a result of this event. The reactor protection systems at both Units actuated as designed to place the reactors in safe shutdown conditions (Hot Standby). Engineered Safety Features systems actuated as required upon receipt of the initiation signals.
412 | 4121995006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121995006R00.pdf | 1995-08-13 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On 8/13/95, with Beaver Valley Unit 2 operating at 100%, a main generator loss of field resulted in a generator/turbine trip and a resulting reactor trip. The unit was at steady state conditions with all safety systems available and in automatic. At 1033 hours, a center tap clamp for one of the exciter field current limiting resistors was causing intermittent contact with ground due to vibration from the exciter. This resulted in a Zone 2 loss of field condition and immediately tripped the generator and turbine. The turbine trip initiated a reactor trip. Both reactor trip breakers opened and all control rods fully inserted. Plant response was as expected for a full power trip. All auxiliary feedwater pumps automatically started as designed on low-low steam generator water level. No primary or secondary relief or safety valves lifted, and the main condenser remained available as a heat sink. Both emergency busses remained energized by offsite power. Operators immediately entered Emergency Operating Procedure E-0, Reactor Trip or Safety Injection. The operators transitioned to procedure ES-0.1, Reactor Trip Response at 1034 hours to stabilize the unit in Hot Standby (Operational Mode 3). Following equipment repairs, the reactor was taken critical on 8/14/95 at 1334 hours, and the generator was synchronized to system at 0114 hours on 8/15/95.
412 | 4121996004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121996004R00.pdf | 1996-08-30 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | SU | 1 | During a refueling outage shutdown on August 30, 1996, at 2041 hours, Beaver Valley Power Station Unit 2 initiated a manual reactor trip, as a conservative action, when the average reactor coolant temperature (T sub ave) reached 541 degrees F. The generator output breakers were opened at 1921 hours. Reduced steam flow to the high pressure turbine, due to the governor valves closing to maintain synchronous speed (1800 RPM), resulted in reduced extraction steam to the high pressure (BP) feedwater heaters. caused feedwater temperature to decrease, as expected. Turbine pedestal testing commenced at 1930 hours, and upon completion, the turbine was tripped at 2004 hours. At 2036 hours, the 'A' steam generator wide range level started increasing above 65%, due to a leaking bypass feedwater regulating valve. Feedwater leakage, in conjunction with routine reactor power reduction from control rod insertion, caused a power mismatch and the decline in T sub ave. <br /><br /> The apparent cause of this event was a leaking bypass feedwater regulating valve, combined with a lack of procedural guidance for the control of the consequential excess feedwater. <br /><br /> Corrective actions for this event include: 1) procedures will be revised to provide the operator with guidance for earlier warning capabilities for the detection and for the correction of feedwater leakage or steam header leakage, 2) procedures will be revised to isolate blowdown to help steam generators attain isothermal temperatures prior to reactor shutdown, 3) procedure changes were validated on the simulator prior to implementation, 4) leakage through the bypass feedwater regulating valve will be monitored and evaluated during the upcoming startup, since leakage and 'AIRCET' (air operated valve actuator testing and analysis) testing performed under cold conditions did not confirm the existence of excessive leakage. <br /><br /> This event was reported pursuant to the requirements of 10CFR50.72(b)(2)(h) as an event or condition that results in a manual or automatic actuation of an Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv) as an event that resulted in manual or automatic actuation of an ESF, including the RPS.
412 | 4121997001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4121997001R02.pdf | 1997-01-06 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 98 | On 1/6/97, at approximately 0556 hours, while in Mode 1 at approximately 98% power, Unit 2 experienced a reactor trip caused by a turbine trip due to Operation of Main Transformer (MT) Ground Protection Relay 59-202G, which actuated MT Auxiliary Relay P7~202Xl. Post- trip control and protection systems functioned correctly, plant parameters were established within normal control bands, and the plant was placed in shutdo~~. NRC 4-hour notification of this event was made, at approximately 0616 hours (same day). The root cause of this event is inadequate design implementation of relay 59-2020, which was in service during operation other than MT backfeeding, since initial Unit startup. Actuation of relay 59-2020 is attributed to an arc to ground in the Main Unit Generator (MUG) when one of the air diffuser screens on the MUG 'B' phase Flexible Links Compartment (FLC) became detached, due to failed support welds, and momentarily contacted the MUG 22 kilo- volt (KV) isophase bus. Relay 59-202G was functionally tested and found acceptable. Other protective relays which could have actuated in response to an actual 22 KV ground fault were tested with no anomalies noted. The relay setting sheet and Operating procedures for relay 59-2020 were revised to ensure the relay is only in service during MT backfeeding. The corresponding Unit 1 relay setting sheet and procedures were reviewed and determined to be correct. The failed air diffuser screen was reattached with bolting and the other Unit 2 air diffuser screens were fastened with similar bolting. Unit 1 utilizes a different design for the MUG isophase leads box air diffuser screens. During the next Unit 1 refueling outage, the Unit MUG FLC will be inspected to ensure no loose components in the compartment.
412 | 3341997005 | https://lersearch.inl.gov/PDFView.ashx?DOC::3341997005R02.pdf | 1997-03-19 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On March 19, 1997, at approximately 0606 hours, while operating at 100% nominal power, Beaver Valley Power Station (BVPS) Units 1 and 2 experienced simultaneous reactor trips due to the opening of the output breakers for both units. The event was initiated by an inadvertent operation of the Bus Backup Timer relay on the #3-345 KV bus in response to a phase to ground fault which occurred on the Ohio Edison system's Mansfield-Hoytsdale 345 KV line. An Emergency Notification System (ENS) report was made pursuant to the requirements of 10CFR50.72(b)(2)(H) at 0922 hours on March 19, 1997. This event is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(iv). <br /><br /> Operations responded to the dual unit trip by entering the appropriate plant Emergency Operating Procedures (EOPs). Stabilization of Unit 1 was completed at approximately 0608 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient. Unit 1 Emergency Diesel Generator (EDG) EE-EG-1 started due to momentary undervoltage on 4 KV emergency bus AE, but was not required to load, since bus AE did not lose power. Unit 1 EDG EE-EG-2 did not start and was conservatively declared inoperable as of 0606 hours on March 19, 1997, until testing was completed which demonstrated that the undervoltage condition on bus DF was of insufficient duration to start EDG EE-EG-2. Both Unit 1 EDGs functioned as designed. <br /><br /> Stabilization of Unit 2 was completed at approximately 0610 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient with the exception of "B" Steam Generator Auxiliary Feedwater (AFW) flow indicating lower than normal. Subsequent investigation indicated that this was due to the concurrent event failure of a check valve in the "B" AFW injection header. The "B" AFW injection header was declared inoperable at 1206 hours on March 19, 1997, and, pursuant to the requirements of Technical Specifications (TS), Unit 2 commenced a boration and cooldown towards Mode 4 at 1731 hours on March 19, 1997. An update to the ENS notification pursuant to the requirements of 10CFR50.72(b)(1)(i)(A) was made at 1302 hours. Unit 2 entered Mode 4 at 1731 hours on March 19, 1997. An evaluation of the AFW check valve failure pursuant to the requirements of 10CFR21 was completed April 24, 1997. ENS Notification of 10CFR21 reportability was made at 1403 hours. <br /><br /> The root cause of the dual unit trip event was inadequate implementation of design specifications and design review which resulted in incorrect wiring between the Unit 2 Static Breaker Failure Unit Relay and its associated Static Relay Unit Bus Backup Timer. Both units were safely shut down in accordance with the applicable procedures. There were no implications to the health and safety of the public as a result of this event.
412 | 4122001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4122001001R00.pdf | 2001-03-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On March 17, 2001, at approximately 2113, Beaver Valley Power Station Unit No. 2 received alarms for steam flow/feedwater flow mismatch and 4160 volt motor overcurrent alarms. It was recognized that steam generator water levels were decreasing, a condensate pump had tripped, and a main feedwater pump had tripped. Implementing Abnormal Operating Procedure 2.24.1, Loss of Feedwater, the Nuclear Shift Supervisor ordered a manual reactor trip. However, while this action was being conducted, an automatic reactor trip properly initiated in response to a low-low steam generator water level in the "B" steam generator. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The automatic initiation of a reactor trip by the Reactor Protection System is reportable pursuant to 10 CFR 50.72 (b) (2)(iv)(B) and 10 CFR 50.73 (a) (2) (iv) (A) .The cause of the automatic trip was the tripping of the "A" Condensate Pump, 2CNM-P21A,due to electrical joint failure of its "C" phase power lead. This failure was attributed to a deficient joint configuration whereby a combination of long term heating, accelerated oxidation, and marginal sizing of the motor cable and terminal lugs resulted in an ultimate catastrophic failure of the joint. The safety significance for this event was small.
412 | 4122003003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4122003003R00.pdf | 2003-10-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 2 | P | WE | PO | 39 | On October 14, 2003, at 2355 hours, Beaver Valley Power Station Unit No. 2 reactor automatically tripped from 39 percent power and Auxiliary Feedwater was actuated due to low-low level in the "B" Steam Generator. Prior to the reactor trip, the control room operators were reducing power from 65 to 30 percent to support mechanical maintenance on the Heater Drain Pumps. The root cause was determined to be a failure of the Westinghouse 7300 multiplier/divider card, 2FWSFX486, in the channel IV "B" loop feedwater flow channel. After the reactor trip, Emergency Operating Procedure E-0 for Reactor Trip was performed, the plant was stabilized in Mode 3 and safety systems functioned as designed. This event was reported under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as a Reactor Protection System (RPS) actuation reactor trip. This event is also reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the RPS and Auxiliary Feedwater System that was not part of a pre-planned sequence. Based on the conditional core damage probability for the event when considering the actual component unavailability that was present at the time of the reactor trip, the safety significance of the automatic reactor trip was low.
412 | 4122006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4122006001R00.pdf | 2006-04-02 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 100 | On April 2, 2006, the Beaver Valley Power Station (BVPS) Unit No. 2 reactor tripped at 1402 hours due to a Main Generator Loss of Field Protection Trip. All safety systems functioned as designed. Both Emergency Diesel Generators (EDGs) automatically started due to a momentary under voltage condition caused by the initial Main Generator trip. Both EDGs ran unloaded. All three Auxiliary Feedwater System pumps started as expected on low steam generator levels. The plant was stabilized in Mode 3 with primary and secondary parameters returned to normal hot standby values.The root cause of the generator trip has been determined to be less than adequate workmanship, manufacturing and/or disassembly inspections. Initial inspection by the vendor (post-trip) identified that the block which supports the field pole #1 and field pole #2 terminals was not present. With this block missing, the field pole connection is subject to increased flexing during normal operation and also during maintenance activities. This increased flexing led to fatigue failure of the Exciter Field. With the open circuit resulting from the failed pole connection, the Main Generator tripped on loss of field. It was indeterminate if the support block was removed during one of the Exciter inspections/ disassemblies or never installed during the manufacturing process.This reactor trip is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event which resulted in the valid automatic actuation of the Reactor Protection System, the Auxiliary Feedwater System, and the on site emergency AC electrical power systems - Emergency Diesel Generators per 10 CFR 50.73(a)(2)(iv)(B). The risk was determined to be very low safety significance.
412 | 4122011002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4122011002R00.pdf | 2011-04-09 | QR6 | Manual Reactor Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 14 | On April 9, 2011, Beaver Valley Power Station Unit No. 2 (BVPS-2) was in the process of power ascension near the end of the fifteenth refueling outage (2R15). BVPS-2 entered Mode 1 at 0931 hours. At approximately 2309 hours on April 9, 2011, a field operator identified an active leak on the 0.75 inch pipe nipple on vent valve 2FWE-940 located on the Auxiliary Feedwater System (AFW) "A" Steam Generator (SG) feedwater injection header. On April 9, 2011 at 2349 hours, the Shift Manager declared the "A" SG feedwater injection header inoperable due to the observed condition. Per Condition D of Technical Specification (TS) 3.7.5 "Auxiliary Feedwater (AFW) System, " BVPS-2 was required to be in Mode 3 within six hours and be in Mode 4 within 18 hours. During the plant shutdown, level in "A" SG was approaching the predetermined low level manual trip criterion point of 25 percent and a manual reactor trip was performed. The manual reactor trip was successfully completed without complications. The Reactor Coolant System (RCS) cooldown resulted in a shrink of level in the "A" SG and the steam driven AFW pump successfully automatically started on low-low SG level in the "A" SG. AFW flow was injected into SGs "B" and "C". Since the "A" SG feedwater injection header had been previously isolated to repair the pipe nipple leak, AFW flow injection to the "A" SG did not occur. A manual main steam line isolation (SLI) was initiated to limit RCS cooldown. These events are reportable per: 10 CFR 50.73(a)(2)(i)(A) due to a completion of a plant shutdown required by Technical Specification, per 10 CFR 50.73(a)(2)(v)(B) and (D) as an event that could have prevented the fulfillment of a safety function for systems needed to remove decay heat and to mitigate the consequences of an accident, and per 10 CFR 50.73(a)(2)(iv)(B)(1) as a Reactor Protection System manual actuation (manual reactor trip), and also as a valid Engineered Safety Feature Actuation System (ESFAS) automatic actuation of the AFW system per 10 CFR 50.73(a)(2)(iv)(B)(6) and manual actuation of the SLI system per 10 CFR 50.73(a)(2)(iv)(B)(2). The root cause of the branch line crack was determined to be less than adequate design guidance contained in the design process to prevent vibration induced high cycle fatigue failure of the pipe nipple associated with 2FWE-940. The root cause of the manual reactor trip and automatic start of the steam driven AFW pump event was determined to be that the shutdown procedure guidance was not adequate for RCS temperature control and steam generator level control at the beginning of life conditions. The safety significance associated with these events is considered to be very low.
412 | 4122014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4122014002R00.pdf | 2014-05-20 | QR6 | Manual Reactor Trip | [45 empty] | Beaver Valley 2 | P | WE | PO | 16 | On May 20, 2014, at 0835 hours during a plant startup following the seventeenth refueling outage, Beaver Valley Power Station (BVPS) Unit 2 operations personnel manually tripped the reactor when it was recognized that the pre-determined trip criteria of 85 percent narrow range water level in the 'A' Steam Generator would be met. This manual trip criterion was reached after the steam generator water level began to oscillate following the start of the second condensate pump. Due to low decay heat input the main steam line isolation valves were shut in order to limit reactor coolant system cool down. Plant trip response was as expected without complications, and all control rods fully inserted in the core.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid manual or automatic actuation of any of the systems listed in (a)(2)(iv)(B) - (1) Reactor Protection System (RPS) and (2) Multiple Main Steam Isolation Valves (MSIVs). A 10 CFR 50.72 notification was made at 1052 hours on May 20, 2014, to report the manual reactor trip and main steam line isolation (EN# 50124).<br /><br /> The cause of this event has been determined to be the lack of an integrated secondary startup procedure. Station operating procedures will be revised to prevent recurrence.
413 | 4131987006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131987006R01.pdf | 1987-01-31 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Catawba 1 | P | WE | PO | 25 | POWER LEVEL - 025%. ON JANUARY 31, 1987, AT 1805:14 HOURS, A REACTOR TRIP OCCURRED ON A HIGH FLUX-LOW POWER REACTOR TRIP SIGNAL. CONTROL ROOM PERSONNEL WERE IN THE PROCESS OF BRINGING THE TURBINE-GENERATOR ON LINE WITH THE UNIT AT APPROXIMATELY 13% POWER. DUE TO A HIGH (APPROXIMATELY 10%/MIN) LOADING RATE WHICH IS AUTOMATICALLY SELECTED WHEN THE GENERATOR BREAKER CLOSES, THE TURBINE DEMAND RESULTED IN A SHARP DECREASE IN REACTOR COOLANT AVERAGE TEMPERATURE. IN AN ATTEMPT TO MAINTAIN TEMPERATURE, REACTOR POWER WAS MANUALLY INCREASED. REACTOR POWER REACHED THE 25% SETPOINT BEFORE CONTROL ROOM PERSONNEL WERE ABLE TO BLOCK THE HIGH FLUX-LOW POWER REACTOR TRIP SIGNAL. THE UNIT WAS AT 25% POWER AT THE TIME OF THE REACTOR TRIP. THIS INCIDENT IS ASSIGNED CAUSE CODE D, DEFECTIVE PROCEDURE. THE OPERATING PROCEDURE FOR THE TURBINE-GENERATOR DID NOT SPECIFY THE NEED TO CHANGE THE LOADING RATE PRIOR TO PLACING LOAD ON THE TURBINE. THE INCIDENT IS ALSO ASSIGNED CAUSE CODE X, OTHER, DUE TO A TRAINING DEFICIENCY. DUE TO NOT HAVING A SITE-SPECIFIC SIMULATOR, SOME CONTROL ROOM PERSONNEL HAVE NOT RECEIVED THE NECESSARY EXPERIENCE TO BECOME TOTALLY FAMILIAR WITH THE RESPONSE OF THE CATAWBA TURBINE-GENERATOR CONTROLS. THE OPERATORS HAVE RECEIVED CLASSROOM TRAINING, BUT HAVE ONLY HAD THE OPPORTUNITY FOR LIMITED ON-THE-JOB TRAINING. THIS INCIDENT IS REPORTABLE PURSUANT TO 10 CFR 50.73, SECTION (A)(2)(IV) AND 10 CFR 50.72, SECTION (B)(2)(II).
413 | 4131987013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131987013R00.pdf | 1987-03-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 58 | POWER LEVEL - 058%. ON 3-16-87, THE UNIT WAS AT 58% POWER AND INCREASING APPROXIMATELY 12% PER HR WHEN STEAM GENERATOR (S/G) A FW CONTROL VALVE CLOSED UNEXPECTEDLY AT 0103:50 HOURS. S/G A LEVEL IMMEDIATELY BEGAN TO DECREASE. THE OPERATOR AT THE CONTROLS (OATC) TOOK MANUAL CONTROL OF THE VALVE BUT IT WOULD NOT REOPEN. THE FW CONTROL BYPASS VALVE DID OPEN AND PROVIDED SOME FEED FLOW, BUT S/G A LEVEL CONTINUED TO DECREASE. THE OPERATOR MANUALLY TRIPPED THE REACTOR AT 0104:50 HOURS WHEN HE REALIZED THAT S/G A LEVEL WOULD NOT RECOVER PRIOR TO REACHING THE LOW-LOW LEVEL TRIP SETPOINT. FOLLOWING THE REACTOR TRIP, AN ERRONEOUS SIGNAL FROM THE BORON DILUTION MITIGATION SYSTEM SHUTDOWN MARGIN MONITOR CAUSED CENTRIFUGAL CHARGING (NC) PUMPS SUCTION TO SWAP FROM THE VOLUME CONTROL TANK (VCT) TO THE REFUELING WATER STORAGE TANK. THE OATC DEFEATED THE SIGNAL AND REALIGNED NV PUMPS SUCTION TO THE VCT. THIS INCIDENT IS CLASSIFIED AS EVENT CAUSE CODE X, OTHER. THE CAUSE OF THE CLOSURE OF THE FEEDWATER CONTROL VALVE COULD NOT BE IDENTIFIED. SUBSEQUENT INSPECTION OF THE VALVE, ITS CONTROL CIRCUIT, AND TESTING OF CONTROL CIRCUIT COMPONENTS REVEALED NO PROBLEMS. NO WORK ACTIVITIES WHICH COULD HAVE CAUSED THE VALVE TO CLOSE WERE IN PROGRESS AT THE TIME OF THE EVENT. THE CONTROL ROOM OPERATORS STABILIZED THE UNIT IN MODE 3, HOT STANDBY, FOLLOWING THE REACTOR TRIP.
413 | 4131987015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131987015R00.pdf | 1987-04-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON APRIL 9, 1987, AT 1040:43 HOURS, WITH UNIT 1 AT 100% POWER, STEAM GENERATOR (S/G) 1A MAIN FEEDWATER (CF) ISOLATION VALVE UNEXPECTEDLY CLOSED. THE REACTOR TRIPPED DUE TO LOW LOW LEVEL IN S/G 1A APPROXIMATELY THIRTY NINE SECONDS LATER. DURING THE RECOVERY FROM THE REACTOR TRIP, THE BORON DILUTION MITIGATION SYSTEM (BDMS) WAS PLACED IN SERVICE TOO SOON PER PROCEDURE, RESULTING IN AN AUTOMATIC SWAP OF THE CENTRIFUGAL CHARGING (NV) PUMPS' SUCTION FROM THE VOLUME CONTROL TANK (VCT) TO THE REFUELING WATER STORAGE TANK. THIS WAS DISCOVERED APPROXIMATELY THREE HOURS AFTER THE REACTOR TRIP WHILE THE NUCLEAR CONTROL OPERATOR WAS INVESTIGATING AN ABNORMALLY HIGH VCT LEVEL. THIS REALIGNMENT CONSTITUTES AN ENGINEERED SAFETY FEATURES ACTUATION. THE REACTOR TRIP IS CLASSIFIED AS EVENT CAUSE CODE B, DESIGN, MANUFACTURING, CONSTRUCTION/INSTALLATION DEFICIENCY. MOISTURE FOUND IN A TERMINAL BOX ON THE VALVE CAUSED A FUSE TO BLOW, FAILING THE VALVE CLOSED. FOLLOWING THE REACTOR TRIP, CONTROL ROOM PERSONNEL STABILIZED THE UNIT IN MODE 3, HOT STANDBY.
413 | 4131987026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131987026R00.pdf | 1987-07-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 6, 1987, AT 1513:31 HOURS, WITH THE UNIT AT 100% POWER, MAIN FEEDWATER PUMP TURBINE (CFPT) 1B SUDDENLY DECREASED SPEED, WHICH STABILIZED AT APPROXIMATELY 3800 RPM. CFPT 1A SPEED AUTOMATICALLY INCREASED TO ITS MAXIMUM ATTEMPTING TO COMPENSATE FOR THE CFPT 1B RUNBACK. THE COMBINED CFPT SPEEDS COULD NOT SUPPLY ENOUGH FEEDWATER AT 100% POWER, AND STEAM GENERATOR (S/G) WATER LEVELS BEGAN TO DECREASE RAPIDLY. CONTROL ROOM PERSONNEL WERE ALERTED BY THE FEED FLOW/STEAM FLOW MISMATCH ALARM AND BEGAN A MANUAL TURBINE GENERATOR LOAD REDUCTION, ENSURED ALL MAIN FEEDWATER (CF) CONTROL VALVES WERE OPENING, AND OPENED THE CF CONTROL BYPASS VALVES. AT 1514:00 HOURS, CFPT 1B TRIPPED ON LOW SUCTION FLOW AND MOTOR DRIVEN AUXILIARY FEEDWATER (CA) PUMP LB WAS STARTED MANUALLY TO INCREASE FEEDWATER FLOW TO THE S/GS. FOLLOWING RECEIPT OF THE S/G C LO LO LEVEL ALERT ANNUNCIATOR, THE DECISION WAS MADE TO MANUALLY TRIP THE REACTOR. THE UNIT WAS STABILIZED IN MODE 3, HOT STANDBY, AND RETURNED TO MODE 1, POWER OPERATION, ON JULY 8, 1987. THIS INCIDENT IS CLASSIFIED AS EVENT CAUSE CODE B, DESIGN, MANUFACTURING, CONSTRUCTION/INSTALLATION DEFICIENCY. A PIECE OF UNINSULATED SCRAP WIRE WAS DISCOVERED BETWEEN THE FREQUENCY TO VOLTAGE (F/V) CONVERTOR CHIP AND THE CIRCUIT BOARD ON WHICH IT WAS MOUNTED.
413 | 4131987028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131987028R00.pdf | 1987-07-11 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Catawba 1 | P | WE | PO | 94 | POWER LEVEL - 094%. ON JULY 11, 1987, AT 0254:21:691 HOURS, WITH UNIT 1 AT APPROXIMATELY 94% POWER, THE REACTOR AUTOMATICALLY TRIPPED ON AN INADVERTENTLY SIMULATED TURBINE TRIP. DUKE POWER PERSONNEL WERE IN THE PROCESS OF CONDUCTING THE WEEKLY MAIN TURBINE VALVE MOVEMENT PROCEDURE WHEN THE DISK DUMP VALVE FOR INTERMEDIATE STOP VALVE NUMBER 6 IS SUSPECTED TO HAVE NOT RESEATED. THIS CAUSED EMERGENCY TRIP SYSTEM (ETS) HEADER PRESSURE TO DECREASE (INDICATING TURBINE TRIP), WHICH GENERATED AN AUTOMATIC REACTOR TRIP SIGNAL FROM THE SOLID STATE PROTECTION SYSTEM. THE REACTOR TRIPPED, AND THE TURBINE AUTOMATICALLY TRIPPED IMMEDIATELY FOLLOWING THE REACTOR TRIP. THIS INCIDENT HAS BEEN CLASSIFIED EVENT CAUSE CODE X, OTHER. THE FAILURE OF THE DISK DUMP VALVE FOR INTERMEDIATE STOP VALVE NO. 6 CAUSED A FALSE INDICATION OF TURBINE TRIP TO BE GENERATED, WHICH RESULTED IN THE REACTOR TRIP. DUKE POWER HAS INSTALLED A TEMPORARY MODIFICATION TO THE MAIN TURBINE VALVES TO ALLOW TESTING TO BE PERFORMED WITHOUT UNSEATING THE DISK DUMP VALVES. DURING THE NEXT REFUELING OUTAGE FOR EACH UNIT, ALL DISK DUMP VALVES WILL BE INSPECTED AND MODIFIED IF NECESSARY. THE HEALTH AND SAFETY OF THE PUBLIC WERE UNAFFECTED BY THIS INCIDENT.
413 | 4131989008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131989008R01.pdf | 1989-03-05 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 3/5/89, AT 2140 HOURS, A UNIT 1 REACTOR TRIP OCCURRED AFTER EXCEEDING THE OVER POWER DELTA TEMPERATURE SETPOINT. IN PREPARATION FOR AUX. SAFEGUARDS TESTING OF STEAM LINE ISOLATION VALVES, THE OPERATOR AT THE CONTROLS MISTAKENLY DEPRESSED THE CLOSE PUSHBUTTON FOR THE MAIN STEAM LOOP A ISOLATION VALVE WHILE ATTEMPTING TO CLOSE THE STEAM GENERATOR 1A POWER OPERATED RELIEF ISOLATION VALVE. THE TWO PUSHBUTTONS ARE ADJACENTLY LOCATED. THE POWER OPERATED RELIEF ISOLATION VALVE HAD FAILED TO CLOSE ON TWO PREVIOUS PUSHBUTTON ACTUATIONS DURING THIS TEST. THE MAIN STEAM ISOLATION VALVE WAS IMMEDIATELY REOPENED, BUT AS OTHER RELIEF VALVES HAD ALSO OPENED, SAFETY INJECTION SUBSEQUENTLY ACTUATED ON LOW RATE COMPENSATED STEAM PRESSURE. UNIT RESPONSE TO THE TRIP AND SAFETY INJECTION WAS AS DESIGNED. CONTROL ROOM PERSONNEL ENTERED THE APPROPRIATE EMERGENCY PROCEDURES TO STABILIZE THE UNIT AND RECOVER FROM THE SAFETY INJECTION. THE APPLICATION OF PROTECTIVE COVERS TO CERTAIN CONTROL DEVICES HAS BEEN REVIEWED. THE POWER OPERATED RELIEF ISOLATION VALVE ACTUATOR DEVICES HAS BEEN REVIEWED. THE POWER OPERATED RELIEF ISOLATION VALVE ACTUATOR WAS FOUND TO HAVE A WORN STEM NUT WHICH WAS SUBSEQUENTLY REPLACED. THE UNIT WAS OPERATING IN MODE 1, POWER OPERATION, AT 100% POWER AT THE TIME OF THE TRIP.
413 | 4131989017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131989017R00.pdf | 1989-06-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JUNE 26, 1989, AT APPROXIMATELY 0635 HOURS, WITH UNIT 1 IN MODE 1, POWER OPERATION, AT 100% POWER, 1CF28, STEAM GENERATOR (S/G) 1A MAIN FEEDWATER (CF) CONTROL VALVE, SLOWLY BEGAN CLOSING, CAUSING S/G 1A LEVEL TO DECREASE. THE S/G 1A LEVEL DEVIATION ALARM WAS RECEIVED AND ICF30 S/G 1A CONTROL BYPASS VALVE, WAS OPENED TO SUPPLY ADDITIONAL CF FLOW. AN OPERATOR WAS DISPATCHED AND DISCOVERED THAT AIR WAS LEAKING FROM THE 1CF28 CONTROL AIR MANIFOLD. A WORK REQUEST WAS ISSUED TO INVESTIGATE AND REPAIR THE AIR LEAK AS S/G 1A LEVEL CONTINUED TO DECREASE. 1CF28 EVENTUALLY CLOSED AND REACTOR POWER WAS REDUCED IN AN ATTEMPT TO MATCH CF FLOW WITH DEMAND. A MANUAL REACTOR TRIP WAS INITIATED AT 0718 HOURS, FROM 86% REACTOR POWER, JUST PRIOR TO A S/G LOW LOW LEVEL REACTOR TRIP SIGNAL. EMERGENCY PROCEDURE EP/1/A/5000/01, REACTOR TRIP OR SAFETY INJECTION, WAS ENTERED. THE TURBINE TRIPPED DUE TO THE REACTOR TRIP AND AUXILIARY FEEDWATER ACTUATION OCCURRED. A GASKET IN THE VALVE'S CONTROL AIR MANIFOLD WAS FOUND TO BE TORN, WHICH APPARENTLY OCCURRED DURING INSTALLATION OF THE GASKET, DUE TO INAPPROPRIATE ACTIONS. THE TORN GASKET WAS REPLACED AND ALL OTHER UNIT 1 S/G CF CONTROL VALVES WERE INSPECTED FOR AIR LEAKS.
413 | 4131989022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131989022R00.pdf | 1989-08-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 8/24/89, UNIT 1 WAS IN MODE 1, POWER OPERATION, AT 100% POWER, AT 1930 HOURS, 1CF28, STEAM GENERATOR (S/G) 1A MAIN FEEDWATER (CF) CONTROL VALVE, BEGAN CLOSING, CAUSING A STEAM GENERATOR 1A LEVEL DEVIATION ALARM. THE CONTROL ROOM OPERATORS (CROS) RESPONDED BY OPENING 1CF30, S/G 1A CF CONTROL BYPASS VALVE, AND DISPATCHING OPERATIONS PERSONNEL AND INSTRUMENTATION AND ELECTRICAL (IAE) PERSONNEL TO INVESTIGATE THE PROBLEM. THE CRO BEGAN POWER REDUCTION TO COMPENSATE FOR THE REDUCED CF FLOW TO S/G 1A. AT 1944 HOURS, S/G 1A LEVEL BEGAN DROPPING RAPIDLY. THE CRO THEN INITIATED A MANUAL REACTOR TRIP AND ENTERED EMERGENCY PROCEDURE EP/1/A/5000/01, REACTOR TRIP OR SAFETY INJECTION. BY 2110 HOURS, S/G 1A WAS RETURNED TO THE NORMAL OPERATING LEVEL. POSITIONER CONTROL AIR MANIFOLD. THE GASKET APPEARED TO HAVE FAILED DUE TO IMPROPER DESIGN AND/OR INSTALLATION DEFICIENCY. THE POSITIONER WAS REPLACED ON 1CF28 AND ON THE REMAINING THREE UNIT 1 CONTROL VALVES BEFORE UNIT 1 RETURNED TO MODE 1, POWER OPERATION, AT 0753 HOURS ON 8/25/89. INSPECTED WEEKLY FOR AIR LEAKS, AND AN IMPROVED GASKET DESIGN HAS BEEN IMPLEMENTED ON UNIT 1.
413 | 4131991013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131991013R01.pdf | 1991-06-20 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Catawba 1 | P | WE | PO | 71 | On June 20, 1991, at 0823 hours, with Unit 1 in Mode 1, Power Operation, at 71% power following a refueling outage, a Reactor trip occurred on the "Low Flow P8. Permissive Trip" due to the trip of Reactor Coolant (NC) Pump 1A. The NC Pump 1A safety breaker opened as a result of a defective Silicon Controlled Rectifier (SCR), which tripped the overcurrent relay for the breaker, thereby tripping the pump. Plant response was as expected, with the Main Turbine tripping on Reactor trip, feedwater isolation, and the Auxiliary Feedwater System starting and supplying water to the Steam Generators. Emergency procedures were entered, and appropriate notifications were made. The Unit was brought back on line by 0545 hours on June 21. This incident is attributed to an Equipment Failure; the SCR for the NC Pump 1A safety breaker 50/51 XYZ overcurrent relay was found to be defective, and was replaced. All other SCRs associated with the NC Pump supply and safety breakers have been checked. Inspections of SCRs in other critical applications have been performed.
413 | 4131991015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131991015R00.pdf | 1991-07-10 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Catawba 1 | P | WE | PO | 92 | On July 10, 1991, at approximately 0901 hours, with Unit 1 in Mode 1, Power Operation, and operating at 92% Reactor power level, a Reactor (Rx) trip occurred as a result of a Turbine trip above P-9 (69% Reactor power). The Turbine tripped because of loss of both Main Feedwater (CF) pumps on low suction pressure. The low suction pressure condition occurred during a secondary side transient which began when the heater drain (HW) tank pump 1C1 outlet control valve (1HW59) failed closed as the control air signal line from the level controller to the valve positioner broke. This prevented 1C1 heater drain tank pump flow from entering the Condensate (CM) system, reducing CF pump suction pressure. The standby CM Booster Pump and Hotwell pump had been tagged out for preventive maintenance prior to the transient and were unavailable. While the operators were reducing load to recover CF pump suction pressure, the pumps tripped on low suction pressure. The Turbine and Reactor trips followed. This incident is attributed to a possible Design/Construction/Installation Deficiency. Metallurgical analysis showed that the failure was caused by vibration coupled with excessive stress loading at the positioner fitting. The failed tubing was replaced, and expansion coils were added.
413 | 4131991019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131991019R00.pdf | 1991-09-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 1 | P | WE | PO | 100 | On September 11, 1991, at 13:02:52 hours, with Unit 1 in Mode 1, Power Operation, and operating at 100% Reactor power level, a Reactor (Rx) trip occurred as a result of a Turbine trip above P-9 (69% Rx power). The Turbine tripped because of loss of both Main Feedwater (CF) pumps on high discharge pressure. The high discharge pressure occurred when the Advanced Digital Feedwater Control System (ADFCS) sensed that there was a loss of two out of three Nuclear Power Channel inputs. The ADFCS responded properly by reducing the S/G level setpoint from 66.5% to 38% based on its median selected value of 0% Reactor power. The setpoint change caused the CF control and bypass valves to rapidly close. The valve movement caused the feedwater header pressure to increase, tripping the CF pumps on high discharge pressure and subsequently tripping the Turbine. This incident is attributed to a possible inappropriate action during nuclear instrument calibration, with a contributing cause of inappropriate action of failure to follow policies, directives, or management procedures. Corrective action included addition of a four second delay in the activation of the ladder logic and input circuitry deviation alarms and 120 second lag time constant reducing the S/G program level to the ADFCS. The Independent Verification program is being evaluated to determine if training and program enhancements are needed.
413 | 4131991021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131991021R00.pdf | 1991-10-02 | QR5 | Turbine Trip | [45 empty] | Catawba 1 | P | WE | PO | 100 | On October 2, 1991, at 1200 hours, with Unit 1 at 100% power, a turbine trip resulting in a reactor trip occurred. A vendor, cleaning the area on the 619 elevation of the turbine building with high pressure water, inadvertently sprayed water into electrical box 1TBOX0047 located on the 594 elevation. The water infiltration caused erroneous 2 of 3 high water level signals in Moisture Separator Reheater "D" to initiate a turbine trip, and, subsequently, at 12:00:04 the reactor tripped. An evaluation of plant data has shown that all systems performed as designed following the trip. Procedures EP/1/A/5000/001A, Reactor Trip Response, and AP/1/A/5500/002, Turbine Generator Trip, were entered at 1205 hours, with all systems responding normally. The EP and AP procedures were completed at approximately 1235 hours, and OP/1/A/6100/005, Unit Fast Recovery, was initiated. This event has been attributed to an Installation Deficiency in failing to properly seal the conduit connectors which penetrate the NEMA 4 box. Corrective actions include an inspection of non-safety related NEMA 4 boxes located in the Unit 1 & 2 turbine buildings and sealing of the connectors as required. The vendor will develop a procedure for proper use of the pressure washer.
413 | 4131993008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131993008R00.pdf | 1993-07-18 | QP5 | Excessive Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | On July 18 at 2031 hours, with Unit 1 in Mode 1, Power Operation at 100% power, a Reactor Trip occurred due to low-low level in Steam Generator (S/G) 1A. Engineering was replacing a backup processor in the Digital Feedwater Control System (DFCS). As the processor was inserted the redundant processor failed, causing Main Feedwater (CF) and all S/G controls to swap to Manual and several Control Room (C/R) indications for S/G 1A to be driven to zero. This led C/R Operators to believe CF flow was lost, therefore they opened a CF valve to restore flow. When a S/G 1A High High Level Alert annunciator was received, CROs realized flow had not been lost and began to close the CF valve. The resulting transient caused the low-low S/G 1A level and Reactor Trip. On July 19 at 0030 hours, with Unit 1 in Mode 3, Hot Standby, Engineering was restoring the DFCS when an Auxiliary Feedwater System autostart occurred. The output control card (QAM) for CF Pump 1A speed control had swapped to its backup QAM. Upon reset to the primary QAM, with the backup in manual mode, a positive step change occurred causing CF Pump 1A to trip due to high discharge pressure. These incidents are attributed to Equipment Specification/Manufacture due to special installation instructions that were not provided. Corrective actions include a review of failure modes for DFCS, a review of spare DFCS parts, and procedure revisions.
413 | 4131994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4131994001R00.pdf | 1994-01-11 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Catawba 1 | P | WE | PO | 98 | On January 11, 1994, at 2258 hours, a Unit 1 Reactor (Rx) trip occurred due to a main Turbine trip on low condenser vacuum. Unit 1 was in Mode 1, Power Operation, at 989. power, when a two inch 'B' heater extraction line sheared off approximately six feet from entry into 'A' condenser, resulting in a loss of vacuum to 'A' condenser. The cause of the sheared extraction line was fatigue failure as a result of vibration over an extended period of time. Corrective actions included repairing the 'B' heater extraction line and examination of other extraction lines on both units. Engineering is evaluating options to reduce the amount of vibration on the extraction lines. Following the Rx trip, a main feedwater (CF) isolation occurred as a result of the Rx trip with low Reactor Coolant average temperature (Tave). Both motor driven auxiliary feedwater system pumps autostarted as expected, when three out of four CF isolation valves closed within two minutes of turbine load decreasing below 40%. A P-12 (Lo-Lo Tave) actuation occurred when one bank of steam dump valves opened causing Tave to decrease below the P-12 setpoint of 553 degrees F. The cause of the P-12 actuation is that a procedure step was not followed correctly. A contributing cause was controller windup due to a pressure transmitter that was reading higher than expected. Corrective actions include meeting with all Control Room Operators to discuss procedure adherence, controller windup, changes to Emergency Procedures that will provide more detail for transferring to the pressure control mode, and performing a calibration on the pressure transmitter.
413 | 4132000001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132000001R00.pdf | 2000-02-13 | QR8 | Spurious Reactor Trip | [45 empty] | Catawba 1 | P | WE | PO | 100 | On February 13, 2000 at 1831 hours with Catawba Unit 1 operating in Mode 1 "Power Operation" at 100% power, a reactor trip occurred. The cause of the reactor trip was actuation of the turbine trip instrumentation inputs to the Solid State Protection System (SSPS) logic. This was due to an electrical short within an electrical connector on the normally energized Turbine Electrical Trip Solenoid Valve (ETSV). This caused the normally energized ETSV to de-energize and dump Emergency Trip System (ETS) pressure, resulting in the pressure switches on the ETS header sensing pressure dropping below their set point and thus sending a signal that the turbine was tripped to the SSPS. The SSPS then initiated a reactor trip. All systems responded as designed to shut down the reactor and maintain it in a safe shutdown condition. This event is being reported as an automatic actuation of the reactor protection system. Corrective Actions included replacing the failed connector. A failure analysis performed on the connector determined that the root cause of the problem was a misapplication of the connector insert insulating material, which is made of neoprene. This connector will be replaced with a high temperature model.
413 | 4132001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132001001R00.pdf | 2001-01-17 | QR5 | Turbine Trip | [45 empty] | Catawba 1 | P | WE | PO | 99 | On January 17, 2001 at 1618 hours with Catawba Unit 1 operating in Mode 1 at 99.8% power, a reactor trip caused by a turbine trip occurred. The Mechanical Trip Solenoid Valve (MTSV) in the Main Turbine Protection System had been replaced in late November 2000 during refueling outage 1EOC12. Since that time a mechanical "Sequence Halt" was experienced when Turbine Trip Testing was performed. Troubleshooting focused on the limit switch associated with the Mechanical Trip Piston and failed to note that the Mechanical Trip Piston was not fully reset. Replacement of the limit switch required adjustment of the limit switch to the Mechanical Trip Piston. This adjustment produced a false reset signal for the test circuitry while the mechanical trip assembly was not fully reset thus causing a Turbine trip. A root cause investigation determined that the root cause of the event was incomplete troubleshooting analysis. The MTSV was replaced. A planned corrective action is for Engineering to develop "at power" troubleshooting guidelines for components of the Main Turbine Controls and the Main Feedwater Pump Turbine Controls.
413 | 4132003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132003001R00.pdf | 2003-02-04 | QP5 | Excessive Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | February 4, 2003, at 1005 hours, Catawba Unit 1 tripped from 100% power. A Main Feedwater (MFW) System header pressure transmitter was being returned to service following replacement. As the transmitter was valved in, its hydraulic interaction with the other two nearby transmitters caused MFW header pressure indication to the MFW control system to fluctuate. In response to the transient, the MFW control system switched from automatic to manual control, as designed, at a pre determined pressure difference between the transmitters. As control room operators attempted to control steam generator levels manually, a high-high level on steam generator B resulted in a turbine trip, which resulted in a reactor trip. The high-high level also resulted in a trip of the MFW pumps, which caused an automatic start of the motor driven Auxiliary Feedwater (AFW) System pumps. This event was caused by an inadequate understanding of the MFW control system response to a common impulse line hydraulic interaction. Corrective actions planned in response to this event include training appropriate plant personnel concerning MFW control system design and response and revising procedures associated with the calibration and maintenance of selected transmitters.
413 | 4132003005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132003005R00.pdf | 2003-08-29 | QR8 | Spurious Reactor Trip | [45 empty] | Catawba 1 | P | WE | PO | 95 | On August 29, 2003 at 0203 hours with Catawba Unit 1 operating in Mode 1 at 95% power, an automatic reactor trip occurred due to an instrument failure. The reactor trip was caused by the pressurizer pressure channel 2 failing low resulting in the reduction of the loop 1B overtemperature delta T (OTdT) setpoint to approximately 50%. When the OTdT setpoint reached the operating value of the loop 1B conditions (approximately 95%), an automatic reactor trip was initiated on 2/4 OTdT trip bistables. The loop 1A OTdT trip bistable was previously tripped due to a reactor coolant system hot leg temperature detector failure. This event was caused by the equipment failure of the pressurizer pressure loop power supply card. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Corrective actions for this event included repairs to the pressurizer pressure channel and reactor coolant system hot leg temperature detectors.
413 | 4132004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132004002R00.pdf | 2004-02-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 1 | P | WE | PO | 100 | On February 22, 2004, at 1729 hours, with Catawba Unit 1 operating in Mode1 at 100% power, the hydraulic system for the actuator on 1B Steam Generator Main Feedwater Isolation valve (1CF-42) failed and the valve closed. As a result, the Operators manually tripped the reactor.This event was caused by the equipment failure of the valve actuator for1CF-42. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Corrective actions for this event included replacing the actuator for valve 1CF-42.
413 | 4132004004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132004004R00.pdf | 2004-12-05 | QR5 | Turbine Trip | [45 empty] | Catawba 1 | P | WE | PO | 100 | On December 5, 2004, at 2135 hours, with Catawba Unit 1 operating in Mode 1 at 100% power, an automatic reactor trip occurred due to a turbine trip above P-9 (69% power). The turbine trip was due to an invalid high water level indication from two of the three level switches for the 1B moisture separator reheater. The root cause of the reactor trip was due to micro-switch mechanisms on the two level switches being out of adjustment, concurrent with external vibration to the switches. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Major plant equipment operated as expected. This event was of no significance with respect to the health and safety of the public. Corrective actions for this event included inspecting all Unit 1 and Unit 2 micro-switch positions, and adjusting or replacing the switch mechanisms as necessary.
413 | 4132006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132006001R00.pdf | 2006-05-20 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Catawba 1 | P | WE | PO | 100 | On 05/20/06, at 1401 hours, both Catawba units tripped automatically from 100% power following a loss of Offsite Power (LOOP) event. The event began when a fault occurred internal to a current transformer associated with one of the switchyard power circuit breakers. A second current transformer failure, along with the actuation of differential relaying associated with both switchyard busses, cleared both busses and separated the units from the grid. A Notification of Unusual Event (NOUE) was declared at 1414 hours. The Emergency Response Organization was electively activated. Both emergency diesel generators on each unit started automatically and supplied their required blackout and essential loads as designed. All three auxiliary feedwater pumps on each unit started automatically and fed the steam generators as designed. Decay heat was removed via natural circulation of the reactor coolant system, with steam relief through the steam generator power operated relief valves. Both units were stabilized in Mode 3 with cooldown activities in progress. Offsite power was restored to all 6900V busses on both units by 05/20/06 at 2041 hours. The NOUE was subsequently terminated on 05/21/06 at 0140 hours.The root cause analysis for this event determined that in 1981, certain switchyard relay tap setting changes were not implemented at Catawba. Power Delivery documentation was subsequently erroneously updated to indicate that the changes had been made. Corrective actions for this event will include developing an enhanced process to ensure correct configuration management for the Catawba protective relay settings. The health and safety of the public were not adversely affected by this event.
413 | 4132012001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132012001R01.pdf | 2012-04-04 | QR2 | Loss of Primary Flow (RPS Trip) PWR |  | X | [13 empty] | X | [29 empty] | Catawba 1 | P | WE | PO | 100 | On 04/04/12 at 2003 hours, Unit 1 tripped from 100% power following a trip of reactor coolant pump 1D. Shortly after the Unit 1 generator power circuit breakers opened, the Zone G protective relaying system unexpectedly actuated on an instantaneous underfrequency condition as a result of an error in the relay logic. This opened the switchyard breakers thereby isolating Unit 1 from the grid and resulting in a Loss of Offsite Power (LOOP). At the time of the trip, Unit 2 was in Mode 5 during its End-of-Cycle 18 Refueling Outage with both of its essential busses aligned to Unit 1 offsite power. Therefore, Unit 2's essential busses lost power as a result of the LOOP. Both emergency diesel generators (EDGs) on each unit automatically started and powered their respective essential busses as designed. A Notification of Unusual Event (NOUE) was declared as a result of the LOOP and the Catawba Emergency Response Organization was activated. Approximately five and one-half hours later, after confirming that the sources of the fault were cleared, offsite power was restored to one essential bus on each unit and the NOUE was terminated. The root causes of this event and the planned corrective actions in response to this event are described in detail in the respective sections of this LER. All plant safety related systems required to mitigate the event were operable and capable of performing their required safety related functions. These systems functioned as designed in response to this event. Therefore, the health and safety of the public were not adversely affected by this event.
414 | 4141987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987002R01.pdf | 1987-01-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 28, 1987, AT 1534 HOURS, UNIT 2 TRIPPED ON STEAM GENERATOR (S/G) D LOW LOW LEVEL. THE LOW LOW LEVEL WAS CAUSED WHEN THE S/G 2D MAIN FEEDWATER (CF) CONTROL VALVE, CLOSED AFTER A TEST CABLE CONNECTED TO ITS CONTROLLER CARD, IN THE 7300 PROCESS CABINET, WAS SHORTED. ALSO, DURING RECOVERY FROM THE TRIP, THE MOTOR DRIVEN AUXILIARY FEEDWATER (CA) PUMPS ACTUATED ON LOSS OF BOTH MAIN FEEDWATER PUMPS WHEN CONTROL ROOM PERSONNEL INADVERTENTLY ENTERED THE CONDENSATE AND FEEDWATER SYSTEM HOT RESTART PROCEDURE WHILE CF PUMP 2A WAS STILL RUNNING AND CLOSED ITS RECIRCULATION VALVE. THE UNIT WAS AT 100% POWER AT THE TIME OF THE REACTOR TRIP. THE UNIT WAS IN MODE 3, HOT STANDBY, AT THE TIME OF THE AUXILIARY FEEDWATER ACTUATION. THIS INCIDENT IS ASSIGNED CAUSE CODE X, OTHER. THE TEST CABLE TO THE 7300 PROCESS CABINET WAS ACCIDENTALLY SHORTED WHEN A TECHNICIAN CLOSED THE CABINET DOOR, FOR HOUSEKEEPING PURPOSES, AND THE CABLE WAS PINCHED BY THE DOOR'S LATCH PIN. THE POSSIBILITY OF THE SHORTING OF THIS TEST CABLE WAS NOT ANTICIPATED. THE METHOD USED TO INSTALL THE TEST CABLE WAS NORMAL ACCEPTABLE PRACTICE. ALSO, THE CA SYSTEM ACTUATION IS ASSIGNED CAUSE CODE A, PERSONNEL ERROR.
414 | 4141987007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987007R01.pdf | 1987-02-24 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON FEBRUARY 24, 1987, AT 1359:17 HOURS, A POWER PANELBOARD 2EPD UNDERVOLTAGE COMPUTER ALARM WAS RECEIVED AT THE CONTROL ROOM. DURING THE INVESTIGATION OF THE SITUATION, A BREAKER WAS DISCOVERED TO BE LOOSE WITH THE APPEARANCE OF BEING TRIPPED. THE BREAKER WAS RESET AND RESULTED IN AN ACTUAL UNDERVOLTAGE CONDITION TO 2EPD. THIS UNDERVOLTAGE RESULTED IN MAIN FEEDWATER ISOLATION AND BOTH MAIN FEEDWATER PUMPS TRIPPED ON HIGH DISCHARGE PRESSURE. THE TURBINE TRIPPED ON LOSS OF BOTH MAIN FEEDWATER PUMPS, AND A REACTOR TRIP FOLLOWED THE TURBINE TRIP. THE UNIT WAS AT 100% POWER AT THE TIME OF THIS INCIDENT. THE INCIDENT HAS BEEN ATTRIBUTED TO A MANAGEMENT DEFICIENCY DUE TO THE DECISION TO CYCLE THE BREAKER BEING MADE WITHOUT SUFFICIENTLY INVESTIGATING THE SITUATION. THE FAILURE OF AN OPTICAL ISOLATOR AND THE FAILURE OF THE FEEDER BREAKER TO INDICATE CORRECTLY ALSO CONTRIBUTED TO THIS EVENT BY GIVING THE FALSE INDICATION OF AN UNDERVOLTAGE OF 2EPD AND BY MISLEADING THE RESPONSIBLE PERSONNEL INTO BELIEVING THAT THE BREAKER HAD TRIPPED, RESPECTIVELY. THE HEALTH AND SAFETY OF THE PUBLIC WERE UNAFFECTED BY THIS EVENT.
414 | 4141987010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987010R00.pdf | 1987-03-23 | QG9 | Primary System Leak | [45 empty] | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON MARCH 23, 1987, AT 1205 HOURS, WITH UNIT 2 AT 100% POWER, THE REACTOR COOLANT (NC) SYSTEM UNIDENTIFIED LEAKAGE RATE WAS DECLARED TO BE GREATER THAN THAT ALLOWED BY TECHNICAL SPECIFICATIONS. AT THIS TIME, DUKE POWER MANAGEMENT DECIDED TO PERFORM THE UNIT LOSS OF ELECTRICAL LOAD TEST TO INITIATE THE REQUIRED UNIT SHUTDOWN. THE NUCLEAR CONTROL OPERATOR (NCO) INITIATED THE GENERATOR FULL LOAD REJECTION AT 1520:40:565 HOURS BY OPENING THE MAIN GENERATOR BREAKERS. THE LOAD REJECTION CAUSED A TRANSIENT IN THE TURBINE EMERGENCY TRIP SYSTEM (ETS) HEADER, WHICH RESULTED IN A 'TURBINE TRIP CAUSES REACTOR TRIP' ALARM AND A REACTOR TRIP. THE UNIT WAS STABILIZED IN MODE 3, HOT STANDBY, SHORTLY AFTER THE TRIP. THIS EVENT IS CLASSIFIED AS EVENT CAUSE CODE X, OTHER. THE TECHNICAL SPECIFICATION REQUIRED SHUTDOWN, DUE TO THE HIGH UNIDENTIFIED NC LEAKAGE RATE, WAS CAUSED BY VALVE STEM PACKING FAILURE ON AN NC POWER OPERATED RELIEF VALVE ISOLATION VALVE. ALL SAFETY SYSTEMS WERE AVAILABLE FOR ACCIDENT MITIGATION IF REQUIRED. THE HEALTH AND SAFETY OF THE PUBLIC WERE UNAFFECTED BY THIS INCIDENT.
414 | 4141987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987018R00.pdf | 1987-05-05 | QR6 | Manual Reactor Trip | [45 empty] | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 2220 HOURS, ON MAY 5, 1987, ROUTINE TESTING IDENTIFIED A DEFECTIVE SOLID STATE PROTECTION SYSTEM (SSPS) RELAY. THE RELAY WAS INADVERTENTLY ACTUATED AT 2307 HOURS, WHILE IT WAS BEING CHANGED OUT. THIS RESULTED IN AN ISOLATION OF CONTAINMENT CHILLED WATER (YV) SYSTEM COOLING WATER TO THE REACTOR COOLANT (NC) PUMP MOTORS. SUBSEQUENT ATTEMPTS TO REESTABLISH FLOW FAILED, AND THE DECISION WAS MADE TO MANUALLY TRIP THE REACTOR AND THEN TRIP THE NC PUMPS TO PREVENT FURTHER OVERHEATING OF THE MOTOR WINDINGS. THE REACTOR WAS TRIPPED FROM 100% POWER AT 0051:36:527 HOURS ON MAY 6, AND ALL NC PUMPS WERE TRIPPED SHORTLY THEREAFTER. THE UNIT WAS STABILIZED IN MODE 3, HOT STANDBY, AND NATURAL CIRCULATION WAS ESTABLISHED TO REMOVE HEAT FROM THE NC SYSTEM. A STUCK CLOSED RN SWAP-OVER VALVE WAS SUBSEQUENTLY OPENED MANUALLY, RESTORING COOLING WATER FLOW TO THE NC PUMP MOTORS. THIS INCIDENT IS CLASSIFIED AS EVENT CAUSE CODE E, MANAGEMENT/QUALITY ASSURANCE DEFICIENCY. THERE WAS NO PROCEDURAL GUIDANCE AVAILABLE TO ASSURE THE RELAY WOULD BE PROPERLY REPLACED. THE APPROPRIATE PROCEDURES WILL BE EVALUATED AND ENHANCED AS NECESSARY. THIS INCIDENT IS ALSO ASSIGNED CONTRIBUTING EVENT CAUSE CODE B, DESIGN, MANUFACTURING, CONSTRUCTION/INSTALLATION DEFICIENCY.
414 | 4141987019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987019R00.pdf | 1987-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 65 | POWER LEVEL - 065%. ON MAY 8, 1987, AT 0304 HOURS, WITH UNIT 2 AT 65% POWER, THE STEAM GENERATOR (S/G) 2C FEEDWATER (CF) CONTROL VALVE UNEXPECTEDLY CLOSED. S/G 2C LEVEL IMMEDIATELY BEGAN TO DECREASE. THE CONTROL ROOM OPERATORS (CRO) UNSUCCESSFULLY ATTEMPTED TO REOPEN THE VALVE. THEY OPENED THE CF BYPASS CONTROL VALVE, BUT S/G 2C LEVEL CONTINUED TO DECREASE. THE CRO MANUALLY TRIPPED THE REACTOR IN ANTICIPATION OF A LOW LOW S/G LEVEL TRIP APPROXIMATELY 37 SECONDS AFTER THE CF CONTROL VALVE CLOSED. THIS INCIDENT IS CLASSIFIED AS EVENT CAUSE CODE X, OTHER. THE UNEXPECTED CLOSURES OF THE S/G 2C CF CONTROL VALVE WAS CAUSED BY THE MALFUNCTION OF A PROCESS CONTROL SYSTEM (PCS) PRINTED CIRCUIT CARD. CONTROL ROOM PERSONNEL STABILIZAD THE UNIT IN MODE 3, HOT STANDBY, FOLLOWING THE REACTOR TRIP. THE PCS PRINTED CIRCUIT CARD WAS SUBSEQUENTLY REPLACED AND THE VALVE WAS RETURNED TO SERVICE. THE HEALTH AND SAFETY OF THE PUBLIC WERE UNAFFECTED BY THIS INCIDENT.
414 | 4141987021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987021R01.pdf | 1987-07-27 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 90 | POWER LEVEL - 090%. ON 7/27/87, UNIT 2 WAS OPERATING AT POWER WHEN A CONDENSATE TRANSIENT OCCURRED WHICH RESULTED IN A REACTOR TRIP. DURING THE TRANSIENT, CONDENSATE BOOSTER PUMP SUCTION PRESSURE DECREASED SIGNIFICANTLY CAUSING THE THIRD HOTWELL PUMP TO START AUTOMATICALLY. MAIN FEEDWATER PUMP SUCTION PRESSURE DECREASED, AND THE THIRD CONDENSATE BOOSTER PUMP STARTED AUTOMATICALLY. ALL CONDENSATE BOOSTER PUMPS TRIPPED. SUBSEQUENTLY, BOTH MAIN FEEDWATER PUMPS TRIPPED CAUSING A TURBINE TRIP FOLLOWED BY THE REACTOR TRIP. THE UNIT WAS STABILIZED IN MODE 3, HOT STANDBY, FOLLOWING THE REACTOR TRIP. CONDENSATE FLOW WAS REESTABLISHED BY OPENING THE CONDENSATE POLISHER BYPASS VALVES. THE INITIATING EVENT FOR THE CONDENSATE TRANSIENT AND LOSS OF CONDENSATE FLOW IS UNKNOWN. THE UNAVAILABILITY OF SECONDARY SYSTEM TRANSIENT MONITOR DATA HAS ADDED DIFFICULTY IN DETERMINING THE INITIATING CIRCUMSTANCES FOR THIS EVENT. A DEFECTIVE PROCEDURE CONTRIBUTED TO THIS EVENT. DURING SUBSEQUENT TESTING BY PERFORMANCE PERSONNEL ON 2/20/88, IT WAS DETERMINED THAT THE UNIT 2 CONDENSATE POLISHING DEMINERALIZER (CPD) DIFFERENTIAL PRESSURE (D/P) TRANSMITTER DID NOT FUNCTION PROPERLY DUE TO A CALIBRATION ERROR. IF THE CPD BYPASS VALVES HAD FUNCTIONED AS DESIGNED DURING THE TRANSIENT, THE TRIP MAY HAVE BEEN PREVENTED. THE OVERRANGE STOP BAR WAS SET CORRECTLY, AND THE TRANSMITTER WAS RECALIBRATED.
414 | 4141987025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987025R00.pdf | 1987-09-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 22 | POWER LEVEL - 022%. ON SEPTEMBER 3, 1987, AT APPROXIMATELY 0617 HOURS, AN AUTOMATIC MAIN FEEDWATER (CF) ISOLATION AND MAIN TURBINE GENERATOR TRIP OCCURRED DUE TO A HIGH HIGH STEAM GENERATOR (S/G ) WATER LEVEL. THE CF ISOLATION CAUSED THE CF PUMP TURBINE (CFPT) TO TRIP AND THE MOTOR DRIVEN AUXILIARY FEEDWATER (CA) PUMPS STARTED AUTOMATICALLY. REACTOR POWER WAS BEING MANUALLY RUN BACK FROM 22% POWER WHEN AT APPROXIMATELY 0619 HOURS, AN AUTOMATIC REACTOR TRIP OCCURRED FOLLOWING A S/G LOW LOW LEVEL REACTOR TRIP SIGNAL WHILE TRANSFERRING CF FLOW TO THE LOWER S/G FEEDWATER NOZZLE. THE TURBINE DRIVEN CA PUMP STARTED AUTOMATICALLY UPON RECEIPT OF A SECOND S/G LOW LOW LEVEL ALARM. FOLLOWING THE REACTOR TRIP, S/G LEVELS WERE RESTORED TO NORMAL, AND THE UNIT WAS STABILIZED IN MODE 3, HOT STANDBY. THE UNIT ENTERED MODE 1 AT 1108 HOURS ON SEPTEMBER 4, 1987. THIS INCIDENT IS ATTRIBUTED TO A PERSONNEL ERROR BECAUSE THE CONTROL ROOM OPERATORS (CROS) DECIDED TO CONTINUE THE NOZZLE TRANSFER WITHOUT FIRST SEEKING ADVICE FROM THE UNIT SUPERVISOR WHEN THEY RECOGNIZED THAT THE CF CONTROL VALVE WAS IN AN ABNORMAL CONDITION. THIS INCIDENT IS ALSO ATTRIBUTED TO A MANAGEMENT DEFICIENCY. THE UNIT SUPERVISOR IN THE CONTROL ROOM DID NOT EXERCISE APPROPRIATE SUPERVISORY CONTROL OVER THE TWO CROS. THE INCIDENT WILL BE REVIEWED WITH THE APPROPRIATE PERSONNEL.
414 | 4141987027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987027R01.pdf | 1987-09-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 48 | POWER LEVEL - 048%. ON SEPTEMBER 15, 1987, AT 0253:35 HOURS, UNIT 2 WAS MANUALLY TRIPPED DUE TO IMPENDING LOW STEAM GENERATOR (S/G) 2B LEVEL. THE TRANSIENT WAS INITIATED WHEN THE S/G 2B MAIN FEEDWATER (CF) CONTROL VALVE FAILED CLOSED CAUSING S/G 2B LEVEL TO DECREASE RAPIDLY. CONTROL ROOM (CR) PERSONNEL ATTEMPTED TO MANUALLY REOPEN THIS VALVE BUT IT WOULD NOT RESPOND. CR PERSONNEL MANUALLY OPENED THE S/G 2B FEEDWATER BYPASS CONTROL VALVE IN AN ATTEMPT TO RECOVER S/G FEED FLOW. HOWEVER, S/G 2B LEVEL DECREASED BELOW 20% AND THE REACTOR WAS MANUALLY TRIPPED. FOLLOWING THE REACTOR TRIP, AN AUXILIARY FEEDWATER (CA) AUTOSTART OCCURRED DUE TO 2 OUT OF 4 LOW LOW S/G LEVELS. ALSO, AT 0335:25 HOURS, A SECOND CA AUTOSTART SIGNAL OCCURRED ON LOSS OF BOTH CF PUMPS WHEN CF PUMP 2A TRIPPED WHILE CR PERSONNEL WERE ATTEMPTING TO RESTART IT. THE UNIT WAS AT 48% POWER AT THE TIME OF THE REACTOR TRIP AND WAS IN MODE 3, HOT STANDBY, AT THE TIME OF THE SECOND CA AUTOSTART. THE CAUSE OF THE CONTROL VALVE CLOSING WAS A FAILURE OF THE VALVE'S CONTROLLER/DRIVER CARD IN THE 7300 PROCESS CABINET. SEVERAL COMPONENTS IN THE CARD'S POWER SUPPLY CIRCUIT OVER HEATED RESULTING IN A ZERO VALVE DEMAND SIGNAL. THE SECOND CA AUTOSTART IS ATTRIBUTED TO AN EQUIPMENT FAILURE DUE TO THE FAILURE OF THE HIGH PRESSURE STOP VALVE TO RESET.
414 | 4141987029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141987029R00.pdf | 1987-11-03 | QR5 | Turbine Trip | [45 empty] | Catawba 2 | P | WE | PO | 59 | POWER LEVEL - 059%. ON NOVEMBER 3, 1987, AT 0836 HOURS, STEAM GENERATOR (S/G) 2C NARROW RANGE (N/R) LEVEL CHANNEL 2 INOPERABLE DUE TO ITS READING BEING OUT OF TOLERANCE. THE UNIT WAS AT 93% POWER. SINCE S/G 2C N/R LEVEL CHANNEL 4 WAS ALSO INOPERABLE, A TECHNICAL SPECIFICATION REQUIRED UNIT SHUTDOWN WAS COMMENCED AT 0926 HOURS. THE CHANNEL 2 READING BECAME INCREASINGLY ERRATIC AND AT APPROXIMATELY 1146 HOURS IT CAUSED A SPURIOUS S/G HIGH HIGH LEVEL TURBINE TRIP, A MAIN FEEDWATER (CF) ISOLATION, AND A CF PUMP TURBINE TRIP. MOTOR DRIVEN (M/D) AUXILIARY FEEDWATER (CA) PUMP 2B STARTED AUTOMATICALLY TO SUPPLY FEEDWATER TO THE S/GS (M/D CA PUMP 2A WAS ALREADY OPERATING). AT 1146:39 HOURS, THE REACTOR WAS MANUALLY TRIPPED FROM 59% POWER. APPROXIMATELY 11 SECONDS LATER, ALL FOUR S/G LEVELS DECREASED BELOW THE LOW LOW LEVEL REACTOR TRIP SETPOINT. THE TURBINE DRIVEN (T/D) CA PUMP STARTED AUTOMATICALLY, HOWEVER, IT TRIPPED WITHIN SECONDS. THE M/D CA PUMPS WERE UTILIZED TO RESTORE S/G LEVELS TO NORMAL AND TO COOL DOWN THE UNIT. THE UNIT ENTERED MODE 4, HOT SHUTDOWN, AT 2013 HOURS. THIS INCIDENT IS ATTRIBUTED TO THE FAILURE OF THE S/G 2C N/R LEVEL CHANNELS DUE TO THEIR REFERENCE LEG VENT LINE ISOLATION VALVES LEAKING STEAM PAST THE SEAT. THE REFERENCE LEG VENT LINE STEAM LEAKS WERE STOPPED, AND THE LEAKING VENT LINE ISOLATION VALVES WILL BE REPAIRED.
414 | 4141988012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988012R00.pdf | 1988-03-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 15 | POWER LEVEL - 015%. ON MARCH 9, 1988, AT APPROXIMATELY 1825 HOURS, CONTROL ROOM OPERATORS (CROS) WERE SWAPPING FROM THE STEAM GENERATOR (S/G) MAIN FEEDWATER (CF) BYPASS VALVE TO THE S/G CF CONTROL VALVE FOR S/G 2B, DURING UNIT STARTUP FOLLOWING END-OF-CYCLE 1 REFUELING OUTAGE. WHEN THE CRO PLACED S/G CF CONTROL VALVE IN AUTO, THE VALVE OPENED UNEXPECTEDLY. THE CROS IMMEDIATELY TOOK MANUAL CONTROL OF THE VALVE AND THE CF PUMP TURBINE (PT) TO STABILIZE FEEDFLOW TO S/G 2B. LEVELS IN S/GS C AND D CONTINUED TO RISE. AT 1825:36:317 HOURS, S/G 2D HI HI LEVEL OCCURRED TRIPPING THE TURBINE AND CFPT, AND INITIATING FEEDWATER ISOLATION. LEVEL IN S/G 2A WAS DECREASING AND AT 1825:44:179 HOURS, REACTOR TRIP OCCURRED FROM 15% POWER DUE TO LOW LOW LEVEL IN S/G 2A. AFTER THE INITIAL TRIP RECOVERY, THE CROS DISCOVERED THAT MOTOR DRIVEN AUXILIARY FEEDWATER (CA) PUMP TRAIN A HAD SWAPPED SUCTION TO THE NUCLEAR SERVICE WATER (RN) SYSTEM. THE UNIT WAS RETURNED TO MODE 2, STARTUP, ON MARCH 18, 1988, AT 1501 HOURS, AND MODE 1, POWER OPERATION, AT 2035 HOURS. THIS INCIDENT HAS BEEN ATTRIBUTED TO AN EQUIPMENT FAILURE. THE UNEXPECTED OPENING OF THE S/G CF CONTROL VALVE WAS ATTRIBUTED TO A DEFECTIVE PRINTED CIRCUIT CARD AND A DEFECTIVE CONTROLLER DRIVER CARD. DUKE POWER PERSONNEL REPLACED THE DEFECTIVE CARDS.
414 | 4141988019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988019R01.pdf | 1988-05-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 000%. ON MAY 27, 1988, AT 1403:21 HOURS, AN UNDERVOLTAGE CONDITION OCCURRED ON THE 240/120 VAC AUXILIARY CONTROL POWER SYSTEM DISTRIBUTION PANEL 2KXPB. THIS UNDERVOLTAGE CONDITION OCCURRED WHILE CYCLING THE ALTERNATE SOURCE TO KXPB BREAKER IN AN ATTEMPT TO CLEAR AN INDICATED ALTERNATE SOURCE UNDERVOLTAGE. THE INDICATED UNDERVOLTAGE CONDITION WAS NOTICED WHILE ISOLATING THE 2KXPB INVERTER FOR CORRECTIVE MAINTENANCE. THE PANEL'S POWER SUPPLY HAD PREVIOUSLY BEEN SWAPPED TO THE ALTERNATE SOURCE TO KXPB SUPPLY FROM REGULATED AC POWER SOURCE, 2RDB. UPON NOTICING THE LOW ALTERNATE SOURCE VOLTAGE INDICATION ON THE MANUAL BYPASS SWITCH, 2KXMB, THE INVOLVED NUCLEAR OPERATIONS SPECIALIST (NOS) REQUESTED ASSISTANCE FROM CONTROL ROOM PERSONNEL. A CONTROL ROOM OPERATOR (CRO) UTILIZED THE OPERATOR AID COMPUTER (OAC) GRAPHICS TO VERIFY THAT A LOW VOLTAGE WAS INDICATED. THE CRO RECOMMENDED THAT THE NOS CYCLE THE ALTERNATE SOURCE TO KXPB BREAKER TO CLEAR THE UNDERVOLTAGE CONDITION. CYCLING THE BREAKER CAUSED AN APPROXIMATE 5 SECOND LOSS OF POWER TO THE LOADS SUPPLIED BY THE KXPB DISTRIBUTION PANEL, ONE OF WHICH WAS THE CONTROL POWER TO MAIN FEEDWATER PUMP TURBINE (CFPT) 2B. THIS RESULTED IN A DECREASE IN CFPT 2B SPEED, LOW STEAM GENERATOR LEVELS, AND A SUBSEQUENT AUTOMATIC REACTOR TRIP. THE UNIT WAS AT 100% POWER AT THE TIME OF THIS INCIDENT.
414 | 4141988020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988020R01.pdf | 1988-05-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 15 | POWER LEVEL - 015%. ON MAY 28, 1988, AT 2355 HOURS, A MANUAL REACTOR TRIP WAS INITIATED BY CONTROL ROOM PERSONNEL TO PREVENT AN AUTOMATIC CHALLENGE OF THE REACTOR PROTECTION SYSTEM ON STEAM GENERATOR (S/G)) 2C LOW-LOW LEVEL. OPERATIONS PERSONNEL WERE PERFORMING THE UNIT FAST RECOVERY PROCEDURE FOLLOWING A MAY 27, 1988, TRIP AND WERE IN THE PROCESS OF UNISOLATING THE MAIN FEEDWATER (CF) CONTROL VALVES. THE CONTROL ROOM OPERATOR HAD JUST OPENED THE CF CONTROL VALVE OUTLET ISOLATION VALVES AND WAS IN THE PROCESS OF OPENING THE INLET ISOLATION VALVES WHEN S/G 2C NARROW RANGE LEVEL BEGAN TO RAPIDLY DECREASE. SUBSEQUENT EFFORTS BY CONTROL ROOM PERSONNEL DID NOT STOP THE LEVEL DECREASE IN S/G 2C, AND THE REACTOR WAS SUBSEQUENTLY TRIPPED. THE REACTOR TRIP IN CONJUNCTION WITH LOW-TAVG RESULTED IN A FEEDWATER ISOLATION, AND THE SUBSEQUENT LOW-LOW LEVEL SIGNAL FOR S/G 2C RESULTED IN AN AUXILIARY FEEDWATER ACTUATION. THE UNIT WAS IN MODE 1, POWER OPERATION, AT APPROXIMATELY 15% POWER AT THE TIME OF THIS INCIDENT. THIS INCIDENT IS CLASSIFIED AS EVENT CAUSE CODE X, OTHER. IT IS SPECULATED THAT DEBRIS IN THE SUPPLY AIR MAY HAVE PREVENTED THE ELECTRIC TO PNEUMATIC (E/P) CONVERTER FOR 2CF48, THE S/G 2C CF BYPASS CONTROL VALVE, FROM OPERATING PROPERLY. THIS INCIDENT IS ALSO CLASSIFIED A CONTRIBUTING EVENT CAUSE CODE X, OTHER.
414 | 4141988021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988021R01.pdf | 1988-06-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 38 | POWER LEVEL - 038%. ON 6/3/88, AT APPROXIMATELY 2240 HOURS, A MANUAL REACTOR TRIP WAS INITIATED DUE TO AN IMMINENT LOW LOW STEAM GENERATOR (S/G) LEVEL. THE UNIT WAS IN THE PROCESS OF DECREASING POWER TO 7% FOR INSPECTION AND REPAIR OF PACKING AND SEAT LEAKS ON VARIOUS VALVES. AT THE PRECEDING SHIFT TURNOVER, ONCOMING OPERATIONS PERSONNEL WERE INFORMED THAT THE AUXILIARY STEAM HEADER WAS ALIGNED TO SUPPLY MAIN FEEDWATER PUMP (CFPT) 2A WHICH WOULD ALLOW THE PACKING AND STEAM LEAK TAGOUT TO BE PLACED. AS THE NUCLEAR EQUIPMENT OPERATOR (NEO) CLOSED THE HIGH PRESSURE STEAM SUPPLY TO CFPT 2A AND 2B PER THE TAGOUT, THE NUCLEAR CONTROL OPERATOR (NCO) NOTICED DECREASING MAIN FEEDWATER/MAIN STEAM (CF/SM) DIFFERENTIAL PRESSURE. A NUCLEAR OPERATOR TECHNICIAN WAS DISPATCHED AND THE CFPT STEAM SUPPLY VALVE WAS REOPENED. THE CF/SM DIFFERENTIAL PRESSURE RETURNED TO NORMAL. THE NCOS WERE MANUALLY CONTROLLING THE CF CONTROL VALVES TO RESTORE S/G LEVELS. DURING THIS PERIOD, THE S/G B CF CONTROL VALVE WAS OVERTHROTTLED, CAUSING THE LEVEL TO DECREASE RAPIDLY. TO PREVENT A CHALLENGE OF THE REACTOR PROTECTION SYSTEM, A MANUAL REACTOR TRIP WAS INITIATED. THE UNIT WAS OPERATING AT 38% POWER AT THE TIME OF THE TRIP. THIS INCIDENT IS ATTRIBUTED TO THE UNIT 2 AUXILIARY STEAM HEADER SUPPLY ISOLATION VALVE BEING CLOSED FOR A UNDETERMINED REASON.
414 | 4141988022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988022R00.pdf | 1988-06-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Catawba 2 | P | WE | PO | 60 | POWER LEVEL - 060%. ON 6/6/88, AT 1338 HOURS, AN AUTOMATIC REACTOR TRIP OCCURRED WHILE DUKE POWER OPERATIONS (OPS) PERSONNEL WERE PERFORMING THE MONTHLY SURVEILLANCE TEST OF THE ROD CONTROL SYSTEM. DURING INSERTION OF SHUTDOWN BANK B, ROD N9 BECAME MISALIGNED BY APPROX. 30 STEPS. AFTER DISCUSSION WITH DUKE POWER INSTRUMENTATION AND ELECTRICAL (IAE) PERSONNEL AND A WESTINGHOUSE SITE REPRESENTATIVE, THE ROD WAS REALIGNED. DURING SUBSEQUENT TESTING OF SHUTDOWN BANK B, ROD N9 DROPPED INTO THE CORE, DUE TO FAILURE OF A FUSE, CAUSING A REACTOR TRIP ON HIGH NEGATIVE FLUX RATE. FEEDWATER ISOLATION WAS AUTOMATICALLY INITIATED. AUX. FEEDWATER ACTUATED ON LO LO STEAM GENERATOR LEVEL. THE UNIT WAS IN MODE 1, POWER OPERATION, AT 60% POWER AT THE TIME OF THIS INCIDENT. THIS INCIDENT HAS BEEN ATTRIBUTED TO A POSSIBLE INSTALLATION DEFICIENCY. THE CHASE-SHAWMUTT FUSE WHICH FAILED IN THE ROD CONTROL SYSTEM CIRCUITRY WAS NOT THE TYPE FUSE SPECIFIED BY WESTINGHOUSE. THE ACTIVITY WHICH INSTALLED THE IMPROPER FUSE COULD NOT BE IDENTIFIED. IT ALSO CANNOT BE DETERMINED IF AN ACTUAL OVERCURRENT CONDITION EXISTED AT THE TIME OF FUSE FAILURE. IAE REPLACED THE FAILED FUSE AND 25 OTHER CHASE-SHAWMUTT TYPE A25X10 FUSES FOUND IN UNIT 2 POWER CABINETS. IAE ALSO VERIFIED THAT THE ROD GRIPPER ASSEMBLY WAS DRAWING THE EXPECTED CURRENT AFTER THE FUSE WAS REPLACED.
414 | 4141988023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988023R00.pdf | 1988-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 98 | POWER LEVEL - 098%. ON 6/20/88, AT 1008:15 HOURS, A SHUTDOWN OF MAIN FEEDWATER PUMP TURBINE LUBE OIL (LF) PUMP 2A1 CAUSED MAIN FEEDWATER PUMP TURBINE (CFPT) 2A TO AUTOMATICALLY TRIP ON LOW BEARING OIL PRESSURE. LF PUMP 2A2 AND THE EMERGENCY BEARING OIL PUMP AUTOMATICALLY STARTED UPON SENSED LOW OIL PRESSURE. THE OUTPUT PRESSURE FROM THESE PUMPS DID NOT BUILD QUICKLY ENOUGH TO PREVENT THE TRIP OF THE CFPT. THE LOSS OF ONE CFPT AUTOMATICALLY INITIATED A RUNBACK OF THE MAIN TURBINE. THE CONDENSER STEAM DUMP VALVES OPENED TO CONTROL THE PRIMARY COOLANT TEMPERATURE AS DESIGNED. STEAM GENERATOR (S/G) LEVELS DECREASED DUE TO DECREASED FEEDWATER FLOW. THE CONTROL ROOM OPERATORS ATTEMPTED TO RESET THE TRIPPED CFPT BUT COULD NOT CLEAR THE INTERLOCKS IN TIME TO PREVENT DECREASING S/G LEVELS TOWARDS THE REACTOR TRIP SETPOINT IN ALL S/GS. THE OPERATORS TRIPPED THE REACTOR MANUALLY DUE TO IMMINENT AUTOMATIC TRIP ON LOW LOW S/G LEVEL. UNIT 2 WAS AT 98% POWER PRIOR TO THIS INCIDENT. THIS INCIDENT HAS BEEN ATTRIBUTED TO A FAILED CUTLER HAMMER MODEL E30JY8 PUSHBUTTON SWITCH. THE FAILURE OF THE LATCHING MECHANISM OF THE SWITCH ALLOWED THE CONTACTS TO OPEN, WHICH MAINTAIN LF PUMP 2A1 IN OPERATION, AND CAUSED THE PUMP TO TRIP. THE FAULTY SWITCH WAS REPLACED. IMPLEMENTATION OF MODIFICATIONS TO THE LF PUMP START CIRCUITRY WILL BE PURSUED.
414 | 4141988025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988025R00.pdf | 1988-06-26 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 6/26/88, AT APPROX. 2300 HOURS, AN AUTOMATIC UNIT 2 REACTOR TRIP OCCURRED DUE TO LOW LOW STEAM GENERATOR (S/G) LEVEL WHILE THE AUXILIARY SAFEGUARDS TEST CABINET PERIODIC TEST WAS BEING CONDUCTED BY PERFORMANCE PERSONNEL. VERIFY CLOSURE OF THE SM ISOLATION BYPASS VALVES AND THAT THE S/G 2D POWER OPERATED RELIEF VALVE (PORV) WOULD CHANGE FROM MANUAL TO AUTOMATIC MODE UPON AN SM ISOLATION SIGNAL. AFTER THE S/G SM ISOLATION BYPASS VALVES WERE VERIFIED TO BE CLOSED AND THE S/G PORV CONTROL MODE WAS VERIFIED, A RELAY WHICH WAS ACTIVATED BY THIS SIGNAL WAS REQUIRED TO BE RESET PER THE PERIODIC TEST. THE PERFORMANCE TEST COORDINATOR (PTC) PLACED A JUMPER BETWEEN TWO TEST POINTS TO RESET THE RELAY. AFTER THE RELAY WAS RESET, THE PTC REMOVED THE JUMPER AND RETURNED TO THE CONTROL ROOM TO START ANOTHER SECTION OF THE PERIODIC TEST. THE NUCLEAR CONTROL OPERATOR (NCO) INCORRECTLY ASSUMED THAT AN SM RESET WAS STILL NECESSARY AND DEPRESSED THE SML CLOSED/RESET BUTTON TO RESET SM ISOLATION. THIS ACTUATION SHUT SM1, MAIN STEAM ISOLATION FOR S/G D, CAUSING A PRESSURE INCREASE IN S/G D AND RESULTING IN A LEVEL DECREASE. THE REACTOR SUBSEQUENTLY TRIPPED ON S/G D LOW LOW LEVEL. THE UNIT WAS OPERATING AT 100% POWER AT THE TIME OF THE TRIP. THIS INCIDENT IS ATTRIBUTED TO A PERSONNEL ERROR.
414 | 4141988028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988028R00.pdf | 1988-09-29 | QR5 | Turbine Trip | [45 empty] | Catawba 2 | P | WE | PO | 95 | POWER LEVEL - 095%. ON 9/29/88, AT 1252:55 HOURS, A UNIT 2 REACTOR TRIP FROM 35% POWER WAS MANUALLY INITIATED UPON LOSS OF MAIN FEEDWATER (CF) TO THE STEAM GENERATORS (S/G) FOLLOWING A TURBINE RUNBACK ON LOSS OF STATOR COOLING WATER FLOW (KG). MAIN GENERATOR KG PUMP 2A WAS INADVERTENTLY TRIPPED AT APPROXIMATELY 1248 HOURS BY CONSTRUCTION AND MAINTENANCE PERSONNEL. FOLLOWING THE TURBINE RUNBACK TO 23% TURBINE LOAD, A HI-HI LEVEL SIGNAL IN S/G 2A RESULTED IN A TURBINE TRIP AND CF ISOLATION. AT THIS TIME, OPERATIONS PERSONNEL MANUALLY TRIPPED THE REACTOR AND TOOK APPROPRIATE ACTION TO STABILIZE THE UNIT. UNIT 2 WAS IN MODE 1, POWER OPERATION, AT 95% POWER PRIOR TO THE LOSS OF KG FLOW. THIS INCIDENT HAS BEEN ATTRIBUTED TO A PERSONNEL ERROR DUE TO THE INADVERTENT TRIP OF KG PUMP 2A. SPORADIC CONDENSER VALVE PERFORMANCE RESULTED IN SWING INVENTORY IN THE S/G'S AND CONTRIBUTED TO THIS EVENT. THE EVENT WAS DISCUSSED WITH APPROPRIATE PERSONNEL. CONDENSER STEAM DUMP VALVE DEFICIENCIES WILL BE CORRECTED. THE HEALTH AND SAFETY OF THE PUBLIC WERE UNAFFECTED BY THIS EVENT.
414 | 4141988031 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141988031R00.pdf | 1988-11-23 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 48 | POWER LEVEL - 048%. ON 11/23/88, AT 0919:56 HOURS, AN INADVERTENT MOMENTARY ACTUATION OF THE TRAIN A INTERIOR DOGHOUSE LEVEL SWITCH INITIATED A SIGNAL FOR SEVERAL VALVES TO CLOSE. TWO VALVES, 2CF51, S/G 2C CF CONT ISOL AND 2CF1O, CF PUMP 2A DISCH ISOL, INITIATED CLOSURE, BUT 2CF51 REOPENED AFTER THE SIGNAL CLEARED. 2CF1O CONTINUED TO CLOSE BECAUSE OF SEAL-IN LOGIC IN THE CIRCUITRY. AS THE VALVE CLOSED, MAIN FEEDWATER PUMP TURBINE (CFPT) 2A TRIPPED ON HIGH DISCHARGE PRESSURE. CF PUMP 2B WAS OUT OF SERVICE FOR MAINTENANCE. CONSEQUENTLY, A MAIN TURBINE TRIP AND AN AUX. FEEDWATER AUTOSTART ON TRIP OF BOTH CFPTS WERE INITIATED. CONTROL ROOM OPERATORS INITIATED A RESET OF CFPT 2A IN AN ATTEMPT TO REESTABLISH FEEDWATER FLOW, BUT RAPIDLY DECREASING STEAM GENERATOR LEVELS CAUSED THE OPERATORS TO MANUALLY INITIATE A REACTOR TRIP. A FEEDWATER ISOLATION WAS INITIATED ON REACTOR TRIP COINCIDENT WITH LOW TAVE. THE UNIT WAS OPERATING AT 48% POWER AT THE TIME OF THIS INCIDENT. THE ACTUATION OF THE LEVEL SWITCH WAS ATTRIBUTED TO K-MAC CLEANING PERSONNEL SWEEPING NEAR THE LEVEL SWITCH AND CONTACTING THE LEVEL SWITCH DISPLACER. THIS INCIDENT HAS BEEN ATTRIBUTED TO A DESIGN DEFICIENCY BECAUSE THE CIRCUIT DESIGN FOR THE LEVEL SWITCHES AND THE MOUNTING DESIGN FOR THE STANDPIPE WERE NOT ADEQUATE TO PREVENT AN INADVERTENT ACTUATION OF THE HIGH DOGHOUSE LEVEL ISOLATION CIRCUITRY.
414 | 4141989001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141989001R00.pdf | 1989-01-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 94 | POWER LEVEL - 094%. ON 1/12/89, AT 0943 HOURS, A BUSSMANN FNA FUSE FAILED IN A MAIN FEEDWATER CONTROL VALVE CIRCUIT CAUSING THE VALVE TO FAIL CLOSED. CONTROL ROOM OPERATORS OPENED THE MAIN FEEDWATER BYPASS VALVE IN AN ATTEMPT TO PROVIDE ADDITIONAL FEEDWATER. THE UNEXPECTED CLOSURE ISOLATED FEEDWATER FLOW TO STEAM GENERATOR 2D AND QUICKLY RESULTED IN AN AUTOMATIC REACTOR TRIP. UNIT 2 WAS IN MODE 1, POWER OPERATION, AT 94% POWER WHEN THIS INCIDENT OCCURRED. PREVIOUS MECHANICAL FAILURES OF BUSSMANN FNA FUSES IN 1986 AT MCGUIRE AND CATAWBA PROMPTED DESIGN ENGINEERING TO IDENTIFY SUITABLE REPLACEMENTS FOR ALL CLASS 1E APPLICATIONS. SCHEDULING OF NON-SAFETY FNA FUSE REPLACEMENT WAS DECIDED TO BE LEFT TO THE DISCRETION OF THE STATION AS THAT WAS CONSIDERED TO BE A RELIABILITY ISSUE. THIS INCIDENT HAS BEEN ATTRIBUTED TO A MANUFACTURING DEFICIENCY. THE FUSE WHICH CLOSED THE MAIN FEEDWATER CONTROL VALVE FAILED MECHANICALLY. THIS ALSO BEEN ATTRIBUTED TO A MANAGEMENT DEFICIENCY. ALTHOUGH THE MECHANICAL FAILURES ON THE BUSSMANN FNS FUSE HAD BEEN PREVIOUSLY IDENTIFIED, NON-SAFETY APPLICATIONS AND SUITABLE REPLACEMENTS WERE NOT IMPLEMENTED IN A TIMELY MANNER. FOLLOWING THIS INCIDENT, ALL BUSSMANN FNA FUSES ON BOTH UNITS, MAIN FEEDWATER CONTROL AND BYPASS CONTROL VALVES WERE REPLACED WITH LITTELFUSE FLQ FUSES.
414 | 4141989002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141989002R00.pdf | 1989-01-21 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 21 | POWER LEVEL - 021%. ON 1/21/89, AT 1848:40 HOURS, THE UNIT 2 REACTOR WAS MANUALLY TRIPPED DUE TO DECREASING LEVEL IN STEAM GENERATOR (S/G) B. THIS TRANSIENT WAS INITIATED BY THE MECHANICAL MALFUNCTION OF A TEMPERATURE TRANSMITTER FOR THE GENERATOR STATOR COOLING WATER (KG) SYSTEM. THE FAILED TRANSMITTER CAUSED 2KG5, GENERATOR STATOR COOLING TEMPERATURE CONTROL VALVE, TO REMAIN OPEN, BYPASSING THE HEAT EXCHANGER. THIS RESULTED IN A TURBINE RUNBACK ON HIGH KG TEMPERATURE. TURBINE RUNBACK WAS TERMINATED AUTOMATICALLY AT APPROX. 1838 HOURS. DURING THE SUBSEQUENT TRANSIENT, THE S/G LEVELS BEGAN A LARGE OSCILLATION. THE MAIN FEEDWATER PUMP TURBINE (CFPT) DISCHARGE PRESSURES BEGAN RISING DUE TO CF REGULATING VALVES CLOSING IN RESPONSE TO INCREASING S/G LEVELS. TO GAIN QUICKER RESPONSE OF CFPT 2A SPEED CONTROL, THE BALANCE OF PLANT OPERATOR SWAPPED FROM THE WESTINGHOUSE TO THE GE CONTROLLER. THIS SWAP WAS PERFORMED WITH A DEVIATION BETWEEN THE TWO CONTROLLERS. CFPT 2A AND CFPT 2B TRIPPED ON HI DISCHARGE PRESSURES. CONTROL OF THE CFPTS COULD NOT BE REGAINED. AS S/G B LEVEL WAS DECREASING TOWARDS THE LO LO LEVEL SETPOINT, THE REACTOR WAS MANUALLY TRIPPED AT APPROX. 21% POWER. PRIOR TO THIS INCIDENT, THE UNIT WAS OPERATING AT APPROX. 95% POWER. THIS INCIDENT HAS BEEN ATTRIBUTED TO AN EQUIPMENT MALFUNCTION.
414 | 4141989003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141989003R01.pdf | 1989-02-21 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Catawba 2 | P | WE | PO | 94 | POWER LEVEL - 094%. ON FEBRUARY 21, 1989, AT 0112 HOURS, IAE TECHNICIANS PLACED A JUMPER TO CHECK RELAY CONTACTS WHILE INVESTIGATING THE FAILURE OF THE '90 PERCENT OPEN' LIGHT TO ILLUMINATE DURING THE MAIN STEAM ISOLATION VALVE MOVEMENT TEST. THIS JUMPER RESULTED IN A SHORT CIRCUIT, CLOSING 2SM3, STEAM GENERATOR (S/G) 2C MAIN STEAM ISOLATION VALVE. THE RESULTING PRESSURE INCREASE IN S/G 2C CAUSED A REACTOR TRIP ON S/G LO LO LEVEL, AND CAUSED 2SV7, S/G 2C PORV, AND THREE S/G 2C CODE SAFETY RELIEF VALVES TO OPEN. THE OPENING OF THESE VALVES RESULTED IN A RAPID DECREASE IN STEAM LINE PRESSURE, WHICH RESULTED IN A SAFETY INJECTION ON LOW STEAM LINE PRESSURE (RATE COMPENSATED). THIS INCIDENT IS CLASSIFIED AS MANAGEMENT DEFICIENCY DUE TO THE LACK OF A POLICY FOR AN INDEPENDENT ASSESSMENT OF ACTIONS TO BE TAKEN UNDER TROUBLESHOOTING PROCEDURES, WITH CONTRIBUTING CAUSES OF EQUIPMENT MALFUNCTION DUE TO THE OPENING SETPOINT FOR 2SV7 BEING FOUND TO BE TOO HIGH, AND LACK OF ATTENTION TO DETAIL PRIOR TO JUMPER PLACEMENT. CORRECTIVE ACTIONS WILL INCLUDE PROVIDING A TROUBLESHOOTING REVIEW GUIDELINE. THE OPEN SETPOINT FOR 2SV7 WAS RECALIBRATED. UNIT 2 WAS IN MODE 1, POWER OPERATION, AT 94% POWER AT THE TIME OF THIS INCIDENT.
414 | 4141990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141990013R00.pdf | 1990-10-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 98 | On October 7, 1990, at approximately 1659 hours, with Unit 2 in Mode 1, Power Operation, and operating at 98% reactor power level, a Reactor (Rx) trip occurred due to low-low level in the 2D Steam Generator (S/G). The Reactor trip occurred after the 2A Main Feedwater Pump Turbine (CFPT-2A) tripped on indicated high discharge pressure which initiated a turbine runback. The Main Turbine ran back past its setpoint of 70% load; terminating at approximately 60% when the Rx tripped. Subsequent investigation of the event revealed that the CFPT-2A trip occurred due to an erroneous high discharge pressure signal which resulted from failed diaphragms in two of the three feedwater pump discharge pressure switches. Subsequent corrective actions included stabilizing the unit and replacing the defective pressure switches. This incident is attributed to an Equipment Failure. Additional corrective actions included review and investigation of the event to determine the root cause of the minor discrepancies noted during the post-trip review, development of a Rx Trip report, and replacement of the failed pressure switches.
414 | 4141991008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141991008R01.pdf | 1991-05-29 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Catawba 2 | P | WE | PO | 100 | On May, 29, 1991, at 0049 hours, Unit 2 was in Mode 1, Power operation, when a Reactor trip,occurred due to low flow on Loop 'B' of the Reactor Coolant (NC) System. The 6900 Volt switchgear feeder breaker, 2TB-3, for NC Pump 2B had tripped due to a spurious activation of a ground fault relay. The unit trip response was normal. Low - Low Steam Generator Level initiated the Auxiliary Feedwater (CA) System. The NC system was stabilized when control room operators reset the CA Auto Start and steam generator levels returned to normal. Power Delivery personnel determined that a Silicon Controlled Rectifier (SCR) within the relay had become electrically degraded, resulting in the spurious initiation of 2TB-3. The SCR was replaced and the relay was returned to service. This incident has been attributed to an Equipment Malfunction due to the degraded SCR. The remaining NC Pump ground fault relay SCRs were tested with no other failures detected. Corrective actions include testing a sample group of switchgear relays and to add SCR tests to the existing switchgear protective relay preventive maintenance activities.
414 | 4141992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141992001R00.pdf | 1992-01-15 | QR5 | Turbine Trip | [45 empty] | Catawba 2 | P | WE | PO | 100 | On January 15, 1992, a Unit 2 Turbine/Reactor Trip occurred at 02:14:18 hours during Main Turbine Hydraulic Oil (LH) System testing per PT/2/B/4250/02A, Main Turbine Weekly Trip Test. Unit 2 was in Mode 1, Power Operation, at 100% power at the time of the event. At 0210 hours, the auto start test of LH Pump 2A was successfully completed. At approximately 0212 hours, the auto start test of LH Pump 2B was initiated, and during the performance of this test, a Turbine Trip occurred due to Hydraulic Fluid Low Pressure. This resulted in a Reactor Trip because Reactor power was above 69% (the P-9 Setpoint). At the time of the event, the LH System temperature was 88 degrees F. At approximately 1600 hours, with the LH System temperature at approximately 107 degrees F, attempts to reproduce the event failed. This event is attributed to Possible Equipment Failure/Malfunction. Corrective actions included corrective maintenance and troubleshooting on the LH System, the addition of a two second time delay to the Turbine Trip Logic and a procedure enhancement. Planned corrective actions include improving the LH System temperature controlling setpoints and the computer alarm setpoints and completing the LH System troubleshooting.
414 | 4141992006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141992006R00.pdf | 1992-12-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 100 | On December 14, 1992 at 1533 hours with Unit 2 in Mode 1, Power Operation, a reactor trip occurred due to low-low level in Steam Generator (S/G) 2D. The reactor trip occurred after the 2A main feedwater pump (CFPT 2A) tripped during the weekly test of the pump's overspeed trip mechanism. The subsequent investigation determined that the momentary relaxation of the operator's hand while holding the trip lockout switch in the lockout position caused the pump to trip. The root cause of the CFPT 2A trip is attributed to its inadequate testability features. The testability features of the CFPTs and the test procedure are being evaluated to identify possible improvements to increase the reliability of the CFPT test. The Digital Feedwater System (DFS) initiated a runback but was unable to prevent the reactor from tripping. The initial investigation of the DFS did not identify any problems, therefore the root cause is unknown. Further investigation is being conducted to identify the root cause. The only significant anomalous behavior identified after the reactor trip was the Reactor Coolant (NC) System loop B average temperature (T-ave) indication. The T-ave indication caused the steam dump valves to open, but were closed only seconds after opening by the low T-ave P-12 interlock when the NC system temperature reached 553 degrees F. Process control cards were determined to be the cause of the T-ave indication problem and have been replaced.
414 | 4141993003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141993003R01.pdf | 1993-09-25 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 2 | P | WE | PO | 100 | On September 25, 1993 at 0937 hours, Unit 2 was operating in Mode 1, Power Operation, at 100 % power. Instrument and Electrical (IAE) personnel were preparing to perform a functional test on Liquid Waste (WL) Sump Pump control circuits, when they improperly opened link A-5 in cabinet 2ATC16. The proper link was A-5 in cabinet 2ATC14. When determining the actions to be taken, IAE did not notice that the diagram legend for link A-5 showed it to be in cabinet 2ATC14. Opening this link caused Main Steam Isolation Valve (MSIV) 2SM7 to close. The closing of the MSIV resulted in a Main Turbine/Reactor trip. This event is attributed to less than adequate self checking and independent verification. Corrective actions include communication of the event to all IAE personnel and revision of the troubleshooting procedure. Following the Turbine/Reactor trip at 1705 hours, Unit 2 was in Mode 3, Hot Standby, when Lo-Lo T-ave (P-12) actuated. P-12 actuated again at 2251 hours. In both events the Main Steam system was in an unusual alignment due to a valve problem. An additional steam load of warning the Main Feedwater Pump Turbines (CFPTs) for start with the unusual steam alignment caused T-ave to drop below 553 degrees F. The root cause of the P-12 events is the failure to adequately evaluate the impact of the unusual steam alignment on future evolutions. The corrective actions include communication of the events to all Operations personnel through an Operator Update and further communication of the details through operator proficiency training.
414 | 4141994003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141994003R00.pdf | 1994-07-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Catawba 2 | P | WE | PO | 100 | On July 10, 1994, at 1347 hours with Unit 2 in Mode 1, Power Operation, at 100% power, a turbine runback occurred following manual trip of a malfunctioning Main Feedwater Pump (CFP). Following the runback, a loss of Main Feedwater (CF) occurred, caused by one of the Steam Generator's (S/G) levels reaching the 'High-High' level ESFAS Interlock Setpoint. This resulted in ESFAS actions to trip the Main Turbine (MT), trip both CFPs, and isolate CF. Tripping of both CFP initiated an ESFAS signal to start both Motor Driven Auxiliary Feedwater Pumps. No automatic reactor trip signal was initiated because the unit was below the Reactor Trip on Turbine Trip Interlock Setpoint. The reactor was manually tripped at 1355 hours from 65% power. The unit was stabilized in Mode 3, Hot Standby, using 'Reactor Trip Response' Emergency Operating Procedure. The Root Cause of this event is attributed to the performance of the CF System following level recovery from low S/G levels. The initial trip investigation did not reveal any anomalies in the response of the S/G Level Control System. Following restart, additional information indicated the need for continuing evaluation of the S/G Level Control System performance. The performance of the S/G Level Control System transient response is a unit availability/reliability concern and not a nuclear safety issue. Corrective actions include evaluation of secondary systems interactions and responsiveness of the S/G Level Control System including the CF Control Valves.
414 | 4141994005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141994005R00.pdf | 1994-08-30 | QR8 | Spurious Reactor Trip | [45 empty] | Catawba 2 | P | WE | PO | 100 | On August 30, 1994 at 2130 hours, Unit 2 Reactor (Rx) Trip occurred while maintenance personnel were investigating the cause of the Reactor Trip/Safety Injection events recorder point being in alarm. Unit 2 was in Mode 1, Power Operation at 100% power. As a part of investigating the cause of the alarm a maintenance technician determined that it would be necessary to open a sliding link. The link as shown on the drawing used by the technician should have been in the Rx Trip/ Safety Injection events recorder point circuitry; however, it was actually in the Manual Safety Injection/Reactor Trip circuitry. This is the circuit that supplies 48 volts direct current (vdc) from the Solid State Protection System (SSPS) to the undervoltage trip coil for the Reactor Trip Breaker (RTB). When the link was opened, the 48vdc was removed from the RTB undervoltage (UV) trip coil resulting in an UV trip immediately followed by a shunt trip induced by the UV coil tripping and a Rx Trip. The subsequent investigation revealed that the wrong link was opened due to being incorrectly identified on the drawing. This event is attributed to less than adequate work practices in that self-checking was not properly applied because the error was not recognized during an earlier revision to the drawing. Corrective actions include revising the drawing, changes to the Engineering guideline for checking drawings, and evaluation of the troubleshooting process.
414 | 4141994006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141994006R00.pdf | 1994-09-13 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 2 | P | WE | PO | 100 | On September 13, 1994, at 1854 hours, Unit 2 was in Mode 1, Power Operation at 100% power, when an automatic Reactor/Turbine Trip occurred on Over Power Differential Temperature after the Main Steam Isolation Valve (MSIV) for 'C' Steam Generator closed unexpectedly. Following the trip, a main feedwater system isolation occurred as a result of a Reactor Trip with low Reactor Coolant System average temperature. Auxiliary Feedwater (CA) System motor driven and turbine driven pumps autostarted as expected, due to lo-lo Steam Generator levels. Letdown isolation occurred due to Pressurizer level decreasing below 17% as a result of cooldown caused by CA system operation. The root cause of this event is equipment failure. The MSIV closure was caused by the failure of an auxiliary relay in the control circuit for the MSIV. A short circuit occurred in a normally energized coil in a Series D26 Cutler Hammer relay. Corrective actions included replacing the relay and evaluating the failure rate of these types of relays to determine if similar relays needed to be replaced. Engineering concluded that this failure was a random failure. During the event, the control room operators entered the correct emergency response and abnormal procedures and performed the required steps to maintain the plant in a safe shutdown condition. All safety systems responded as designed to shutdown the Reactor and maintain it in a safe shutdown condition.
414 | 4141994007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141994007R00.pdf | 1994-10-18 | QR8 | Spurious Reactor Trip | [45 empty] | Catawba 2 | P | WE | PO | 100 | On October 18, 1994 at 0955 hours, with Unit 2 in Mode 1, Power Operation Trip, at 100% power, a Reactor Trip occurred. Two Instrumentation and Electrical (IAE) teams were performing independent tests on components of the Reactor Trip System when both trains of the Solid State Protection System (SSPS) received General Warning indications, causing the Reactor Trip Breakers to open. The Train B General Warning was expected; the Train A General Warning occurred unexpectedly when an IAE technician moved the SSPS Train A multiplexer test switch through 'Inhibit'. Document Use Practices, with a contributing cause of less than adequate Management Directions. Corrective actions for the Reactor Trip include communication of expectations for procedure use, philosophies for cross train work, and identifying uncompleted work to Work Control. Following the trip, with Unit 2 in Mode 3, Hot Standby, the Auxiliary Feedwater (CA) Pumps were secured and the discharge flow control valves for the Motor Driven Pumps (2A and 2B) were closed. On October 21 at 0435 hours, with Unit 2 in Mode 1 at 100% power, an operator discovered during a routine Control Board walkdown that the valves were closed. Subsequent investigation revealed the CA system had not been placed in standby readiness per the operating procedure after the system was secured. The root cause of this event is due to Written Communication, with a contributing cause of less than adequate Work Practices. Corrective actions for the closed CA valves include procedure revisions and clarifying/communicating a clear philosophy on operator responsibilities.
414 | 4141995001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141995001R01.pdf | 1995-02-21 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 2 | P | WE | PO | 100 | On February 21, 1995, at 2153 hours, Unit 2 was in Mode 1, Power Operation at 100%, when an automatic Reactor/Turbine Trip occurred on Over Power Differential Temperature after the Main Steam Isolation Valve (MSIV) for "B" Steam Generator (S/G) closed unexpectedly. Following the trip, a Main Feedwater System isolation occurred as a result of a reactor trip with low Reactor Coolant (NC) System average temperature (T-ave). Auxiliary Feedwater (CA) System motor driven and turbine driven pumps autostarted as expected due to lo-lo steam generator levels. Following reset of the CA System, NC T-ave increased above no-load setpoint allowing the Steam Dump System to actuate which resulted in S/G level decreasing below lo-lo level setpoint causing a second CA System turbine driven pump autostart. Engineering is evaluating transient data and will provide operations with recommendations concerning maintaining S/G levels following transients. The MSIV closure was caused by a degraded optical isolator within the control circuitry for the MSIV. Corrective Actions included testing and replacing degraded isolators in the control circuitry for all MSIVs and in critical applications in other systems for both units. The degraded optical isolators were returned to the vendor for testing. Engineering is evaluating reliability improvements of optical isolators and developing a trending program for optical isolators. All safety systems responded as designed to shutdown the Reactor and maintain it in a safe shutdown condition.
414 | 4141995004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141995004R00.pdf | 1995-04-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Catawba 2 | P | WE | PO | 100 | On April 27, 1995, at 1156 hours, Unit 2 was in Mode 1, Power Operation, at 100% power when a component in the 'A' Reactor Trip Breaker cubicle failed to change state during surveillance testing. As a result an invalid reactor trip indication to the Steam Generator (S/G) Level Control System occurred. The S/G Level Control System responded by reducing speed of both Main Feedwater (CF) Pumps to minimum. A reactor trip occurred when S/G levels decreased to the S/G Lo-Lo Level Reactor Trip Setpoint. The Auxiliary Feedwater (CA) System responded as expected to restore S/G levels. When average reactor coolant temperature (Tave) reached 553 degrees F, Engineered Safety Feature, Actuation System (ESFAS) Interlock, P-12, occurred, closing the steam dump valves. This event is attributed to component failure. Corrective actions include replacing the failed component. At 2345 hours, Unit 2 was in Mode 3, Hot Standby, with Tave at 557 degrees F, and S/G levels being maintained by CF. During checkouts to determine the failed component, a P-4 reactor trip signal was generated. CF Isolation occurred as a result of P-4 with Tave less than 564 degrees F. This event is attributed to work practices in that required procedures were not used. Corrective actions included appropriate management counseling of the involved individual.
414 | 4141995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141995005R00.pdf | 1995-05-01 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 14 | On May 1, 1995, at 1603 hours, Unit 2 was in Mode 1, Power Operation at 14%, when the Main Turbine tripped due to loss of both Main Feedwater (CF) System Pumps. Following the Turbine trip, the Reactor was manually tripped due to loss of Main Feedwater. A CF System isolation signal was generated as a result of a Reactor Trip with low Reactor Coolant (NC) System Average Temperature (T-ave). The Auxiliary Feedwater (CA) System motor driven pumps autostarted as expected due to loss of Main Feedwater. The CA System autostart caused NC System T-ave to cooldown below 553 degrees Fahrenheit which resulted in the Steam Dump System to isolate on a P- 12 permissive (Lo-Lo T-ave) to prevent excessive cooldown of the NC System. The root cause of this event is attributed to work practices, system alignment not properly verified by the Non-Licensed Operator (NLO) when aligning the Condensate System. Corrective Actions included communication by Operations Management of management expectations for human performance improvement to all Operations work groups and appropriate corrective action was taken with the NLO involved in this incident.
414 | 4141996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141996001R00.pdf | 1996-02-06 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Catawba 2 | P | WE | PO | 100 | Unit Status: Unit 2 - Mode 1 (Power Operation) at 100 percent power. Event Description: On February 6, 1996, at 1231 hours, ground faults on the resistor bushings for 2A Main transformer X phase potential transformer and 2B Main Transformer Z phase potential transformer resulted in a phase to phase fault. Protective relay actuation on both Main Transformers resulted in a loss of offsite power. The reactor tripped on Reactor Coolant Pump bus underfrequency. As a result of the blackout, 2A Emergency Diesel Generator started and sequenced on all required loads. 2B Emergency Diesel Generator was inoperable due to battery charger repairs, therefore B Train 4Kv Essential Bus did not automatically reenergize. Cold auxiliary feedwater being automatically supplied to the steam generators, in combination with the effects of various steam loads, resulted in a Low Steamline Pressure Safety Injection. At 1522 hours, B Train 4Kv Essential Bus was energized from 2B Emergency Diesel Generator. By 2000 hours, both 4Kv Essential Buses were being supplied from train related offsite power sources. <br /><br /> Event Cause: The root cause of the event is attributed to the application of the type of resistor bushings used. A deficiency lies in the use of these resistor bushings in a vertical orientation at the bottom of vertical branch-lines of the Isolated Phase Bus ducting leading to the potential transformers. The outdoor location and lack of air flow within this portion of the ducting, is conducive to moisture intrusion and corrosion. A contributing factor was the lack of adequate preventative maintenance to prevent moisture intrusion/condensation problems. <br /><br /> Corrective Action: All resistor bushings in this application were replaced on both Catawba units with bushings having external resistors. The current preventative maintenance programs for the IPB system and transformer yard equipment will be enhanced to ensure continued equipment reliability. Enhancements should include measures to protect against the effects of moisture and condensation.
414 | 4141997005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141997005R00.pdf | 1997-06-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Catawba 2 | P | WE | PO | 100 | Unit Status: Unit 2- mode 1, power operation, 100% power. Event Description: On June 26, 1997, an automatic reactor trip occurred while in mode 1. While searching for an electrical ground, the reactor coolant pump lost power when its associated bus isolated. Bus isolation and the loss of the reactor coolant pump resulted in low flow in one loop of the reactor coolant system and subsequent automatic trip of the reactor. A faulty push button caused the electrical ground.Root Cause: The root cause of the reactor trip was equipment failure of a Cutler-Hammer E30JY5 close/trip push button switch.Corrective Action: Maintenance and Engineering found and replaced the defective switch. The failed switch has been sent to Duke Power Testing Lab to determine cause of failure. Engineering will evaluate the results of the testing and determine any additional corrective actions necessary.
414 | 4141997006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141997006R00.pdf | 1997-07-26 | QL5 | Partial Closure of MSIVs | [45 empty] | Catawba 2 | P | WE | PO | 100 | Unit Status: Unit 2 was in Mode 1, Power Operation, at 100% power. Event Description: On July 26, 1997, at 2223 hours, and on August 17, 1997, at 0130 hours Unit 2 was manually tripped to preclude an automatic trip following closure of Main Steam Isolation Valve (MSIV) 2SM-1. During both events all safety systems responded as designed. Auxiliary Feedwater (CA) automatically started upon receipt of a low steam generator (S/G) level signal to maintain S/G level. Emergency Core Cooling System (ECCS) actuation was not necessary and did not occur. A second CA autostart occurred during the August 17 event when the level in the S/G isolated by 2SM-1 closure inadvertently decreased below the low level setpoint.Root Cause: The cause of both manual reactor trips is attributed to failure of a digital optical isolator (DOI) within the control circuitry of MSIV 2SM-1. The July event involved the "A" train circuitry and the August event involved the "B" train circuitry.Corrective Action: Operations personnel correctly diagnosed each event and tripped, evaluated and stabilized Unit 2 per station procedures. Failed and suspect DOIs have been replaced. An improved method of testing DOIs for the identified failure has been developed. All DOIs in MSIV applications have been tested and will receive additional testing. All DOIs in critical control applications with the same model number as the DOIs noted in this LER and having AC input and DC output will be tested. Additional failure analysis by vendors is being performed to identify the failure mechanism internal to the DOI. Engineering will review the results of the failure analysis and recommend additional corrective actions as necessary.
414 | 4141999006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4141999006R01.pdf | 1999-12-30 | QR8 | Spurious Reactor Trip | [45 empty] | Catawba 2 | P | WE | PO | 100 | On December 30, 1999 at 1821 hours with Catawba Unit 2 operating in Mode 1 "Power Operation" at 100% power, a reactor trip occurred. The cause of the reactor trip was actuation of the turbine trip instrumentation inputs to the Solid State Protection System (SSPS) logic. This was due to an electrical ground within an electrical connector on the normally energized Turbine Electrical Trip Solenoid Valve (ETSV). This caused the normally energized ETSV to de-energize and dump Emergency Trip System (ETS) pressure, resulting in the pressure switches on the ETS header sensing pressure dropping below their set point and thus sending a signal that the turbine was tripped to the SSPS. The SSPS then initiated a reactor trip. All systems responded as designed to shut down the reactor and maintain it in a safe shutdown condition. This event is being reported as an automatic actuation of the reactor protection system. A failure analysis performed on the connector determined that the root cause of the problem was a misapplication of the connector insert insulating material, which is made of neoprene. This connector will be replaced with a high temperature model.
414 | 4142000003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4142000003R01.pdf | 2000-06-05 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Catawba 2 | P | WE | PO | 100 | On June 5, 2000 at 1237 hours with Catawba Unit 2 operating in Mode 1 "Power Operation" at 100% power, a reactor trip occurred. Rainwater entered the Turbine Building and affected control of Main Feedwater Pump 2B. A feedwater transient occurred which resulted in a reactor trip. The root cause of this aspect of the event is inadequate oversight of a Turbine Building roof modification. On June 8, 2000 from 0914 to 1414 hours with Unit 2 in Mode 1 at power levels ranging from 17% to 31%, there were eight separate occurrences prohibited by Technical Specification (TS) 3.3.2. This involved working on Main Feedwater Pump 2B without having it in the "tripped" condition as required by the TS .The root cause of this aspect of the event is inadequate communications between station groups. Corrective actions include measures to ensure that excessive rainfall can drain to the outside of the Turbine Building, instituting housekeeping controls for roofing work, defining and documenting oversight responsibilities of the job sponsor for roofing modifications, procedure revisions to clarify requirements for installation of jumpers and development of measures to address inadequate communications between station groups.
414 | 4142001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4142001003R00.pdf | 2001-12-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Catawba 2 | P | WE | PO | 100 | On December 7, 2001 at 2350 hours with Catawba Unit 2 operating in Mode 1 "Power Operation" at 100% power, an automatic reactor trip occurred. The reactor trip was caused by low flow in the D loop when the 2D reactor coolant pump (RCP) 6900VAC feeder breaker opened in response to protective relay actuation caused by an electrical fault internal to the RCP motor. The electrical fault in the RCP motor also caused protective relaying to open the normal feeder breaker supplying power to the essential bus 2ETB, creating an undervoltage condition on 2ETB. The associated emergency diesel generator (EDG) automatically started and powered the bus and required equipment as designed. The 2B motor-driven and the turbine driven auxiliary feedwater pumps automatically started in response to the 2ETB blackout as designed. The 2A motor-driven auxiliary feedwater pump automatically started in response to lo lo water level in the 2D steam generator (S/G). All systems responded as designed to shut down the reactor and maintain it in a safe shutdown condition. Corrective actions included replacing the failed 2D RCP motor and verification of proper operation of the protective relaying associated with the breakers that opened. The RCP motor failure was determined to be a "turn-to-turn" failure of a single coil. The damaged coil is on the line end of the stator core and appears to be the first coil in the Z-phase (T3) coil group. A possible cause of the coil failure is a manufacturing defect of the magnet wire.
414 | 4142004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4142004002R00.pdf | 2004-10-28 | QR3 | Reactivity Control Imbalance | [45 empty] | Catawba 2 | P | WE | PO | 100 | On October 28, 2004, at 0052 hours, with Catawba Unit 2 operating in Mode 1 at 100% power, all four control rods from Shutdown Bank D inserted into the core. Consequently, the Operators responded by manually tripping the reactor. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. All plant equipment operated as expected.The most probable cause of this event was an intermittent failure of a circuit card in the rod control system. Corrective actions for this event included replacing the suspect circuit card and sending the card to the vendor for further analysis. This event was of no significance with respect to the health and safety of the public.
414 | 4132006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4132006001R00.pdf | 2006-05-20 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Catawba 2 | P | WE | PO | 100 | On 05/20/06, at 1401 hours, both Catawba units tripped automatically from 100% power following a loss of Offsite Power (LOOP) event. The event began when a fault occurred internal to a current transformer associated with one of the switchyard power circuit breakers. A second current transformer failure, along with the actuation of differential relaying associated with both switchyard busses, cleared both busses and separated the units from the grid. A Notification of Unusual Event (NOUE) was declared at 1414 hours. The Emergency Response Organization was electively activated. Both emergency diesel generators on each unit started automatically and supplied their required blackout and essential loads as designed. All three auxiliary feedwater pumps on each unit started automatically and fed the steam generators as designed. Decay heat was removed via natural circulation of the reactor coolant system, with steam relief through the steam generator power operated relief valves. Both units were stabilized in Mode 3 with cooldown activities in progress. Offsite power was restored to all 6900V busses on both units by 05/20/06 at 2041 hours. The NOUE was subsequently terminated on 05/21/06 at 0140 hours.The root cause analysis for this event determined that in 1981, certain switchyard relay tap setting changes were not implemented at Catawba. Power Delivery documentation was subsequently erroneously updated to indicate that the changes had been made. Corrective actions for this event will include developing an enhanced process to ensure correct configuration management for the Catawba protective relay settings. The health and safety of the public were not adversely affected by this event.
416 | 4161987009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161987009R02.pdf | 1987-06-29 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON JUNE 29, 1987 AGASTAT RELAY N62-R33 SUSTAINED AN INTERMITTENT FAILURE WHICH CAUSED THE MAIN STEAM INLET VALVE (N62-FOO1B) TO STEAM JET AIR EJECTOR (SJAE) 'B' TO CLOSE. THE CLOSURE OF THIS VALVE CAUSED A LOSS OF CONDENSER VACUUM RESULTING IN A MAIN TURBINE TRIP AND REACTOR SCRAM. THE CLOSURE OF VALVE N62-FOO1B PREVENTED THE SJAE FROM REMOVING NON-CONDENSABLE GASES FROM THE MAIN CONDENSER. IN ADDITION, MOTOR OPERATED VALVE N62-FO03B FAILED TO CLOSE DUE TO A FAILED RELAY ALLOWING REVERSE FLOW THROUGH THE OFF-GAS SYSTEM BACK INTO THE CONDENSER. THESE TWO FAILURES COMBINED TO DECREASE MAIN CONDENSER VACUUM RESULTING IN A MAIN TURBINE TRIP AND REACTOR SCRAM ON THE TURBINE STOP VALVE FAST CLOSURE SIGNAL. FOLLOWING THE SCRAM THE SJAES WERE SECURED WHICH CLOSED THE N62-FO03B VALVE AND TERMINATED THE LOSS OF VACUUM EVENT. VACUUM STABILIZED AT APPROXIMATELY 21 INCHES MERCURY. DURING THE SCRAM RECOVERY, A DIVISION II GROUP 8 AUTOMATIC ISOLATION OCCURRED WHEN OPERATORS PREPARED TO PLACE THE REACTOR WATER CLEANUP (RWCU) SYSTEM INTO THE BLOWDOWN MODE OF OPERATION. SYSTEMS ENERGY RESOURCES, INC. IS CONTINUING TO PURSUE A MEANS TO PRECLUDE THE OCCURRENCE OF UNPLANNED RWCU DIFFERENTIAL FLOW ISOLATIONS.
416 | 4161987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161987012R00.pdf | 1987-08-06 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON AUGUST 6, 1987 AT APPROXIMATELY 0625, THE REACTOR SCRAMMED ON A TURBINE CONTROL VALVE FAST CLOSURE SIGNAL. THE EVENT WAS INITIATED BY A BACKUP PROTECTION SCHEME RELAY LOCATED IN THE SWITCHYARD CONTROL HOUSE. THE RELAY IS DESIGNED TO OPEN THE GENERATOR OUTPUT BREAKERS ONLY WHEN THE GENERATOR IS OFF-LINE. AN INVESTIGATION REVEALED THAT MOISTURE HAD COLLECTED IN THE TERMINAL CABINETS AND APPARENTLY SHORTED AN INTERLOCK SWITCH WHICH CAUSED THE RELAY TO ACTUATE AND TRIP THE TWO MAIN GENERATOR OUTPUT CIRCUIT BREAKERS. THIS RESULTED IN A TURBINE CONTROL VALVE FAST CLOSURE SCRAM INITIATION. THE SAFETY RELIEF VALVE LOW-LOW SET LOGIC FUNCTIONED PROPERLY TO CONTROL REACTOR PRESSURE, LIFTING VALVES B21-F051D, F051B, F047G, F051A, F047D, AND F051F. REACTOR PRESSURE REACHED A MAXIMUM OF 1107 PSIG. SINCE THE BACKUP PROTECTION SCHEME RELAY IS USED ONLY WHEN THE GENERATOR IS OFF-LINE, IT WAS REMOVED FROM SERVICE AND WILL REMAIN OUT OF SERVICE UNTIL THE NEXT REFUELING OUTAGE. AT THAT TIME IT WILL BE THOROUGHLY CHECKED AND ANY PROBLEMS WILL BE CORRECTED AS REQUIRED. PLANT RESTART WAS DELAYED DUE TO UNRELATED PROBLEMS DESCRIBED IN LER 87-013-0. THE PLANT REACHED CRITICALITY ON AUGUST 9, 1987, AT APPROXIMATELY 1324. SYNCHRONIZATION OCCURRED ON AUGUST 10, 1987, AT APPROXIMATELY 1225.
416 | 4161988002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988002R00.pdf | 1988-01-10 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 95 | POWER LEVEL - 095%. ON JANUARY 10, 1988 THE 'B' PHASE GENERATOR OUTPUT TRANSFORMER FAILED CAUSING THE GENERATOR OUTPUT BREAKERS TO OPEN ON A TRANSFORMER DIFFERENTIAL TRIPPING THE MAIN TURBINE/GENERATOR. THE REACTOR AUTOMATICALLY SCRAMMED ON THE TURBINE CONTROL VALVE FAST CLOSURE SIGNAL. AN INVESTIGATION DETERMINED THAT A WINDING FAULT OCCURRED ON THE HIGH VOLTAGE SIDE OF THE TRANSFORMER. THE 'B' PHASE TRANSFORMER WAS DISCONNECTED AND A SPARE TRANSFORMER CONNECTED TO THE 'B' PHASE. ELECTRICAL TESTS AND OIL SAMPLES OF THE 'A' PHASE, 'C' PHASE, AND THE SPARE TRANSFORMERS INDICATED ACCEPTABLE INSULATION LEVELS AND OIL CHARACTERISTICS. PREVIOUS TEST RESULTS OF THE 'B' PHASE TRANSFORMER WERE REVIEWED TO DETERMINE IF THE FAILURE COULD HAVE BEEN ANTICIPATED. BASED ON THE DATA AVAILABLE, A PRELIMINARY INVESTIGATION CONCLUDED THAT THE FAULT COULD NOT HAVE BEEN ANTICIPATED OR PREVENTED AND THAT THE EXISTING PREVENTATIVE MAINTENANCE PROGRAM OF OIL SAMPLING AND ANALYSIS IS ADEQUATE. ALTHOUGH SYSTEM ENERGY RESOURCES, INC. BELIEVES ITS CURRENT PROGRAM IS ADEQUATE, AN INDEPENDENT REVIEW BY HIGH VOLTAGE SPECIALISTS WILL BE PERFORMED TO SEE IF ANY ENHANCEMENT TO THE CURRENT PROGRAM WOULD BE BENEFICIAL.
416 | 4161988006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988006R00.pdf | 1988-01-20 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 97 | POWER LEVEL - 097%. ON 1/20/88 AT 0439 THE REACTOR AUTOMATICALLY SCRAMMED ON LOW REACTOR WATER LEVEL (LEVEL 3, +11.4 INCHES). THE LOW REACTOR WATER LEVEL OCCURRED WHEN THE CONDENSATE AND CONDENSATE BOOSTER PUMPS TRIPPED RESULTING IN LOSS OF FEEDWATER FLOW. THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM WAS MANUALLY INITIATED AND THE HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM AUTOMATICALLY INITIATED ON LOW LOW REACTOR WATER LEVEL (LEVEL 2, -41.6 INCHES) AND INJECTED TO THE REACTOR VESSEL. A CONDENSER CIRCULATING WATER MANWAY COVER LEAKED AND SPRAYED WATER ON THE HOTWELL LOW LEVEL SWITCHES CAUSING A FALSE LOW HOTWELL LEVEL SIGNAL. THE LEAK WAS FROM A RUBBER GASKET WHICH SLIPPED FROM ITS GROOVE ON A MANWAY COVER. THE GASKET WAS REPLACED AND GLUED IN PLACE PREVENTING SLIPPAGE BETWEEN THE COVER AND THE MATING SURFACE. PROTECTIVE SHIELDS WERE INSTALLED AROUND THE LEVEL SWITCHES TO PROTECT THEM AGAINST WATER SPRAY EVENTS.
416 | 4161988010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988010R00.pdf | 1988-03-15 | QR3 | Reactivity Control Imbalance | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON MARCH 15, 1988 A SURVEILLANCE TEST ON THE REACTOR WATER LEVEL INSTRUMENTATION WAS BEING RUN. A PART OF THIS SURVEILLANCE TEST INSERTED A PLANNED HALF SCRAM SIGNAL OF REACTOR PROTECTION SYSTEM (RPS) 'B' LOGIC. AT THIS TIME 29 CONTROL RODS WERE FULLY INSERTED INTO THE REACTOR CORE. THE INSERTION OF THE 29 RODS CAUSED A RAPID POWER DECREASE AND A CORRESPONDING REDUCTION IN THE STEAM VOID GENERATION RATE. THE REDUCTION OF STEAM VOLUME CAUSED THE REACTOR WATER LEVEL TO DECREASE TO THE SCRAM TRIP SETPOINT OF +11.4 INCHES WHICH INITIATED A FULL REACTOR SCRAM AT 0950. ALL PLANT SYSTEMS RESPONDED TO THE EVENT AS DESIGNED. THE MINIMUM REACTOR WATER LEVEL REACHED DURING THE EVENT WAS -2 INCHES WHICH IS 164.7 INCHES ABOVE THE TOP OF ACTIVE FUEL. NO EMERGENCY CORE COOLING SYSTEMS ACTUATED OR INJECTED DURING THE EVENT. AS A RESULT OF THE INVESTIGATION OF THIS EVENT IT WAS DISCOVERED THAT A LOOSE CONNECTION IN AN RPS TERMINAL BOX HAD DEENERGIZED THE 'A' SCRAM PILOT SOLENOIDS OF THE 29 CONTROL RODS. THIS PLACED THE RODS IN A HALF SCRAM CONDITION. THIS CONDITION WAS NOT DETECTABLE SINCE NO ALARM OR ABNORMAL STATUS WAS INDICATED. THE SURVEILLANCE TEST INITIATED RPS 'B' LOGIC TRIP IN CONJUNCTION WITH THE DEENERGIZED 'A' SOLENOIDS WHICH PRODUCED A FULL SCRAM FOR THE 29 RODS. THE CONNECTION IN THE TERMINAL BOX WAS CLEANED AND TIGHTENED.
416 | 4161988012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988012R02.pdf | 1988-08-15 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON 8/15/88 AT 1553 HRS THE PLANT TRIPPED ON AVERAGE POWER RANGE MONITORS (APRM) NEUTRON FLUX HIGH SIGNAL. AN ELECTRICAL STORM WITH LIGHTNING STRIKES WAS OCCURRING IN THE GENERAL SITE AREA. SEVERAL APRM CHANNELS MOMENTARILY SPIKED HIGH DUE TO AN INHERENT CONDITION WITHIN THE PLANT ELECTRICAL GROUNDING SYSTEM WHICH TRANSMITTED THE VOLTAGE SPIKES TO THE APRMS. ALL PLANT SYSTEMS RESPONDED AS DESIGNED. THE APRM CABINETS WERE VISUALLY INSPECTED FOR GENERAL CONDITION AND FOR THE PRESENCE OF GROUNDING STRAPS. NO OBVIOUS DISCREPANCIES WERE OBSERVED. AN ENGINEERING TASK FORCE WAS ASSEMBLED TO INVESTIGATE THE ROOT CAUSE AND RECOMMEND CORRECTIVE ACTIONS TO ELIMINATE THE PROBLEM. RESULTS OF A GENERAL ELECTRIC INSPECTION TEAM ATTRIBUTED THE SPIKE TO A GROUNDING STRAP FOR THE PLANT SECURITY FENCE LOCATED ON THE ROOF OF THE TURBINE AND CONTROL BLDGS. THE GROUNDING STRAP WAS ROUTED ACROSS THE ROOF AND DOWN THE SIDE OF THE CONTROL BLDG AND THEN ACROSS THE ROOF OF THE AUX. BLDG IN CLOSE PROXIMITY TO THE SIGNAL CABLES OF THE APRM CHANNELS THAT SPIKED. IT THEN TIED IN WITH ANOTHER GROUNDING STRAP WHICH IS TIED TO THE PLANT GROUNDING MAT. THE GROUNDING STRAP HAS BEEN RELOCATED TO A NON-SENSITIVE AREA TO PREVENT INTERFERENCE WITH THE APRMS. THE SCRAM FREQUENCY REDUCTION COMMITTEE WILL CONTINUE TO EVALUATE GES RECOMMENDATION FOR PLANT LIGHTNING PROTECTION UNTIL A FINAL RESOLUTION IS ACHIEVED.
416 | 4161988013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988013R00.pdf | 1988-09-05 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 5, 1988 A SECONDARY CONTAINMENT ISOLATION VALVE FAILED TO CLOSE WITHIN THE REQUIRED TIME LIMIT DURING A QUARTERLY SURVEILLANCE. THE REDUNDANT ISOLATION VALVE WAS CLOSED AND AN EQUIPMENT CLEARANCE WAS ISSUED TO DEACTIVATE IT IN ACCORDANCE WITH THE TECHNICAL SPECIFICATION LIMITING CONDITION FOR OPERATION. A POWER PANEL BREAKER WAS OPENED TO DEACTIVATE THE REDUNDANT VALVE. THE BREAKER POWERED 17 OTHER ISOLATION VALVES, INCLUDING AN AUXILIARY BUILDING ISOLATION VALVE AND A CONTAINMENT ISOLATION VALVE IN THE INSTRUMENT AIR SYSTEM. WHEN THE BREAKER WAS OPENED THESE VALVES CLOSED. THE ISOLATED INSTRUMENT AIR HEADER BEGAN TO DEPRESSURIZE, RESULTING IN MULTIPLE CONTROL ROD DRIFTS. OPERATORS INITIATED A MANUAL SCRAM IN ACCORDANCE WITH THE OFF-NORMAL EVENT PROCEDURE; HOWEVER, AN AUTOMATIC SCRAM ON SCRAM DISCHARGE VOLUME HIGH WATER LEVEL WAS RECEIVED JUST PRIOR TO THE MANUAL ACTUATION. CORRECTIVE ACTIONS INCLUDE DISCIPLINARY ACTION, TRAINING OF PERSONNEL, INSTALLING CAUTION LABELS ON ESF POWER PANELS WHICH FEED ISOLATION VALVES, AND DEVELOPING A CONTROLLED DOCUMENT FOR ASSESSING THE IMPACT OF OPERATING POWER PANEL BREAKERS.
416 | 4161988019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161988019R01.pdf | 1988-10-10 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON OCTOBER 10, 1988 AT 1058 THE HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM (EIIS SYSTEM CODE: BG) AND THE HPCS EMERGENCY DIESEL GENERATOR (EIIS SYSTEM CODE: EK) AUTOMATICALLY INITIATED WHEN AN OPERATOR KEYED A RADIO IN THE VICINITY OF THE LOW LEVEL INSTRUMENT TRANSMITTERS. REACTOR WATER LEVEL REACHED +45 INCHES (APPROXIMATELY 10 INCHES ABOVE THE NORMAL OPERATING RANGE). AT THAT POINT THE SHIFT SUPERINTENDENT DIRECTED OPERATORS TO SECURE THE HPCS PUMP. OPERATORS SECURED THE HPCS PUMP AT +47.4 INCHES AND TOOK MANUAL CONTROL OF FEEDWATER FLOW TO AVOID A HIGH LEVEL TRIP AS LEVEL REACHED +50 INCHES. THE REACTOR WATER LEVEL PEAKED AT APPROXIMATELY +52.5 INCHES CAUSING A SINGLE RPS INSTRUMENT CHANNEL TO TRIP ON REACTOR HIGH WATER LEVEL WHICH COMPLETED HALF OF THE SCRAM LOGIC. OPERATORS MANUALLY INCREASED FEEDWATER FLOW AS LEVEL BEGAN TO DECREASE; HOWEVER, WITHIN 10 SECONDS OF THE HIGH LEVEL CHANNEL TRIP REACTOR WATER LEVEL DROPPED TO THE LOW LEVEL SCRAM SETPOINT OF +11.4 INCHES INITIATING A REACTOR SCRAM. OPERATORS CONTINUED TO INCREASE FEEDWATER FLOW AND MANUALLY INITIATED THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM (EIIS SYSTEM CODE: BN) TO RESTORE WATER LEVEL. RADIO TRANSMISSION ON THE 139 FOOT ELEVATION AREA OF CONTAINMENT HAS BEEN PROHIBITED.
416 | 4161989006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161989006R00.pdf | 1989-05-05 | QP5 | Excessive Feedwater Flow | [45 empty] | Grand Gulf | B | GE | SU | 5 | POWER LEVEL - 005%. ON MAY 5, 1989 AT 0948 HOURS, THE REACTOR TRIPPED ON LOW REACTOR WATER LEVEL. A CONTROLLED PLANT SHUTDOWN WAS IN PROGRESS WHEN OPERATORS EXPERIENCED LEVEL CONTROL PROBLEMS. ATTEMPTS TO CONTROL THE VESSEL OVERFEED CONDITION WERE UNSUCCESSFUL AND THE OPERATING REACTOR FEED PUMP TURBINE (RFPT) TRIPPED ON HIGH WATER LEVEL. SUBSEQUENT ATTEMPTS TO RESTART THE TRIPPED RFPT AND RESTORE LEVEL WERE UNSUCCESSFUL. THE CAUSE OF THE VESSEL OVERFEED WAS DETERMINED TO BE THE FEEDWATER HEATER OUTLET VALVES INDICATING CLOSED WHEN IN FACT THEY WERE SLIGHTLY OPEN. THE RFPT TRIP RESET LOGIC MISLED THE OPERATORS WHEN THEY ATTEMPTED TO RESTART THE TRIPPED RFPT. DESIGN CHANGES TO THE FEEDWATER CONTROL LOGIC ARE BEING EVALUATED TO PREVENT RECURRENCE. ALSO TRAINING ON THE EVENT WILL BE CONDUCTED TO MAKE OPERATORS AWARE OF THE LESSONS LEARNED. ALL PLANT SAFETY SYSTEMS PERFORMED AS EXPECTED. THE MINIMUM WATER LEVEL REACHED WAS APPROXIMATELY 14 FEET ABOVE THE TOP OF ACTIVE FUEL. ALL EMERGENCY CORE COOLING SYSTEMS WERE OPERABLE AND AVAILABLE TO RESPOND IF NECESSARY.
416 | 4161989010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161989010R00.pdf | 1989-07-22 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON JULY 22, 1989, A SEVERE ELECTRICAL STORM PASSED OVER GRAND GULF NUCLEAR STATION. DURING THE STORM, THE REACTOR AUTOMATICALLY SCRAMMED DUE TO A HIGH NEUTRON FLUX SIGNAL ON THE AVERAGE POWER RANGE MONITORS (APRMS). ADDITIONALLY, A SPIKE TO THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM LOGIC CAUSED RCIC TO AUTOMATICALLY ACTUATE AND INJECT INTO THE REACTOR VESSEL. REACTOR WATER LEVEL DECREASED TO -15 INCHES AND WAS RAISED TO THE LEVEL 8 HIGH LEVEL TRIP (+53.5 INCHES) IN APPROXIMATELY 2 MINUTES. A CHANNEL CHECK OF APRM INDICATIONS WAS PERFORMED DURING PLANT RESTART ON JULY 2 3, 1989 TO CONFIRM PROPER RESPONSE. NO ABNORMALITIES WERE OBSERVED. SYSTEM ENERGY REQUISITIONED A SPECIALIST IN LIGHTNING PROTECTION TO PERFORM A PLANT SURVEY AND STUDY OF THE EXISTING PLANT LIGHTNING PROTECTION SYSTEM. THE CONTRACTOR HAS SUBMITTED PROPOSALS TO PROVIDE LIGHTNING DISSIPATION ARRAYS ON VULNERABLE STRUCTURES. SYSTEM ENERGY IS PRESENTLY EVALUATING IMPLEMENTATION METHODS AND CONSTRUCTING A SCHEDULE FOR IMPLEMENTATION . CURRENT PROGRESS INDICATES THAT IMPLEMENTATION WILL LIKELY BE COMPLETED BY DECEMBER 31, 1989. IN ANY CASE, IMPLEMENTATION WILL BE COMPLETED NO LATER THAN THE STARTUP FROM THE FOURTH REFUELING OUTAGE (RF04).
416 | 4161989012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161989012R00.pdf | 1989-08-14 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON 8/14/89, A MAIN CONDENSER EXPANSION JOINT FAILED CAUSING CONDENSER VACUUM TO DECREASE. THE MAIN TURBINE TRIPPED ON CONDENSER LOW VACUUM RESULTING IN A REACTOR SCRAM DUE TO THE FAST CLOSURE OF THE MAIN TURBINE STOP AND CONTROL VALVES. DURING THE COURSE OF THE EVENT TWO SUBSEQUENT RPS ACTUATIONS OCCURRED ON LOW REACTOR WATER LEVEL SIGNALS. A MAIN STEAM ISOLATION VALVE (MSIV) ISOLATION SIGNAL WAS ACTUATED ON LOW CONDENSER VACUUM. THE REACTOR CORE ISOLATION COOLING SYSTEM WAS MANUALLY INITIATED TO CONTROL REACTOR WATER LEVEL. NO ECCS WERE INITIATED MANUALLY OR AUTOMATICALLY. ALL CONTROL RODS FULLY INSERTED WITH THE EXCEPTION OF CONTROL ROD 32-45 WHICH STOPPED AT POSITION 08. ALL MSIVS PROPERLY CLOSED WITH THE EXCEPTION OF B21-F022B WHICH CLOSED APPROXIMATELY 35 MINUTES FOLLOWING A MANUAL CLOSURE SIGNAL. COMPONENTS IN THE CONTROL ROD HYDRAULIC CONTROL UNIT WERE REPLACED TO CORRECT THE CONTROL ROD MALFUNCTION. THE FAILURE MECHANISM OF THE MSIV WAS DETERMINED TO BE GENERIC TO OTHER INSTALLED MSIVS AND IS REPORTED SEPARATELY IN LER 89-013. A 3 FOOT SECTION OF THE CONDENSER EXPANSION BELT HAD TORN HORIZONTALLY NEAR THE LOWER RETAINING CLAMPS. THE HEMP REINFORCEMENT FIBERS HAD APPARENTLY DEGRADED DUE TO MOISTURE INTRUSION THROUGH THE RUBBER. THE BELTS ON ALL 3 CONDENSER SECTIONS WERE REPLACED WITH BELTS USING A POLYESTER REINFORCEMENT FIBER.
416 | 4161989016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161989016R00.pdf | 1989-11-07 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | POWER LEVEL - 100%. ON NOVEMBER 7, 1989, A SEVERE THUNDER STORM WAS IN PROGRESS IN THE SITE VICINITY. DURING THE STORM, LIGHTNINQ STRUCK THE SITE CAUSINQ A SPIKE ON PLANT INSTRUMENTATION. THE REACTOR AUTOMATICALLY SCRAMMED DUE TO THE SPIKE SIMULATING A HIGH FLUX SIGNAL ON THE AVERAGE POWER RANGE MONITORS (APRMS). THE SPIKE CAUSED TWO HIGH PRESSURE CORE SPRAY (HPCS) LOW WATER LEVEL CHANNELS TO TRIP. HPCS DID NOT INITIATE DUE TO THE SHORT DURATION OF THE SPIKE. ALSO, REACTOR CORE ISOLATION COOLING (RCIC) RECEIVED AN INITIATION SIGNAL, BUT DID NOT INJECT DUE TO THE TRIP THROTTLE VALVE BEING IN THE CLOSED POSITION IN PREPARATION FOR AN I&C SURVEILLANCE. REACTOR WATER LEVEL DECREASED TO -18 INCHES AND WAS SUBSEQUENTLY RAISED TO 51 INCHES BY THE FEEDWATER SYSTEM. A FUNCTIONAL CHECK OF APRM INDICATIONS AND HPCS TRIP UNITS WAS PERFORMED PRIOR TO PLANT STARTUP. NO ADVERSE EFFECTS WERE OBSERVED. A DESIGN CHANGE PACKAGE WAS ISSUED TO INSTALL A LIGHTNING DISSIPATION SYSTEM ON VULNERABLE STRUCTURES. IMPLEMENTATION OF THE SYSTEM IS DUE TO BE COMPLETED BY STARTUP FROM THE FOURTH REFUELING OUTAGE (RF04).
416 | 4161989019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161989019R00.pdf | 1989-12-30 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Grand Gulf | B | GE | PO | 83 | POWER LEVEL - 083%. ON DECEMBER 30, 1989, A TOTAL LOSS OF PLANT SERVICE WATER (PSW) WAS EXPERIENCED DUE TO A LOSS OF POWER TO THE SUPPLY WELLS. REACTOR POWER WAS REDUCED BY DECREASING RECIRCULATION FLOW THROUGH THE REACTOR CORE AND A REACTOR SHUTDOWN SEQUENCE WAS COMMENCED. WHILE REDUCING REACTOR POWER, THE OPERATORS DETERMINED THAT PSW WOULD NOT BE READILY RESTORED AND THE REACTOR WAS MANUALLY SCRAMMED. THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM WAS INITIATED FOR REACTOR VESSEL LEVEL CONTROL. THE MAIN STEAM LINE ISOLATION VALVES WERE CLOSED IN ACCORDANCE WITH PROCEDURES. THIS ACTION CAUSED A HIGH PRESSURE SCRAM SIGNAL AND AN ATWS/ARI RPT ACTUATION. STANDBY SERVICE WATER (SSW) WAS INITIATED AND PROVIDED COOLING FOR THE COMPONENT COOLING WATER HEAT EXCHANGERS AND THE DRYWELL CHILLERS. THE SSW BASIN LEVEL DROPPED BELOW THE TECH. SPEC. LIMIT DUE TO LEAKAGE OF SSW INTO PSW. EVENTUALLY, PSW WAS RESTORED AND SSW BASIN INVENTORY WAS RECOVERED. THE POWER LOSS TO THE SUPPLY WELLS WAS DUE TO A MALFUNCTION OF THE MICROWAVE INFORMATION AND CONTROL SYSTEMS. PERIODIC MICROWAVE OPERATIONAL CHECKS ARE BEING ESTABLISHED.
416 | 4161990011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161990011R00.pdf | 1990-07-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Grand Gulf | B | GE | PO | 100 | On July 24, 1990 at 1355, the reactor tripped on high reactor water level. Reactor power was in the process of being reduced in an attempt to control "B" Reactor Feed Pump Turbine (RFPT) oscillations caused by a malfunction of the "B" RFPT Controller.<br /><br /> The cause of the malfunctioning "B" RFPT Controller was determined to be an intermittent failure of the Linear Variable Differential Transformer (LVDT) and the associated circuit board to the Electronic Automatic Positioner (EAP). <br /><br /> The EAP Dahl Controller was calibrated in accordance with the vendor recommended setting. The calibration procedure for the Reactor Feed Pump Turbine "A" and "B" FAP Dahl control circuit has been improved and the calibration frequency has been increased. <br /><br /> All plant safety systems performed as expected. The minimum water level reached was approximately 126.7 inches above the top of active fuel. The RCIC was manually started and functioned as designed.
416 | 4161990017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161990017R00.pdf | 1990-09-16 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Grand Gulf | B | GE | PO | 100 | A Division I Load Shedding and Sequencing System malfunction caused a Balance of Plant (BOP) load shed on September 16, 1990. The loss of major plant equipment, which received power from the shedded BOP busses, resulted in a reactor scram, due to Main Turbine Control Valve fast closure. Subsequent to the scram, reactor water level decreased to -41.6 inches where an automatic , High Pressure Core Spray System actuation occurred. During restoration of Main Steam Isolation Valves, as a part of scram subsequent actions, a second reactor scram occurred due to low reactor water level.<br /><br /> The load shed is attributed to a defective light bulb being placed in the load shed panel. The shorted light bulb caused an overcurrent which subsequently caused degradation of a computer chip which initiated the load shed. The cards which contained degraded computer chips, due to the overcurrent, were replaced. The Division I Load Shed Panel was tested satisfactorily and operability was verified. <br /><br /> All safety systems functioned as designed. The minimum water level reached was -54.1 inches which was approximately 112 inches above the top of active fuel.
416 | 4161990028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161990028R00.pdf | 1990-12-10 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [9 empty] | X | [5 empty] | X | [24 empty] | X | Grand Gulf | B | GE | PO | 100 | Actuation of Engineered Safety Features occurred on December 10, 1990, including the reactor protection system (RPS) and the emergency core cooling system (ECCS) high pressure core spray (HPCS) system. The subsequent reactor scram from full power was caused indirectly by a failed solder joint in the instrument air system. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv) and plant Technical Specification 3.5.1 Action Item h.<br /><br /> The failed pipe joint was investigated. A leaking root valve apparently caused a slight pressure differential across the joint and precluded optimum capillary action during the soldering process. It is believed that vibrations in combination with system pressure caused the resultant separation of this inadequately soldered joint. This joint had been soldered on November 9, 1990. Applicable plant administrative procedures will be revised to preclude inadequate welding and similar failures. <br /><br /> The actuation of the RPS and the resultant automatic scram occurred as designed. Actuation of the ECCS initiated as designed by injecting condensate from the condensate storage tank into the reactor vessel via HPCS. The safety of the general public was not compromised by this event.
416 | 4161990029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161990029R00.pdf | 1990-12-18 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 17 | On December 18, 1990, during a controlled shutdown, a Reactor Protection System actuation occurred resulting in an automatic plant shutdown. The actuation occurred due to low reactor water level which was caused by a Reactor Feedwater Pump trip. <br /><br /> The high discharge pressure trip of the feedwater pump was a result of the interaction between the startup level control system and the master feedwater control system. <br /><br /> The investigation, which followed the scram, identified the air supply valve for the startup level control valve not being fully open and the 'A' electric automatic positioner's high speed stop limit switch for the Reactor Feedpump Turbine not being properly set. The combined effect of these problems are the most probable cause of the event. <br /><br /> All safety systems performed as designed during the transient. The minimum water level reached was -25 inches as indicated on the wide range level instrumentation. The minimum level was approximately 142 inches above the top of active fuel.
416 | 4161991002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991002R01.pdf | 1991-04-06 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 74 | During a routine surveillance of the Main Turbine Mechanical Overspeed Trip Devices, an automatic reactor shutdown occurred. The test was being performed by the Automatic Turbine Tester (ATT) which uses a computerized test program. During the reset step of the computer program, a miniature circuit breaker in the ATT circuitry tripped open. This deenergized three solenoids which were needed to prevent a turbine trip due to testing. The cause of the premature breaker trip is attributed to the circuit breaker being undersized for its application. Due to aging and the breaker operating at loads which sometimes exceeded its rated current value, the breaker was operating in a degraded condition. The operating module which contained the miniature breaker was replaced and the test was successfully completed. <br /><br /> Following a review of the test circuitry design, a breaker with a higher current rating was placed in the test circuit. The circuitry was tested satisfactorily and used to perform the mechanical overspeed test. The installed breaker will remain in service pending further design review. All safety systems functioned as designed. The reactor water remained at least 164 inches above the top of active fuel.
416 | 4161991004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991004R00.pdf | 1991-06-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 35 | On June 11, 1991, a controlled shutdown was in progress for maintenance on the mechanical seals for both reactor recirculation water pumps. In accordance with approved plant procedures, the reactor recirculation water pumps were shifted from fast to slow speed. This caused a swell in reactor water level which resulted in a decrease in feedwater and condensate flow. The condensate system flow rate decreased to the minimum flow setpoint, but the minimum flow valve failed to respond to the low flow condition. <br /><br /> The failure resulted in a loss of feedwater and a subsequent automatic reactor scram. The failure is attributed to a failed pneumatic relay inside the valve positioner. The most probable cause for the relay failure is excessive vibration experienced during minimum flow conditions. The positioner was replaced and retested satisfactorily. An evaluation will be performed to determine methods or modifications to preclude valve failure due to vibration. In the interim, a task will be implemented to perform a functional test and a visual inspection of the positioner prior to controlled shutdowns and start-ups. Additionally, a task will be generated to replace the valve's positioner each refueling outage until a more suitable resolution is determined. Based on reviews of the event, all safety systems functioned as designed. The reactor water remained at least 140 inches above the top of the active fuel during the transient.
416 | 4161991005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991005R01.pdf | 1991-06-17 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X | [28 empty] | X | [5 empty] | Grand Gulf | B | GE | PO | 73 | On June 17, 1991 a fault occurred on the B-phase of breaker J5232 (500 KV). The fault resulted in a loss of power (LOP) to two balance of plant (BOP) busses and two engineered safety feature (ESF) busses. An automatic reactor scram occurred due to a main turbine control valve fast closure signal which was a result of the breaker fault. Power was restored to the BOP busses via their alternate supply. <br /><br /> The emergency diesel generator associated with each deenergized ESF bus responded to the bus undervoltage and functioned as designed. Power to the ESF busses was restored and the diesel generators were secured and placed in standby. The LOP also caused a Main Steam Line Isolation valve closure which resulted in a loss of feedwater and an increase in vessel pressure. Main Steam Line Safety Relief valves (SRV) were manually operated to control pressure. The High Pressure Core Spray System automatically initiated and injected into the vessel due to a low water level (reported per TS 3.5.1.h). <br /><br /> Based on an investigation of the occurrence, it was determined that the cause of the breaker fault is attributed to inadequate maintenance practices. There was no degradation of safety systems or components during the transient. Reactor water level was maintained at least 121 inches above the top of active fuel.
416 | 4161991007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991007R00.pdf | 1991-07-28 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 100 | A load shed of balance of plant (BOP) equipment occurred while troubleshooting a Division 2 load shedding and sequencing (LSS) system trouble alarm. A reactor scram ensued. Investigation revealed that LSS panels had a logic coupling in that energizing the 15 volt converter without power from the 24 volt converter will cause a BOP load shed. This system response contradicts LSS system specification requirements. A vendor design error occurred and was not detected previously. Pre-operational testing had not detected the logic coupling and was a contributing factor. LSS panels were modified to preclude BOP load shed due to loss of the LSS panel 24 volt power converter. Analysis of the reactor scram and subsequent events determined that safety systems operated as designed. This report is being submitted to describe the ESF actuations pursuant to 10 CFR 50.73(a)(2)(iv) and plant Technical Specification 3.5.1 Action h.
416 | 4161991010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991010R00.pdf | 1991-08-10 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On August 10, 1991, a severe thunderstorm was in progress in the site vicinity. During the storm, a lightning strike caused a spike on plant neutron monitoring instrumentation. The reactor automatically scrammed due to the spike simulating a high flux signal on the Average Power Range Monitors (APRMs). The spike caused two High Pressure Core Spray (HPCS) low water level channels to trip. HPCS did not initiate due to the short duration of the spike. Reactor water level decreased to -19 inches and was subsequently restored to normal by the feedwater system. <br /><br /> A functional check of APRM indications and HPCS trip units was performed prior to plant startup. No adverse effects were observed. <br /><br /> Following an evaluation, recommendations were made for extending the existing lightning protection system to provide expanded site protection. There was no degradation of safety systems or components as a result of this occurrence.
416 | 4161991012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161991012R00.pdf | 1991-11-19 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On November 19, 1991, a thunderstorm with severe lightning occurred in the site vicinity. At approximately 2049, during the storm, the Division 2 Average Power Range Monitors (APRM) IG! received a high neutron flux signal resulting in a trip on the Division 2 Reactor Protection System (RPS). Prior to the trip occurring on the Division 2 RPS, a Maintenance surveillance was in progress which caused the Division 1 RPS to be in the tripped condition. Both systems being in the tripped condition, resulted in an automatic reactor scram. Following the scram, vessel water level decreased to -14 inches. Water level was restored by the Condensate and Feedwater Systems. <br /><br /> Based on a review of computer data, it appears that the output of a five volt power supply associated with the APRMs may have been deenergized, then reenergized. This would have resulted in an APRM scram. A supplemental report will be submitted following the determination of the root cause of the lightning induced scrams experienced at GGNS.
416 | 4161992010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161992010R01.pdf | 1992-06-06 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | SU | 5 | On June 6, 1992 at approximately 1836 hours station licensed operators were increasing reactor thermal power following the fifth refueling outage. During the power ascension, the reactor scrammed due to an RPS actuation signal from the Average Power Range Monitoring System (APRM). In STARTUP the high neutron flux trip occurs at approximately 15 percent thermal power. Following the scram, vessel level decreased to approximately 14 inches. Level was restored by the Feedwater system and the plant was stabilized in accordance with plant procedures. Generation of a scram signal is believed to have been caused by electromagnetic interference (EMI) coupling into the APRM system. The EMI was the result of an electrical storm in the vicinity of the plant. GGNS is currently monitoring and evaluating data experienced during lightning activity. The results of the evaluation will be used to develop additional corrective actions, if warranted. No safety functions or components were compromised as a result of this event. Therefore the occurrence did not adversely impact the health and safety of the public.
416 | 4161992013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161992013R00.pdf | 1992-06-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Grand Gulf | B | GE | PO | 100 | On June 18, 1992 during maintenance on a main turbine control fluid filter, a reactor scram occurred as a result of a high neutron flux condition due to partial closure of the main turbine stop and control valves. The filter which was to be changed had a leaking isolation valve which allowed the filter to remain at system pressure. The filter was not verified depressurized in accordance with procedures prior to an attempt to remove the filter cover. During the removal of the cover, the filter O-ring blew out which resulted in a control fluid spill and subsequent closure of the main turbine stop and control valves. Following the scram, vessel level decreased to approximately - 28 inches. <br /><br /> Level was restored by feedwater and Reactor Core Isolation Cooling systems. This event did not compromise the safety of the public. LER92013.DOC
416 | 4161992017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161992017R02.pdf | 1992-08-04 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On August 4, 1992, the reactor scrammed due to a fast closure of the main turbine stop valves. The fast closure of the stop valves occurred as a result of a main generator trip which was caused by a low primary cooling water tank level signal. The erroneous signal was generated due to perturbations in the Primary Water level sensing circuitry. The perturbations in the Primary Water level sensing circuit was caused by the operation of a 24 Vdc battery ground detection circuit. Tests performed during the investigation confirmed that noise spikes were generated on the Primary Water level instrument loop upon operation of this battery's ground detection circuit. Following the scram, vessel level decreased to approximately 1 inch, which is approximately 167 inches above the top of active fuel. Steam dome pressure increased to approximately 1111 pounds per square inch. Two main steam safety relief valves operated to relieve vessel pressure. Level was restored to approximately 47 inches by the feedwater system. This event did not compromise the safety of the public.
416 | 4161993008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161993008R00.pdf | 1993-09-13 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Grand Gulf | B | GE | PO | 100 | On September 13, 1993 during normal plant operations, an actuation of the High Pressure Core Spray system occurred. Reactor vessel water level increased to high water level scram setpoint. Reactor water level decreased to approximately -36 inches and was restored by the Feedwater system. The plant was stabilized in accordance with plant procedures. A subsequent investigation revealed that the HPCS initiation was the result of low water level signals from the C and G channels of HPCS level instrumentation. It is believed that flow impingement as a result of a displaced jet pump mixer caused perturbations in the HPCS level instrumentation. The unit was required to shut down due to an inoperable jet pump. Additional information associated with the jet pump malfunction will be submitted in an upcoming submittal. This report also serves as a Special Report pursuant to GGNS Technical Specification 3.5.1.h. The HPCS actuation and injection did not degrade the capability of any safety related plant system. Therefore the health and safety of the public were not compromised as a result of this occurrence.
416 | 4161994004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161994004R00.pdf | 1994-03-26 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 73 | On March 26, 1994, scram time testing was being performed which found five slow rods. Although these failures did not constitute a violation, the plant was ordered shutdown in consideration of Technical Specification 3.1.3.2 Action c.1. An additional 163 control rods were analyzed at 0001 on March 27, 1994, when the reactor was manually scrammed and scram times recorded. Of these rods, 44 additional rods were slow moving but all were satisfactory for insertion to position 13. <br /><br /> The cause of the slow moving control rods was determined to be contamination of the internal surfaces of the scram solenoid pilot valve head assemblies. A thread sealant used during maintenance on the valves caused the seats in the top head assembly to adhere slightly to adjacent surfaces resulting in a delay in the initial opening of air exhaust ports. In its uncured state, the sealant attacked the viton seats and may have caused metallic moving parts to stick. <br /><br /> Immediate remedial actions included installing the pilot valve top head assemblies using a thread sealant tape rather than the sealant previously used and using an approved detergent to clean 193 new assemblies. Long term corrective actions are: evaluate training maintenance personnel on proper use of various thread sealants, write generic procedure on proper use of various thread sealants and evaluate, in other applications, the use of sealants and other similar generic materials. <br /><br /> A review of operating data determined that all safety systems behaved as expected. This incident did not degrade the ability of other plant systems or equipment to perform their intended function. The safety and health of the general public were not compromised by this event.
416 | 4161994011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161994011R00.pdf | 1994-11-01 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | A reactor scram occurred on November 1, 1994 while plant maintenance personnel were performing a quarterly surveillance on the reactor protection system. All control rods inserted fully and vessel level was maintained with the reactor feedwater pumps.<br /><br /> Causes of the event were determined to be the ground detection circuit for the Division 1 125 VDC system which had been modified recently in conjunction with a bolted ground fault on the Division 1 backup scram solenoid valve. The bolted fault was found to be on the negative pole lead of the solenoid located at its pigtail condulet. The modification of the ground detection circuit was determined to increase the sensitivity of system components to ground faults which could result in inadvertent actuations. While the ground detection system modification had focused on the safety design basis, it failed to consider potential operational impact such as inadvertent actuations upon postulated ground faults. <br /><br /> Immediate corrective action included repairing the bolted ground fault on the negative pole lead for the valve's coil. Also, the continuous monitoring ground detection circuit of the 125 VDC ground detection system was eliminated to preclude similar adverse consequences. Local periodic monitoring for system grounds was not affected by eliminating the continuous monitoring circuit. Long term corrective actions will evaluate modification of continuous monitoring circuits in all Class 1E DC ground detection systems. <br /><br /> This incident did not impair the ability of any system to perform its safety function. Health and safety of the public were not compromised by this event.
416 | 4161995004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161995004R01.pdf | 1995-03-16 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | A reactor scram occurred on March 16, 1995, while plant maintenance personnel were performing a semiannual surveillance on the neutron monitoring system. All control rods inserted fully and vessel level was maintained with the reactor feedwater system.<br /><br /> Causes of the event were determined to be a ground fault on the minimum flow valve for the Reactor Core Isolation Cooling System (RCIC) and a ground on a backup scram valve solenoid. The ground on the solenoid was due to liquid in the solenoid housing. The performance of the surveillance coupled with the two grounds resulted in the inadvertent actuation of the backup scram valve.<br /><br /> Immediate corrective actions included reworking the ground on the RCIC valve, replacing the backup scram valve solenoid and the sealing of the conduit going to the solenoid to prevent moisture intrusion. A Material Nonconformance Report was initiated to address the presence of liquid in the solenoid housing. <br /><br /> The interim actions taken as a result of the November 1994 scram did not prevent recurrence of inadvertent actuation of a backup scram valve due to ground faults on the DC bus. <br /><br /> A ground detection circuit is presently being redesigned to provide annunciation in the control room of the ungrounded Class 1E DC buses. This will support prompt identification and removal of identified grounds. In the interim, increased ground detection checks utilizing the local ground detection meters are being performed by maintenance and operations personnel. <br /><br /> This incident did not impair the ability of any system to perform its intended safety function. The health and safety of the public were not compromised as a result of this event.
416 | 4161995007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161995007R00.pdf | 1995-07-03 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | A reactor scram occurred at 2032 on July 3, 1995. The cause of the scram was the absence of trip indication in conjunction with the performance of the monthly high level trip functional surveillance. When the channel signal was increased to the high level setpoint a trip of the Main Turbine and both Reactor Feedwater Pumps resulted which caused a full Reactor Protection System actuation and a reactor scram.<br /><br /> Immediate corrective actions included an investigation of the high level trip circuitry which resulted in the replacement of blown fuses and a burnt out light bulb. Operations then depressed all three high water level trip reset pushbuttons which cleared all three amber logic lights. The monthly surveillance was then performed satisfactorily and revealed no other abnormalities. As a long term corrective action Maintenance strengthened the monthly procedure to require a verification that the fuses are not blown, that all three trip reset pushbuttons are depressed and a verification that the trip logic lights are off prior to the start of the high level trip surveillance. <br /><br /> This event resulted in an automatic Emergency Core Cooling System (ECCS) discharge into the Reactor Coolant System. The ECCS injection is reportable in accordance with the Special Reporting requirements of the GGNS Technical Requirements Manual. The scram is reportable pursuant to 10CFR50.73(a)(2)(iv). This event did not impair the ability of any system to perform its intended safety function. No safety relief valves actuated during the plant transient. The health and safety of the general public were not compromised as a result of this event.
416 | 4161995008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161995008R00.pdf | 1995-07-12 | QL6 | Condenser Leakage | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Grand Gulf | B | GE | PO | 100 | On July 12, 1995, a reactor SCRAM occurred due to a Main Turbine trip on low condenser vacuum. Failure of a condenser expansion joint resulted in rapid condenser vacuum decrease which led to a turbine trip and actuation of the Reactor Protection System (RPS). Continued decreasing Main Condenser vacuum following the reactor SCRAM led operators to close the Main Steamline Isolation Valves (MSIV). Reactor pressure and level was controlled using two Safety Relief Valves (SRV) and Reactor Core Isolation Cooling (RCIC). In the process of pressure control, a second SCRAM occurred on low level (Level 3, 11.4 inches) when the SRV was closed, however, at the time of the second SCRAM all control rods were fully inserted. This report is being submitted pursuant to 10CFR 50.73(a)(2)(iv). <br /><br /> The cause of the event was failure of one of the rubber boots that form the Main Condenser expansion joints. The rubber expansion joint had been weakened by oil contamination.<br /><br /> All control rods inserted fully and reactor level did not decrease below the automatic Emergency Core Cooling System (ECCS) actuation set point (Level 2, -41.6 inches). The RCIC system was manually initiated for vessel level and pressure control and two SRVs were manually cycled for pressure control. The health and safety of the general public were not compromised by this event.
416 | 4161995010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161995010R00.pdf | 1995-07-30 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | At 1148 on July 30, 1995, a reactor scram occurred due to a Main Turbine/Generator trip. The Main Turbine/Generator trip resulted in a turbine control valve fast closure and turbine stop valve closure actuation immediately followed by a full Reactor Protection System (RPS) actuation. <br /><br /> Operators determined that the generator tripped on Generator Current Differential. The root cause of the scram was the failure of a current transformer on the 'A' phase for one of the generator output breakers. The current transformer failure generated an 'A' phase Unit Differential Protective Relay trip. <br /><br /> Corrective actions include an inspection/test of all equipment monitored by the unit differential relay scheme, replacement in kind of the failed current transformer and a failure analysis of the current transformer to be performed by the transformer vendor to determine the failure mode. <br /><br /> The RPS actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). Emergency Core Cooling Systems did not inject and safety relief valves did not actuate during the plant transient. not compromised as a result of this event.
416 | 4161995011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161995011R00.pdf | 1995-09-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Grand Gulf | B | GE | PO | 100 | On September 17, 1995, at approximately 2200 hours, GGNS Operations personnel were conducting the Reactor Feed Pump Turbine Emergency Governor Exercise Monthly Test of the 'B' Reactor Feed Pump Turbine. During the course of the test, a trip of the 'B' Reactor Feed Pump Turbine occurred, followed by a Reactor Protection System actuation on low reactor water level and a reactor SCRAM. This Reactor Protection System actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> The low reactor water level Reactor Protection System actuation occurred due to the trip of the 'B' Reactor Feed Pump Turbine and failure of the associated pump's discharge check valve to close quickly enough to prevent reverse flow from the 'A' Feed Pump back through the 'B' pump. Investigation revealed that wear of the valve disc stop allowed the valve disc to open at an angle beyond manufacturer's specifications. The 'A' and 'B' check valves were corrected by weld build-up of the disc stops. <br /><br /> This event resulted in an Emergency Core Cooling System, High Pressure Core Spray discharge into the Reactor Coolant System as the result of a valid Engineered Safety Feature signal and is being reported as a Special Report in accordance with GGNS Technical Requirement Manual section 7.7.2.1.
416 | 4161996004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161996004R01.pdf | 1996-06-06 | QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | [45 empty] | Grand Gulf | B | GE | PO | 100 | At 1126 on June 6, 1996, GGNS experienced an opening Of Six Main Steam Safety/Relief Valves (SRV) which resulted in an increase in suppression pool temperature. The reactor was manually scrammed by control room operators before temperature limits were reached. The cause of the SRV lifts was the failure of a capacitor on a card supplying power to the logic train which caused a momentary voltage spike sufficient to initiate the Division 11 logic for the SRVs in addition to the logic for the low-low set SRVs. Six SRVs opened due to the seal-in feature of low-low set. Following the manual scram, the six SRVs closed sequentially as reactor pressure decreased.<br /><br /> Initial short-term corrective actions included troubleshooting/replacing the trip unit card in addition to functionally checking the other card files in the same panel. A material nonconformance report was generated to document the failure of the capacitor on the failed trip unit. Long-term corrective actions are to evaluate improvements to the low-low set function (which is not single-failure proof) to improve the reliability of the SRV function, perform a failure analysis on the failed trip unit card and review generic implications for similar circuit logic issues. <br /><br /> Failure analysis performed on the trip unit indicated the most likely cause of the failure to be the shorting of the capacitor. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv). Although the Emergency Core Cooling System (ECCS) was available to perform its safety function, ECCS injection was not required during the event. The health and safety of the general public were not compromised as a result of this event.
416 | 4161996006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161996006R00.pdf | 1996-11-27 | QR3 | Reactivity Control Imbalance | [45 empty] | Grand Gulf | B | GE | SU | 1 | On November 27, 1996 plant startup was commencing from the eighth refueling outage, with vessel pressure 600 psig and the 'B' control rod drive (CRD) pump in service. The 'B' CRD pump tripped and plant implemented the applicable off-normal event procedure requirements. Actions were taken to restore by swapping components. With a low CST level, CRD flow was unable to be restored. <br /><br /> The scram accumulator alarm for multiple control rods was received (only one alarm associated with a withdrawn control rod). When the in-service CRD pump could not maintain adequate suction pressure, the Shift Superintendent directed the Mode switch be placed to shutdown. The Operations Shift Superintendent elected to conservatively scram the reactor based upon accumulator low pressure alarms and CRD low suction pressure in lieu of verifying that the accumulator pressure had decreased below the Technical Specification minimum pressure and to prevent damage to the CRD pump. The reactor Mode switch was placed in SHUTDOWN and the plant was stabilized in accordance with applicable procedures. Technical Specification (TS) 3.1.5 requires reactor shutdown with vessel pressure below 600 psig concurrent with one or more control rod scram accumulators inoperable associated with a withdrawn control rod and charging water header pressure less than 1520 psig. <br /><br /> Subsequent investigation indicated that a malfunctioning CST level transmitter resulted in a erroneous CST level reading. The transmitter was replaced, satisfactorily tested and returned to service. <br /><br /> The ability to achieve and maintain safe shutdown was not adversely impacted, nor was public health and safety compromised by this event.
416 | 4161998001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161998001R00.pdf | 1998-01-28 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On January 28, 1998, the Grand Gulf reactor was manually scrammed from 100% power in accordance with turbine vendor recommended standing orders due to Moisture Separator Reheater (MSR) differential temperature. The standing order specified the scram for protection of the turbine.The differential temperature resulted from loss of output power from inverter 1Y98. Output of inverter 1Y98 was lost during maintenance activities. The inverter output supplied power to the temperature control valves for the second stage MSRs. When the temperature delta between the MSRs increased, operators manually scrammed the reactor per standing orders.The cause of the scram was manual operator action. The apparent cause of loss of the inverter output is that a malfunction of the synchronization board relay circuit and/or the static switch controls led to non-synchronized transfer. Analysis of the sequence of events and personnel observations found that such a failure was consistent with the subsequent events observed (i.e., the blown fuses and loss of power leading to the uneven heating at the MSRs).The components suspected of failure, static switch controller (master and slave), were replaced and have been sent to the vendor for failure analysis.This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
416 | 4161999003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4161999003R00.pdf | 1999-02-21 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Grand Gulf | B | GE | PO | 83 | On February 21, 1999, a reactor SCRAM was manually inserted as part of a preplanned sequence based on specific plant conditions related to the condenser system. Failure of a condenser expansion joint resulted in rapid condenser vacuum decrease that led to a rapid plant shutdown. Continued decreasing main condenser vacuum following the reactor SCRAM led operators to close the main steamline isolation valves. Reactor pressure and level were controlled using several safety relief valves and the reactor core isolation cooling system.All control rods inserted fully and reactor level did not decrease below the automatic Emergency Core Cooling System actuation set point. The Reactor Core Isolation Cooling system was manually initiated for vessel level and pressure control and several SRVs were manually cycled for pressure control.The health and safety of the general public were not compromised by this event. Because the reactor was manually SCRAMMED in anticipation of a possible automatic trip due to loss of vacuum, this event is being reported pursuant to 10CFR50.73(a)(2)(iv).
416 | 4162000005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162000005R00.pdf | 2000-09-15 | QR8 | Spurious Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On 9/15/00 at approximately 0630 hours, while operating at steady state conditions, a reactor scram occurred. The scram was the result of a reactor protection system actuation from a turbine control valve fast closure signal. This signal was the result of a generator load transient caused by failure of a 500 kV circuit breaker located in an offsite switchyard which directly feeds the GGNS switchyard.A generator load reject was sensed due to the grid voltage transient, causing generator load demand to automatically switch off. A turbine control valve fast closure was sensed as Turbine Control Valves (TCVs) closed. However the generator stayed online and, due to the speed demand signal that was still present, the TCVs did not go full closed. The reactor scrammed but the End of Cycle Recirculation Pump Trip (EOC-RPT) did not occur. This issue is being addressed in Licensee Event Report 200-00600.No major equipment was out of service except for Engineered Safety Feature Transformer 12 to 17AC bus feeder breaker, which was tagged out of service. All control rods inserted and all other equipment responded as expected. Reactor Core Isolation Cooling initiated and began injecting into the vessel, however no ECCS initiated. Additionally, due to the low grid voltage, the Division III diesel generator started on undervoltage as designed, tied to and provided power to the 17AC bus.
416 | 4162001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162001003R00.pdf | 2001-08-07 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On August 7, 2001 at approximately 2017 hours, while operating at steady state conditions, a reactor scram occurred. The scram was the result of a reactor protection system actuation from a Turbine Control Valve fast closure signal. This signal was the result of a generator load transient caused by failure of a 500 kV disconnect. The disconnect that failed is located in an offsite switchyard which directly feeds the GGNS switchyard. A generator load reject was sensed due to the grid transient, causing generator load demand and valve rate limiters to automatically switch off. A turbine control valve fast closure response was sensed as Turbine Control Valves moved in the closed direction. The reactor scrammed but the End of Cycle Recirculation Pump Trip did not occur, as expected. This event is bounded by the current analyses, as discussed in the safety assessment, Section G.No major equipment was out of service at the time of this occurrence. The Reactor Core Isolation Cooling system was inoperable due to the performance of corrective maintenance, however the maintenance had been completed and the system was functional at the time of the scram. All control rods inserted and all other equipment responded as expected. The Condensate/Feedwater System was lost shortly after the scram occurred due to hotwell level problems. The Reactor Core Isolation Cooling system was manually initiated and used for reactor water level control.
416 | 4162002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162002003R00.pdf | 2002-06-22 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Grand Gulf | B | GE | PO | 100 | On June 22, 2002 at approximately 2217, while operating at steady state conditions of 100 percent rated thermal power and 88.7 percent total core flow, a reactor scram occurred on Turbine Control Valve fast closure. It was the result of a ground fault on the secondary (i.e. 34.5 kV side) of Service Transformer 21 Engineered Safety Feature busses 16 and 17 were de-energized. Division 2 and 3 diesel generators started and energized busses 16 and 17, respectively. No Emergency Core Cooling System initiated. A partial loss of plant non-safety power busses occurred. Those powered by Service Transformer 21 were lost, while those powered by Service Transformer 11 remained energized. Important loads lost were both Reactor Recirculation Pumps, and the running Electro-hydraulic Control (EHC) pumps. A third EHC pump auto started on low fluid pressure. Condensate Pumps B and C, and Condensate Booster Pump C tripped due to loss of buss 14AE. Numerous Division 2 isolations occurred due to loss of 16AB. The lowest reactor level noted during the transient was minus 7 inches, approximately 18 inches below the low level automatic scram setpoint of 11 inches. Auxiliary site power loop was also de-energized. Important loads lost were the Emergency Operations Facility and a partial loss of security lighting. Both Reactor Feed Pumps (RFPs) tripped on low suction pressure about 8 minutes after the scram. One RFP was immediately restored.Safety related control room air conditioner “B” failed to sequence back on after the diesel re-energized buss 16. The air conditioner was started manually.
416 | 4162003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162003001R00.pdf | 2003-01-30 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 100 | On January 30, 2003, at approximately 10:54 a.m., Grand Gulf Nuclear Station was operating at 100 percent power when operators inserted a manual reactor scram. The manual scram was initiated due to decreasing reactor water level resulting from a loss of feedwater. The loss of feedwater was caused by isolation of the condensate demineralizers due to shorting of a conductor which tripped the common power supply for the position indication limit switches for the demineralizers valves. The loss of the inlet valve's position indication caused all operating demineralizer outlet valves to close.High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) auto initiated and injected into the reactor vessel to restore level.In response to the HPCS initiation the Division 3 Emergency Diesel Generator auto started but was not needed to supply the Division 3 Buss.As designed, Standby Service Water system loops "A" and "C" started, for required support of equipment.
416 | 4162003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162003002R00.pdf | 2003-04-24 | QR5 | Turbine Trip |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Grand Gulf | B | GE | PO | 100 | GGNS automatically scrammed at approximately 0948 CDST on 4/24/2003 due to a partial loss of offsite power. At the time of the scram, there was a severe thunderstorm in the vicinity. High winds apparently resulted in closure of an open disconnect in the GGNS Switchyard which in turn led to the partial loss of offsite power.During the event the Reactor Protection System (RPS) auto-actuated; High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) auto-initiated on Reactor (Rx) Water Level 2 and injected into the Rx to restore Rx water level; Division 2 and 3 Diesel Generators (DGs) started and energized the 16AB and 17AC Electrical Buses, respectively; the 15AA Electrical Bus lost power and was re-energized by the Division 1 DG shortly after the initial event; all Standby Service Water (SSW) divisions started; all main steam line isolation valves (MSIVs) isolated on loss of power; and containment isolation occurred.Rx water level and pressure were restored and stabilized. Plant data was reviewed to confirm proper response of plant equipment. Switchyard inspections were conducted to assess damage and verify equipment condition prior to restoring tripped equipment. The NRC Resident Inspector was notified. NRC call-in per 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv) was made at 1320 CDST.
416 | 4162005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162005001R00.pdf | 2005-02-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 100 | On February 11, 2005 at 1959, Grand Gulf experienced an automatic reactor scram as a result of breaker 552-1105 tripping due to a ground fault on the 34.5 kV bus work of Service Transformer ST11. Loss of ST11 resulted in the loss of power to 12HE, 13AD and 15AA buses. Emergency Diesel Generator (EDG) 11 started on a loss of power and connected to the 15AA bus. All control rods inserted to 00 position. Reactor vessel water level dropped to approximately minus 75 inches on wide range level instrumentation before the High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems, initiated at Reactor Vessel Water Level Low Low, Level 2 (minus 41.6 inches), and restored level to the normal operating band. Concurrent with this event, EDG 13 (Division III) started on Reactor Vessel Water Level Low Low, Level 2. Standby Service Water (SSW) started to support EDG operation. Containment isolation occurred as a result of Reactor Vessel Water Level Low Low, Level 2. The affected bus was lined up to other available power sources. The safety related bus was synchronized back to the grid and the EDGs were secured. Normal feedwater level control was established and both HPCS and RCIC were secured.
416 | 4162007002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162007002R00.pdf | 2007-05-19 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Grand Gulf | B | GE | PO | 100 | On May 19, 2007 at 1127, a Reactor SCRAM from 78% Core Thermal Power (CTP) occurred due to a Main Turbine trip on low Condenser vacuum. Reactor power had been lowered from 100% to 78%, per Loss of Condenser Vacuum Off-Normal-Event Procedure (ONEP), just prior to the automatic actuation of the Reactor Protection System (RPS). Failure of a High Pressure (HP) Condenser expansion joint resulted in degrading Condenser vacuum and subsequent turbine trip over an approximately three minute period. Pressure control was initially maintained with Turbine Bypass Control valves until vacuum decreased to the point that bypass was no longer available. Then Reactor pressure was controlled using a Safety Relief Valve (SRV). Reactor water level continued to be maintained with Condensate system. This report is being submitted pursuant to10CFR50.73(a)(2)(iv)(A).The cause of the event was the failure of the HP Condenser expansion joint between the Main Turbine and Condenser. Failure of the expansion joint resulted in low condenser vacuum.All Control Rods inserted fully and Reactor level did not decrease below the automatic Emergency Core Cooling System (ECCS) actuation set point (Level 2, -41.6 inches). The Reactor vessel level 3 isolation setpoint of + 11.4 inches was reached for Shutdown Cooling which was already isolated. The expansion joint was replaced to correct the condition.
416 | 4162007003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162007003R00.pdf | 2007-08-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Grand Gulf | B | GE | PO | 100 | On August 21, 2007 at 1415 hours Grand Gulf Nuclear Station experienced an actuation of the ReactorProtection System (RPS) which resulted in an automatic reactor shutdown (SCRAM) from 100 percentpower due to decreasing reactor water level. The initiation of RPS resulting in an automatic reactorSCRAM is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A).At the time of the SCRAM technicians were securing from routine maintenance in the Bailey INFI-90digital Feed Water control panel for the "A" Feed Pump when an unexpected Power Failure Interrupt(PFI) signal was received. This unexpected signal drove the "A" Feed Pump governor control valve tominimum position which lead to a reactor scram on Level 3 (+11.4 inches) low reactor water level.The reactor water level did not reach the Level 2 set point (-41.6 inches) for initiation of Emergency CoreCooling Systems (ECCS), therefore no ECCS initiation occurred. All control rods were fully inserted intothe core and all other system performed as designed. The normal heat sink (main condenser) remainedavailable therefore no Safety Relief Valve actuations occurred.The Feed Water panel was inspected and as a precaution, the bus monitor, auto transfer, power supply,and power entry panel were replaced.
416 | 4162008001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162008001R00.pdf | 2008-01-12 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 99 | On January 12, 2008, at 1626 hours a manual reactor scram was initiated from 99 percent power due toloss of cooling to the Main Transformers. After the scram reactor water level decreased to Level 2 (-41.6inches) and Reactor Core Isolation Cooling initiated. There were no inoperable structures, systems, orcomponents at the start of the event that contributed to the event. The normal heat sink (main condenser) remained available and no Main Steam Safety Relief Valves actuations occurred during theevent. All control rods fully inserted and all safety systems functioned as designed and responded properly.The cause of this event was the loss of cooling to the Main Transformers caused by loss of Auxiliary Power to the Main Transformer cooling system. Inspection of the complete circuit for Main TransformerAuxiliary Power showed that the “B” phase power cables were found to be burned in two at the transferswitch panel. The cause of the “B” phase power cable failure is attributed to failure of an electrical compression connection on a lug connection. This particular cable and connection has been inservice since plant start-up. Potential root causes were determined to be use of a compression connection forhigh current applications versus the preferred crimp type connection and an inadequate preventive maintenance strategy to provide early detection. Corrective actions included an inspection of the powerpanel and replacement of all damaged cabling.
416 | 4162008002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162008002R00.pdf | 2008-03-21 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On March 21, 2008 at 1525 hours Grand Gulf Nuclear Station experienced an actuation of the ReactorProtection System (RPS) which resulted in an automatic reactor shutdown (scram) from 100 percentpower. The scram was due to main turbine control valve fast closure following a main generator trip caused by "C" phase unit differential lockout. There were no inoperable structures, systems, or components at the start of this event that contributed to the event. The normal heat sink (main condenser) remained available. All control rods fully inserted and all safety systems functioned asdesigned.The minimum reactor water level recorded during this event was -8.2 inches wide range. The level forinitiation of Emergency Core Cooling Systems (ECCS) is -41.6 inches, therefore no ECCS initiationoccurred. Six safety relief valves (SRVs) lifted momentarily and then closed at the onset of the event.After SRV closure, reactor pressure was controlled with the main turbine bypass valves and reactor levelwas maintained the entire time using normal condensate and feedwater.The cause of the event was a main generator trip as the result of a "C" phase unit differential lockout.Troubleshooting which included inspection of the high voltage circuit and check of calibration of both the"A" and "B" relays was initiated; however, no definitive cause for the trip was identified. As a precaution,the suspect "C" phase unit different relay was replaced.
416 | 4162008004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162008004R00.pdf | 2008-10-23 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Grand Gulf | B | GE | PO | 10 | On October 23, 2008 at 0721 Grand Gulf Nuclear Station was operating in MODE 1 at approximately 10 percent power when an actuation of the Reactor Protection System (RPS) occurred due to decreasing reactor coolant level. The decreasing reactor coolant level was the result of closure of the "A" Reactor Feed Pump Turbine (RFPT) steam inlet valves. During restoration of the "B" RFPT Overspeed Trip Test a non-licensed operator (NLO) closed the steam supply drain valves on the "A" RFPT train instead of the "B" train. Closure of the drain valves did not cause loss of feedwater to the reactor vessel. Upon discovery of the mistake the NLO tried to correct the error and closed the "A" RFPT steam inlet valves. This led to the loss of feedwater flow to the reactor vessel.A reactor SCRAM was received per design at Level 3 (+11.4 inches) and all control rods fully inserted. Operators manually initiated the Reactor Core Isolation Cooling system to restore and maintain reactor vessel level. No emergency core cooling system initiation setpoint was reached and no safety relief valves lifted. The normal heat sink (main condenser) remained available during this event.The root cause of this event was determined to be a lack of commitment to Human Performance Program implementation.
416 | 4162008005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162008005R00.pdf | 2008-10-26 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 50 | On October 26, 2008 at 1125, Grand Gulf Nuclear Station was in Mode 1 operating at approximately 50 percent power when an automatic reactor scram was initiated by the Reactor Protection System (RPS) on detection of fast closure of the Turbine Control Valves (TCVs). After the scram reactor water level decreased to -2.67 inches and was maintained with the reactor feedwater system. There were no inoperable structures, systems, or components at the start of the event that contributed to the event. The normal heat sink (main condenser) remained available and no Main Steam Safety Relief Valves actuations occurred during the event. All control rods fully inserted and all safety systems functioned as designed and responded properly.The cause of this event was due to the Main Generator Thyristor Voltage Regulator (TVR transferring from automatic control to manual control resulting in an unexpected under excited condition which tripped the main generator which then caused a fast closure of the TCV. It was determined that the TVR card manual reference setter was not tracking the automatic reference setter due to a defective manual reference setter motor operated potentiometer (MOP).The root cause of this event was determined to be lack of a preventive maintenance (PM) strategy for the TVR control system to ensure reliability of the voltage control circuits.
416 | 4162010001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162010001R00.pdf | 2010-03-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Grand Gulf | B | GE | PO | 100 | On March 8, 2010, at approximately 1635 hours Central Standard Time (CST), Grand Gulf Nuclear Station (GGNS) was in Mode 1 operating at approximately 100 percent power, when an actuation of the Reactor Protection System (RPS) occurred due to decreasing reactor water level. The cause of the event was the combination of the Reactor Feed Pump B (RFP B) minimum flow valve failing open due to an erroneous signal from flow instrumentation, and the Reactor Feed Pump Turbine A (RFPT A) tripping due to speed demand mismatch caused by control valve linkage binding. One feed pump could not support the reactor feedwater demand, resulting in a reactor scram per design on Reactor Water Level 3 (+11.4 inches narrow range). The appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. All control rods inserted to shut down the reactor. No loss of offsite or Engineered Safety Feature (ESF) power occurred. No emergency core cooling system (ECCS) initiation setpoint was reached and no safety relief valves (SRVs) lifted. The normal heat sink (main condenser) remained available during this event. Reactor water level was restored and maintained by the condensate and feedwater system.
416 | 4162012002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162012002R00.pdf | 2012-02-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Grand Gulf | B | GE | PO | 22 | On February 19, 2012, at 1904 hours Central Standard Time (CST), Grand Gulf Nuclear Station (GGNS) was in Mode 1 operating at approximately 22 percent power during a planned plant shutdown with the Reactor Feed Pump A (RFP A) secured when a manual reactor scram was initiated due to decreasing reactor pressure vessel (RPV) water level. The cause of the event was a combination of the isolating steam valve to the Reactor Feed Pump B (RFP B) being out of position, ninety percent closed, which isolates the main steam header from RFP B and a planned power reduction. The power reduction resulted in the turbine bypass valves (TBPV) opening as designed, then when the TBPVs reached 16 percent open, RFP B began to decrease in speed. This resulted in a decreasing level in the RPV. As level decreased, the Control Room Supervisor directed a manual scram be inserted prior to reaching the low level scram set point (+11.4 inches narrow range). After the scram, Reactor Core Isolation Cooling (RCIC) was manually started to inject water into the RPV and RFP A was restarted to restore and maintain reactor water level. The appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. All control rods inserted to shut down the reactor. No emergency core cooling system (ECCS) initiation setpoint was reached and no safety relief valves (SRVs) lifted. The normal heat sink (main condenser) remained available during this event.
416 | 4162012008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162012008R00.pdf | 2012-12-29 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On December 29, 2012, at 00:18 Central Standard Time, Grand Gulf Nuclear Station was operating in Mode 1 at 100 percent thermal power when an unexpected Reactor SCRAM occurred due to a Main Generator trip. All systems responded as expected with the exception of Safety Relief Valve (SRV) 1B21F047A, which was slow to close, and high pressure feedwater heater start-up outlet valve 1N21F010B, which did not open. The shift immediately entered the appropriate Off Normal Event Procedures. Reactor water level was controlled using the normal condensate/feedwater system throughout the event. All control rods inserted after Reactor Protection System signals were received. There were no Emergency Core Cooling System actuations. The plant was stabilized with pressure control on the main turbine bypass valves, and level controlled on the start-up level control valve. The plant responded to the trip as designed with the exception of the one SRV and one start-up outlet valve noted above. The cause of the SCRAM was not initially determined. Additional monitoring equipment was installed to detect a similar condition. Following a second SCRAM on January 4, 2013, the cause was determined to be grounding of the Main Generator 'A' Phase Neutral Current Transformer. There were no adverse effects on the health and safety of the public.
416 | 4162013001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162013001R00.pdf | 2013-01-04 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 94 | At 23:37 Central Standard Time on January 4, 2013, Grand Gulf Nuclear Station experienced an unexpected Reactor SCRAM caused by a Main Generator trip. The plant was operating in Mode 1 at 94 percent thermal power. All safety systems responded per design. Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate Off Normal Event Procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve, although high pressure feedwater heater start-up outlet valve 1N21F010B did not open. The cause of the SCRAM was the Main Generator 'A' Phase Neutral Current Transformer (CT) experienced partial grounding due to inadequate clearance between the micarta plate bolts and bottom of the CT allowing the conductors to come in contact with a bolt providing a shunt path to ground. This was caused by inadequate workmanship and work instructions not specifying the clearance during installation. There were no adverse effects on the health or safety of the public as a result of this event. The micarta plate bolts were subsequently removed or cut to provide adequate clearance prior to plant restart.
416 | 4162013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162013002R00.pdf | 2013-01-14 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | At 18:05 Central Standard Time on January 14, 2013, Grand Gulf Nuclear Station experienced an automatic Reactor SCRAM caused by a Turbine Trip due to a Main Generator lockout. The plant was operating in Mode 1 at 100 percent thermal power. All safety systems responded per design. Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve, although high pressure feedwater heater start-up outlet valve 1N21F010B did not open when placing the start-up level control valve in service. There were no adverse effects on the health and safety of the public as a result of this event. The cause of the SCRAM was the Main Generator Isolated Phase Bus Cooling System experienced partial grounding due to design configuration of the horizontal bushing in an energized section of the bus, in close proximity to a degraded viewing port, which allowed water accumulation that created a ground condition. Additional portions of the isophase bus with seal off bushings were de-energized, and covers were installed over the viewing ports prior to plant restart.
416 | 4162013003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162013003R00.pdf | 2013-07-30 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | At 14:32 Central Daylight Time on July 30, 2013, Grand Gulf Nuclear Station experienced an unexpected Reactor SCRAM from 100% thermal power due to high reactor pressure detected by the Reactor Protection System. Operations staff immediately entered the appropriate off-normal event procedures. Reactor Core Isolation Cooling (RCIC) initiated and injected briefly during the transient, The RCIC initiation signal was valid, but not required to maintain the reactor vessel water level. Reactor levels were verified and RCIC was subsequently secured. All other systems operated as expected. Reactor pressure was controlled by discharging steam to the main condenser via the main turbine bypass valves. Reactor water level was controlled using the condensate and feedwater systems via the startup level control valve. No safety relief valves actuated. The cause of the SCRAM was a human performance-induced error due to inadequate troubleshooting activities on the Turbine Stress Evaluator (TSE). A temperature transmitter failure was not recognized nor corrected, thereby resulting in a false high turbine stress temperature signal. Upon restoration of the TSE, the incorrect signal forced turbine control valves in the closed direction and resulted in a high reactor pressure transient. Procedures and work orders are being revised to prevent recurrence of this event. There were no adverse effects to the health and safety of the public.
416 | 4162014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162014002R00.pdf | 2014-03-17 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 41 | On March 17, 2014, at 05:14 Central Daylight Time with the plant at 41 percent rated core thermal power during power ascension from refueling outage 19, Grand Gulf Nuclear Station manually actuated the Reactor Protection System (RPS) to shut down the reactor due to a steam leak in the turbine building. All control rods fully inserted and all safety systems operated as designed. The Main Steam Isolation Valves (MSIVs) were manually shut and the Reactor Core Isolation Cooling (RCIC) System was manually initiated. No Safety Relief Valves (SRVs) actuated automatically. Manual cycling of SRVs and RCIC was used to maintain reactor water level and pressure within normal bands. Group 2 and 3 Residual Heat Removal (RHR) isolation signals were received. However, no valve movement occurred since the affected valves are normally closed. The cause of the manual RPS actuation was a steam leak in the turbine building resulting from a failed turbine first stage pressure sensing line (TFSPSL) followed by a failed main steam line four inch drain line. The failed drain line has been replaced and both TFSPSLs have been removed. Temporary modifications have been issued for implementation of "a current source" strategy. This action removes the TFSPSLs and installs two electronic modules as an interim action while a design change to eliminate the need for the TFSPSLs is being developed. The event posed no threat to public health and safety.
416 | 4162014003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162014003R00.pdf | 2014-03-29 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 87 | On March 29, 2014, at 10:08 Central Daylight Time with the plant at 87 percent rated core thermal power, Grand Gulf Nuclear Station experienced an automatic actuation of the reactor protection system and plant scram due to a Main Turbine Overspeed Protection Load Reject Relay (LRR) fault. All control rods fully inserted and safety systems operated as designed. No safety relief valves lifted and no isolation signals were received. Reactor Water Level increased, resulting in a Level 9 SCRAM signal which caused an automatic trip of both reactor feed pumps to reduce reactor water inventory. However, reactor feedwater was promptly restored. The cause of the event was an L-RR fault which caused a fast closure signal to the Main Turbine Control Valves (TCV). The TCV closure resulted in the automatic actuation of the reactor protection system and plant scram. Investigations determined the cause of the LRR fault was a failed ceramic capacitor on a Multiplier Module (MM) card. The failed MM card has been replaced as well as the LRR power supply, power measurement input module and voltage measurement input module. The event posed no threat to public health and safety.
416 | 4162015001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162015001R00.pdf | 2015-02-07 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | On Saturday, February 7, 2015, at 1856 hours Central Standard Time, with the plant at 100 percent thermal power, Grand Gulf Nuclear Station experienced an automatic actuation of the reactor protection system (RPS) and subsequent reactor SCRAM. The "B" main transformer differential trip caused a generator lockout. The generator lockout was followed by a turbine control valve fast closure (RPS SCRAM signal), turbine trip and reactor SCRAM. All control rods fully inserted and safety systems operated as designed. Eleven safety relief valves (SRVs) lifted to control pressure. Feedwater was manually secured to transfer to the startup level control mode. There were no emergency core cooling systems (ECCS) actuations required or initiated in response to this SCRAM. Turbine bypass valves opened to stabilize pressure causing reactor water level to fluctuate. Residual heat removal (RHR) group 2 and 3 containment isolation signals were received on low level 3. A hard ground was discovered on the non-safety protective circuitry between the current transformer and control cabinet on "B" main transformer. The faulted cables and other similar cables were determinated and alternate wiring and conduit was installed before placing the transformers back into service. The event posed no threat to public health and safety.
416 | 4162016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162016002R01.pdf | 2016-03-29 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 37 | On March 29, 2016, at 1123 Central Daylight Time, Grand Gulf Nuclear Station was operating in Mode 1 and ascending in power at approximately 37 percent rated thermal power when an unplanned uncomplicated automatic reactor SCRAM occurred. A generator lockout was received due to a Main Transformer 'B' Differential Relay Trip which was followed by a turbine control valve fast closure, turbine trip, and reactor SCRAM. The Reactor Protection System and all other safety systems functioned as designed. The direct cause of this event was the premature actuation of the "B" Main Transformer Current Differential Relay (1N41-M703B) that resulted in a main generator lockout, turbine trip, and automatic Reactor SCRAM. The root cause of this event is maintenance fundamental procedures for lifting and landing leads and troubleshooting were not followed by supplemental personnel performing transformer re-wiring project to maintain configuration control. Corrective actions included correcting the transformer wiring issue, revision of procedures, and strengthening maintenance training and qualification processes. This event posed no threat to public health and safety.
416 | 4162016004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162016004R01.pdf | 2016-06-17 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Grand Gulf | B | GE | PO | 65 | On June 17, 2016, at 0256 Central Daylight Time, Grand Gulf Nuclear Station experienced an automatic reactor scram. Prior to the scram, Grand Gulf Nuclear Station was operating in Mode 1 at approximately 65% rated thermal power and performing the Turbine Stop and Control Valve Operability Surveillance. During the surveillance, after the 'B' Turbine Stop valve was closed per procedure, the 'D' Turbine Stop Valve unexpectedly closed. The 'A' and 'C' Turbine Control Valves were then challenged to control Turbine and Reactor pressure resulting in Reactor pressure and power oscillations. The causes of this event were inadequate procedural guidance and the failure to use conservative decision making strategy. Corrective actions included replacement of the defective solenoid valves, and the revision of the applicable testing and Operations performance standards procedures.
416 | 4162016005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162016005R01.pdf | 2016-06-25 | QR5 | Turbine Trip | [45 empty] | Grand Gulf | B | GE | PO | 99 | On June 25, 2016, at 1407 Central Daylight Time, Grand Gulf Nuclear Station was operating in Mode 1 at approximately 98.75 percent rated thermal power, performing final power ascension to 100% power with Reactor Recirculation Flow Control Valves, when an unplanned automatic reactor SCRAM occurred. All safety systems responded per design. Two Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate Off Normal Event Procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve. The cause of this event was a failed operational amplifier installed on circuit card that provided input to the Turbine Control System Channel 1. Corrective actions include the replacement of the rate limiter circuit cards with re-furbished cards. Future corrective actions will include the implementation of a modification to replace the turbine control system with a digital control system. There were no actual nuclear safety consequences or radiological consequences during the event.
416 | 4162017003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162017003R02.pdf | 2017-04-04 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 75 | At 00:10 on, April 4, 2017, the reactor was manually shutdown from approximately 75 percent core thermal power due to condensate storage tank level lowering to 24 feet. All control rods fully inserted and all systems actuated and operated as designed. No safety relief valves actuated. Reactor level and pressure were controlled within normal bands. Reactor core isolation cooling (RCIC) was manually initiated for level control. Decay heat was removed via steam discharge to the condenser, and to the suppression pool via RCIC. The electrical grid was stable and supplying plant loads. The cause of the condensate depletion was a condensate system leak. <br /><br /> The condensate system leak was a failed pipe connection caused by cycling water injection valves that induced excessive vibration on the pipe flange. A failing Turbine Control Card caused the faulty signals; which led to the water injection valves cycling. The piping and flange connection were repaired, and the Turbine Control Card was replaced. In addition, the Turbine Control System is planned to be replaced in Refueling Outage 22 in 2020. <br /><br /> All other systems operated as designed, and there were no actual nuclear safety or radiological consequences during the event.
416 | 4162018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162018001R01.pdf | 2018-01-30 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 91 | On January 30, 2018, Grand Gulf Nuclear Station (GGNS) was operating in Mode 1 at 91% power and was in the process of increasing power. At 1739 hours CST on January 30, 2018, GGNS experienced main turbine control valve (TCV) position changes of between 3 and 5 percent and main generator output load changes of approximately 20 megawatts with a periodicity of approximately 3 seconds.<br /><br /> At 1822 on January 30, 2018, operators performed a manual shut down of the reactor by moving the reactor mode switch from RUN to SHUTDOWN to place the unit in Mode 3. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. The TCV position changes were caused by an inappropriately high gain setting in one channel of the TCVs resonance compensator circuit. Corrective actions include adjustments to the control circuit, and revision of work task documents for adjustment of the control circuits. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
416 | 4162018009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162018009R01.pdf | 2018-09-14 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Grand Gulf | B | GE | PO | 100 | On September 14, 2018, Grand Gulf Nuclear Station (GGNS) was operating in Mode 1 at 100 percent power and performing a backfill of a 6A feedwater heater level transmitter. At 1638 hours technicians began backfilling operations of the transmitter. During the activity, GGNS experienced the 6A feedwater heater drain valve going full open and subsequent heater drain tank level control valve oscillations, which resulted in automatic condensate booster pump and feedwater pump trips on low suction pressure. The feedwater pump trip was followed by a reactor recirculation flow control valve runback. At 1644 hours operators performed a manual reactor protection system shut down of the reactor to place the unit in Mode 3. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. The root cause of the event was that test instructions did not include dynamic tuning of Air Operated Valves. The cause of the manual shutdown was operator response in anticipation of reactor water level lowering to the 11.4 inch automatic scram setpoint. Corrective actions included adjustments to the heater drain tank level control circuit. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety for this event.
416 | 4162018010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4162018010R01.pdf | 2018-12-12 | QR6 | Manual Reactor Trip | [45 empty] | Grand Gulf | B | GE | PO | 100 | At approximately 1351 hours on Wednesday, December 12, 2018, while operating in MODE 1 at approximately 100 percent power, the Grand Gulf Nuclear Station was manually shutdown in response to Main Steam Bypass Stop and Control Valve A drifting open. The Main Steam Line Isolation Valves were manually closed as a mitigating action to control reactor pressure vessel rate of depressurization and cooldown. During the scram recovery, the Reactor Core Isolation Cooling (RCIC) System injection was delayed. During preparation to initiate High Pressure Core Spray (HPCS) System the operator noted that RCIC had started to inject but due to the water level and the rate of change the operator started HPCS. HPCS was secured once water level was trending higher. RCIC was utilized for reactor water level control until RCIC was placed in standby at 1645 hours. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. <br /><br /> The direct cause of the condition is a failed linear variable differential transformer (LVDT) in the actuator for the Main Steam Bypass Stop and Control Valve A. The cause of the event was the existing operating guidance for the turbine electro hydraulic control (EHC) did not provide procedural steps to manually swap from a faulty controller to an auxiliary controller, which would have allowed the operators to close the valve. Corrective actions included swapping wiring from the failed LVDT to an installed spare LVDT and enhancement of the procedural guidance to ensure operators have the tools to manually swap from a faulty controller to an auxiliary controller. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of systems as listed in 10 CFR50.73(a)(2)(iv)(B), specifically the Reactor Protection System, HPCS, and RCIC systems were actuated.
423 | 4231987001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987001R00.pdf | 1987-01-13 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 13, 1987 AT 1055 WITH THE PLANT AT 100% POWER IN MODE 1, THE PLANT RECEIVED AN AUTOMATIC REACTOR TRIP AS A RESULT OF AN AUTOMATIC TURBINE TRIP. THE TURBINE TRIP WAS DUE TO A LOSS OF CONDENSER VACUUM IN THE 'A' MAIN CONDENSER. LOSS OF CONDENSER VACUUM WAS CAUSED BY THE AUTOMATIC TRIPPING OF THE 'A' AND THE 'B' CIRCULATING WATER PUMPS DUE TO LOW LUBE WATER PRESSURE. LOW LUBE WATER PRESSURE WAS A RESULT OF ISOLATION OF THE NORMAL LUBE WATER SUPPLY FROM THE SERVICE WATER SYSTEM AND OPERATION ON THE TEMPORARY BACKUP LUBE WATER SUPPLY FROM THE CONSTRUCTION DOMESTIC WATER SYSTEM, CONCURRENT WITH LOW CONSTRUCTION DOMESTIC WATER SUPPLY PRESSURE. THE ROOT CAUSE OF THIS TRIP WAS INADEQUATE COMMUNICATIONS BETWEEN OPERATIONS PERSONNEL COMPOUNDED BY INADEQUATE OPERATIONAL INSTRUCTIONS ON THE BYPASS JUMPER. AS CORRECTIVE ACTION THE OPERATIONAL PROCEDURES HAVE BEEN UPDATED AND OPERATIONS PERSONNEL HAVE BEEN BRIEFED ON THE IMPORTANCE OF CLEAR, UNAMBIGUOUS COMMUNICATIONS. THIS REPORT IS BEING SUBMITTED AS REQUIRED BY 10CFR50.73(A)(2)(IV). ATIONS. THIS REPORT IS BEING SUBMITTED AS REQUIRED BY 10CFR50.73(A)(2)(IV).
423 | 4231987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987002R00.pdf | 1987-01-14 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 3 | P | WE | PO | 7 | POWER LEVEL - 007%. ON 1/14/87 AT 0924 HOURS WHILE IN MODE 1 (POWER OPERATION) AT 7% POWER (562 DEGREES FAHRENHEIT/2260 PSIG) A REACTOR TRIP OCCURRED WHEN THE REACTOR OPERATOR ACCIDENTLY RESET THE SOURCE RANGE HIGH FLUX REACTOR TRIP BLOCK. ALL AUTOMATIC ACTIONS OCCURRED AS REQUIRED AND THE OPERATORS CARRIED OUT THE STEPS FOR REACTOR TRIP AND REACTOR TRIP RECOVERY PER PROCEDURES. THE REACTOR WAS STABLE AT HOT STANDBY CONDITION AT APPROXIMATELY 0945. THE CAUSE OF THE EVENT WAS OPERATOR ERROR COMPOUNDED BY A SENSITIVE SWITCH. THE OPERATOR WAS REACHING TO SILENCE AN ANNUNCIATOR WHEN HE BRUSHED THE SOURCE RANGE BLOCK AND RESET SWITCH CAUSING IT TO RESET. THE INSTRUMENT AND CONTROLS DEPARTMENT (I&C) DETERMINED THAT THE SWITCH REQUIRED ONLY 5 DEGREES TO 10 DEGREES OF ROTATION TO RESET. ADDITIONALLY, A HANDLE EXTENDER HAD BEEN ADDED FOR HUMAN FACTORS CONSIDERATIONS. THE EXTENDERS WERE REMOVED AND CAUTION TAGS ADDED. A PLANT MODIFICATION IS BEING EVALUATED TO INVESTIGATE MODIFICATION OR REPLACEMENT OF THE SWITCHES WITH A DESIGN WHICH WOULD PROTECT AGAINST ACCIDENTAL CONTACT. THIS REPORT IS BEING SUBMITTED AS REQUIRED BY 10CFR50.73(A)(2)(IV).
423 | 4231987008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987008R00.pdf | 1987-03-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 3/7/87 AT 1745 HOURS, WHILE OPERATING AT 100% POWER IN MODE 1, A REACTOR TRIP OCCURRED DUE TO LOW LOW STEAM GENERATOR LEVEL IN THE D STEAM GENERATOR. THE CONTROL ROOM OPERATORS VERIFIED THE OPENING OF ALL REACTOR TRIP BREAKERS, AND FULL INSERTION OF ALL CONTROL RODS. IMMEDIATELY PRIOR TO THE TRIP, THE OPERATORS OBSERVED THAT THERE WAS A FEED FLOW/STEAM FLOW MISMATCH ON ALL THE STEAM GENERATORS, THAT THE FEEDWATER FLOW TO THE D GENERATOR HAD DROPPED TO 0 GPM, AND THAT THE MAIN FEEDWATER ISOLATION VALVE TO THAT GENERATOR, 3FWS*CTV41D, HAD CLOSED. THEY ATTEMPTED TO REOPEN THE VALVE, BUT WERE NOT ABLE TO DO SO BEFORE THE PLANT TRIPPED. THE FAILED VALVE COULD NOT BE REOPENED AFTER THE TRIP. THE ROOT CAUSE OF THE REACTOR TRIP WAS EQUIPMENT FAILURE. AN INSPECTION OF THE ISOLATION VALVE INDICATED THAT THE FAILURE WAS DUE TO THE FAILURE OF ONE OF THE SOLENOID VALVES CONTROLLING HYDRAULIC OIL FLOW TO THE VALVE. THE FAILURE OF THE SOLENOID VALVE WAS INTERNAL TO THE SOLENOID COIL. THE SOLENOID VALVE WAS REPLACED. A REVIEW OF THE LITERATURE AND WORK HISTORY REVEALED NO OTHER PROBLEMS WITH THIS TYPE OF SOLENOID, SO IT HAS BEEN DETERMINED THAT THIS IS AN ISOLATED FAILURE. NO FURTHER WORK IS PLANNED.
423 | 4231987021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987021R00.pdf | 1987-04-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Millstone 3 | P | WE | PO | 15 | POWER LEVEL - 015%. AT 1808 ON APRIL 12, 1987 WHILE AT 15% POWER IN MODE 1, A REACTOR TRIP OCCURRED DUE TO LOW-LOW STEAM GENERATOR LEVEL FOLLOWING A FEEDWATER ISOLATION SIGNAL. ALL EQUIPMENT OPERATED AS EXPECTED AND THE PLANT WAS SAFELY BROUGHT TO A SHUTDOWN CONDITION. THE CAUSE OF THE EVENT WAS OPERATOR ERROR. THE STEAM DUMP AND STEAM GENERATOR WATER LEVEL CONTROL WERE IN MANUAL WHILE ATTEMPTING TO ROLL THE MAIN TURBINE DURING A PLANT STARTUP. A LEVEL OSCILLATION IN A STEAM GENERATOR CAUSED A FEEDWATER ISOLATION WHICH LED TO A REACTOR TRIP ON STEAM GENERATOR LOW-LOW LEVEL. TO PREVENT RECURRENCE OF THIS EVENT, THE TRIP WAS DISCUSSED WITH ALL LICENSED OPERATORS EMPHASIZING OPERATIONS UTILIZING THE MOTOR DRIVEN FEED PUMP. REVISED PROCEDURAL GUIDANCE HAS BEEN PROVIDED TO THE OPERATORS ON APPROPRIATE MEASURES TO MAINTAIN LEVELS IN THE STEAM GENERATORS DURING PLANT STARTUPS.
423 | 4231987020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987020R00.pdf | 1987-04-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 66 | POWER LEVEL - 066%. ON APRIL 12, 1987 AT 0618 HOURS, WHILE OPERATING AT 66% POWER IN MODE 1, A REACTOR TRIP OCCURRED DUE TO LOW LOW STEAM GENERATOR LEVEL IN THE D STEAM GENERATOR. THE CONTROL ROOM OPERATORS WERE IN THE PROCESS OF INCREASING POWER DURING THE INITIAL START UP FOLLOWING A SCHEDULED MAINTENANCE OUTAGE. APPROXIMATELY 15 MINUTES PRIOR TO THE TRIP, THE OPERATORS HAD INCREASED REACTOR POWER FROM 56% TO 66% WITHIN A 16 MINUTE INTERVAL. WHEN AT 66% POWER THE SPEED CONTROLLER TO THE A TURBINE-DRIVEN FEEDWATER PUMP (3FWS- P2A) BEGAN TO OSCILLATE. THE RESPONSIBLE OPERATOR ASSUMED MANUAL CONTROL OF THE PUMP IN AN ATTEMPT TO STOP THE OSCILLATIONS. HE WAS UNABLE TO DO SO BEFORE THE LEVEL IN THE D STEAM GENERATOR FELL TO THE LOW LOW LEVEL AND THE PLANT TRIPPED. THE OPERATORS VERIFIED THE OPENING OF ALL REACTOR TRIP BREAKERS AND FULL INSERTION OF ALL CONTROL RODS. THE ROOT CAUSE OF THE REACTOR TRIP IS EQUIPMENT FAILURE. THE PRIMARY CAUSE WAS AN AIR LEAK IN AN AIR SUPPLY LINE TO THE D FEEDWATER REGULATING VALVE, WHICH RESULTED IN LOW LOW STEAM GENERATOR LEVEL. THE LEAK HAS BEEN FIXED. A CONTRIBUTING CAUSE WAS OSCILLATIONS IN THE A TURBINE-DRIVEN FEEDWATER PUMP CONTROLLER. A VENDOR REPRESENTATIVE WAS CONSULTED AND FOUND NO PROBLEMS WITH THE PUMP CONTROLLER. IT RESPONDED CORRECTLY DURING A PLANT STARTUP ON APRIL 13, 1987. NO OTHER WORK IS PLANNED.
423 | 4231987025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987025R00.pdf | 1987-05-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 44 | POWER LEVEL - 044%. ON MAY 7, 1987, AT 1944 HOURS, WHILE REDUCING POWER FROM 97% TO 40%, IN MODE 1, A REACTOR TRIP OCCURRED AT 44% DUE TO LOW LOW LEVEL IN THE D STEAM GENERATOR. THE CONTROL ROOM OPERATORS WERE IN THE PROCESS OF REDUCING POWER IN ORDER TO REMOVE THE MOTOR-DRIVEN FEEDWATER PUMP FROM SERVICE. AT APPROXIMATELY 25 MINUTES PRIOR TO THE TRIP (1919 HOURS), WHILE AT 97% POWER THE OPERATORS RECEIVED A HIGH BEARING TEMPERATURE ALARM ON THE MOTOR-DRIVEN FEEDWATER PUMP. AT 1930 HOURS THEY BEGAN A POWER REDUCTION TO TAKE THE PUMP OFF LINE. AT THE TIME THE MOTOR-DRIVEN PUMP WAS STOPPED, AT 64%, THE STEAM GENERATOR LEVELS BECAME UNSTABLE AND THE FEEDWATER FLOWS WERE OSCILLATING. THE A STRING FOURTH POINT FEEDWATER HEATER DRAIN PUMP THEN TRIPPED WHICH DECREASED THE FEEDWATER FLOW. THE OPERATORS WERE UNABLE TO CONTROL THE LEVEL OSCILLATIONS IN THE STEAM GENERATORS AND THE REACTOR TRIPPED FROM 44% POWER ON LOW LOW LEVEL IN THE D STEAM GENERATOR. THERE WERE NO EQUIPMENT MALFUNCTIONS AS A RESULT OF THE TRIP. THE ROOT CAUSE OF THE REACTOR TRIP WAS PROCEDURE INADEQUACY. THE PROCEDURES ON ALARM RESPONSES TO HIGH BEARING TEMPERATURE ALARMS AND ON REMOVING A FEEDWATER PUMP FROM SERVICE HAVE BEEN REVISED TO PROVIDE THE OPERATORS WITH MORE GUIDANCE ON THESE ACTIONS IN ORDER TO PREVENT A RECURRENCE OF THIS EVENT.
423 | 4231987026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987026R00.pdf | 1987-05-14 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 3 | P | WE | PO | 69 | POWER LEVEL - 069%. ON MAY 14, 1987 AT 1007 HOURS, WHILE OPERATING IN MODE 1 AT 69% POWER, A REACTOR TRIP OCCURRED DUE TO THE OPENING OF THE TRAIN B REACTOR TRIP BREAKER (3RPS*ACB-RTB). THE SIGNAL THAT CAUSED 3RPS*ACB-RTB TO OPEN HAS NOT BEEN DETERMINED AND IS CONCLUDED TO BE SPURIOUS. ALL EQUIPMENT OPERATED AS EXPECTED IN RESPONSE TO THE TRIP AND THE PLANT WAS STABLE IN MODE 3 (HOT STANDBY) AT APPROXIMATELY 1035 HOURS. AT THE TIME OF THE TRIP, SURVEILLANCE TESTING WAS IN PROGRESS ON THE TRAIN A REACTOR TRIP BREAKER (3RPS*ACB-RTA). BASED ON INTERVIEWS WITH PERSONNEL INVOLVED WITH THE TEST, A REVIEW AND WALKDOWN OF THE PROCEDURE, AND SUCCESSFUL PAST PERFORMANCES OF THE SURVEILLANCE AT POWER, IT WAS CONCLUDED THAT THE OPENING OF 3RPS*ACB-RTB WAS NOT THE RESULT OF THE SURVEILLANCE IN PROGRESS. EXTENSIVE POST TRIP TESTING AND INSPECTION OF THE REACTOR TRIP BREAKERS AS WELL AS ASSOCIATED SOLID STATE PROTECTION SYSTEM (SSPS) COMPONENTS AND WIRING INDICATED THAT THESE SYSTEMS ARE FULLY FUNCTIONAL AND OPERATING ACCORDING TO THEIR INTENDED DESIGN. THE INVESTIGATION HAS DETERMINED THE TRIP TO BE SPURIOUS. THE TESTING AND INVESTIGATION COMPLETE THE CORRECTIVE ACTION.
423 | 4231987027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987027R00.pdf | 1987-06-05 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1323 ON JUNE 5, 1987, WITH THE PLANT AT 100% POWER, THE NORMAL SUPPLY BREAKER TO TRAIN 'A' VITAL BUS 34C WAS TRIPPED OPEN. THE MAIN STEAM ISOLATION VALVES IMMEDIATELY CLOSED ON LOSS OF 120VAC TO THEIR SOLENOID TEST CONTROL CIRCUITRY. A REACTOR TRIP FOLLOWED ON LOW-LOW STEAM GENERATOR LEVELS, WHICH SIGNALED A TURBINE TRIP. A TRAIN 'A' LOSS OF POWER SIGNAL WAS GENERATED, THE EMERGENCY DIESEL GENERATOR STARTED AND SUCCESSFULLY ENERGIZED VITAL LOADS. THE MAIN STEAM ATMOSPHERIC RELIEF VALVES AND STEAM GENERATOR CODE SAFETIES OPENED AS DESIGNED. A TRAIN 'A' CONTROL BUILDING ISOLATION, AND TRAIN 'A' AND 'B' FEEDWATER ISOLATION RESULTED FROM THE EVENT. THE PLANT WAS IN HOT STANDBY (MODE 3) BY 1600 HOURS, JUNE 5, 1987. THE CAUSE OF BUS 34C TRIP WAS A RESULT OF PERSONNEL ERROR, DUE TO AN OPERATOR DROPPING A RACKING MOTOR ONTO THE 4.16KV SWITCHGEAR.
423 | 4231987031 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987031R01.pdf | 1987-06-14 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JUNE 14, 1987 AT 0320 WITH THE PLANT AT 100% POWER (MODE 1) THE REACTOR TRIPPED AS A RESULT OF A TURBINE TRIP. THE TURBINE TRIPPED ON LOW BEARING LUBE OIL HEADER PRESSURE IMMEDIATELY FOLLOWING A TRIP OF THE TURNING GEAR OIL PUMP (TGOP). THE TGOP HAD BEEN AUTOSTARTED APPROXIMATELY 9 SECONDS EARLIER AS PART OF WEEKLY TURBINE/GENERATOR PREVENTIVE MAINTENANCE TESTING, AND WAS NOT THE PRIMARY SOURCE OF LUBE OIL HEADER PRESSURE. PRESSURE WAS PRIMARILY SUPPLIED BY THE (TURBINE) SHAFT DRIVEN OIL PUMP, WHICH WAS OPERATING CORRECTLY. ALL EQUIPMENT OPERATED AS EXPECTED IN RESPONSE TO THE TRIP AND THE PLANT RETURNED TO POWER OPERATION (MODE 1) AT APPROXIMATELY 2012 HOURS. THE CAUSE FOR THIS EVENT WAS A DEFECTIVE BEARING HEADER RELIEF VALVE AND AN OVERSIZED TURNING GEAR OIL PUMP. AS CORRECTIVE ACTION, THE BEARING HEADER RELIEF VALVE WAS REPAIRED AND THE IMPELLER ON THE TGOP WAS SHAVED TO LOWER PRESSURE.
423 | 4231987034 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231987034R00.pdf | 1987-09-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 23, 1987, AT 1351 HOURS, WHILE OPERATING AT 100% POWER IN MODE 1, A REACTOR TRIP OCCURRED DUE TO LOW LOW STEAM GENERATOR LEVEL IN THE A STEAM GENERATOR. THE OPERATORS VERIFIED THAT ALL CONTROL RODS WERE FULLY INSERTED, AND THAT ALL REACTOR TRIP BREAKERS HAD OPENED. IMMEDIATELY PRIOR TO THE TRIP, THE OPERATORS OBSERVED THAT THERE WAS A FEED FLOW/STEAM FLOW MISMATCH IN ALL THE STEAM GENERATORS, AND THAT THE MAIN FEEDWATER ISOLATION VALVE TO THE A STEAM GENERATOR, 3FWS*CTV41A, HAD CLOSED. THE PLANT TRIPPED BEFORE ANY CORRECTIVE MEASURES COULD BE TAKEN. THE ROOT CAUSE OF THE EVENT WAS EQUIPMENT FAILURE. AN INSPECTION OF THE ISOLATION VALVE CIRCUIT INDICATED THAT THE FAILURE WAS DUE TO THE FAILURE OF ONE OF THE SOLENOID VALVES WHICH CONTROLS HYDRAULIC OIL FLOW TO THE ISOLATION VALVE. THE FAILURE OF THE SOLENOID VALVE WAS INTERNAL TO THE SOLENOID COIL. THE SOLENOID WAS REPLACED. THERE HAVE BEEN TWO SIMILAR EVENTS OF REACTOR TRIPS DUE TO THE INADVERTENT CLOSURE OF A MAIN FEEDWATER ISOLATION VALVE.
423 | 4231988009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231988009R00.pdf | 1988-02-10 | QP5 | Excessive Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 20 | POWER LEVEL - 020%. ON FEBRUARY 10, 1988, 0907 WITH THE PLANT AT 20% POWER, 586 DEGREES, AND 2250 PSIA (MODE 1), AN AUTOMATIC REACTOR TRIP OCCURRED DUE TO A FEEDWATER TRANSIENT. AT THE TIME OF THE EVENT, THE PLANT WAS REDUCING POWER TO PERFORM TURBINE OVERSPEED TESTING. FEED CONTROL WAS BEING TRANSFERRED FROM THE MAIN FEED REGULATING VALVES TO THE FEED BYPASS VALVES. THE OPERATOR EXPERIENCED DIFFICULTY CONTROLLING STEAM GENERATOR LEVEL LEADING TO A FEEDWATER ISOLATION DUE TO HIGH LEVEL IN D STEAM GENERATOR. THE FEEDWATER ISOLATION SIGNAL ACTED TO ISOLATE FEED FROM THE STEAM GENERATORS. PRIOR TO COMPLETING RECOVERY ACTION, A REACTOR TRIP WAS RECEIVED DUE TO LOW-LOW LEVEL IN B STEAM GENERATOR. THE IMMEDIATE CAUSE OF THE EVENT WAS THE INABILITY OF THE ASSIGNED OPERATOR TO CONTROL FEEDWATER TO ALL STEAM GENERATORS SIMULTANEOUSLY. THE ROOT CAUSE OF THE EVENT WAS INSUFFICIENT JOB PLANNING ON THE PART OF SHIFT SUPERVISION. AS ACTION TO PREVENT RECURRENCE, A PROCEDURE CHANGE HAS BEEN APPROVED REQUIRING A DEDICATED OPERATOR AT THE FEED STATION AREA OF THE MAIN CONTROL BOARDS WHENEVER FEEDWATER CONTROL IS BEING SWITCHED FROM THE MAIN FEEDWATER VALVES TO THE BYPASS VALVES.
423 | 4231988014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231988014R00.pdf | 1988-04-13 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON APRIL 13, 1988 AT 1652 HOURS, WITH THE PLANT AT 1OO% POWER IN MODE 1, THE PLANT RECEIVED AN AUTOMATIC REACTOR TRIP AS A RESULT OF A TURBINE TRIP. THE TURBINE TRIP WAS DUE TO A LOSS OF CONDENSER VACUUM IN THE 'A' MAIN CONDENSER. LOSS OF CONDENSER VACUUM WAS CAUSED BY THE AUTOMATIC TRIPPING OF THE 'A' AND THE 'B' CIRCULATING WATER PUMPS (CWS) DUE TO HIGH DIFFERENTIAL PRESSURE ACROSS THE TRAVELING SCREENS. HIGH DIFFERENTIAL PRESSURE ACROSS THE TRAVELING SCREENS WAS A RESULT OF: A) LEAKING STRAINER ISOLATION VALVES ON THE OPERATING TRAIN WHICH REQUIRED THAT THE ASSOCIATED SCREEN WASH PUMP BE STOPPED IN ORDER TO CLEAN THE STRAINER, B) ONLY ONE SCREEN WASH PUMP BEING IN OPERATION, AND C) ENVIRONMENTAL CONDITIONS CAUSING HIGHER THAN NORMAL SEAWEED FOULING ON THE SCREENS. ROOT CAUSE OF THE TRIP WAS LEAKING ISOLATION VALVES ON THE SCREEN WASH DUPLEX STRAINERS REQUIRING THE OPERATING PUMP TO BE REMOVED FROM SERVICE. AS CORRECTIVE ACTION, THE OPERATIONAL PROCEDURES HAVE BEEN UPDATED TO PROVIDE GUIDANCE ON CLEANING OF THE SCREEN WASH STRAINERS. THE OUT OF SERVICE PUMP HAS BEEN FIXED.
423 | 4231988023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231988023R00.pdf | 1988-10-06 | QL5 | Partial Closure of MSIVs | [45 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 10/6/88 AT 1353 HOURS, WITH THE PLANT AT 100% POWER, THE 'C' MAIN STEAM ISOLATION VALVE (MSIV), 3MSS 'CTV27C, CLOSED DURING THE PERFORMANCE OF ITS PARTIAL STROKE SURVEILLANCE TEST. THIS RESULTED IN A REACTOR TRIP DUE TO LOW LEVEL IN THE 'C' STEAM GENERATOR. ROOT CAUSE OF THE EVENT WAS PROCEDURAL INADEQUACY. IDENTIFY THE REQUIREMENT TO JUMPER THE VOLTAGE ATTENUATORS OF THE 2A AND 2B SOLENOIDS. BYPASSING THE VOLTAGE ATTENUATORS ALLOW FULL VOLTAGE TO BE APPLIED TO THE SOLENOIDS WHICH ALLOW THEM TO OVERCOME THE INHERENT DRAG FORCES WITHIN THE SOLENOIDS. THE MSIV'S SUCCESSFULLY COMPLETED THE PARTIAL STROKE SURVEILLANCE TEST AFTER ATTENUATOR JUMPERS WERE PLACED ON THE 2A AND 2B SOLENOIDS. MATERIAL CHANGES TO THE SOLENOID VALVE PISTON ROD, POSITION INDICATOR FEELER AND VALVE PLUG HAD BEEN PLANNED TO MINIMIZE THE DRAG EFFECTS WITHIN THE SOLENOIDS BY THE NEXT COLD SHUTDOWN. THE PLANT SUBSEQUENTLY WENT TO COLD SHUTDOWN ON OCTOBER 24, 1988 AND THE MATERIAL CHANGES WERE MADE TO THE 1A, 1B, 2A, AND 2B SOLENOIDS. THE APPLICABLE SURVEILLANCE PROCEDURE HAS BEEN CHANGED TO REQUIRE BYPASSING OF THE VOLTAGE ATTENUATOR ON THE APPROPRIATE MSIV SOLENOIDS.
423 | 4231988024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231988024R00.pdf | 1988-10-22 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 10/22/88 AT 0507 HOURS, WITH THE PLANT IN MODE 1 AT 100% POWER, A MANUAL REACTOR TRIP WAS INITIATED DUE TO AN ANTICIPATED TURBINE TRIP. PRIOR TO THE TRIP, THE PLANT WAS EXPERIENCING FOULING OF THE TRAVELING SCREENS DUE TO LARGE AMOUNTS OF STORM INDUCED SEAWEED AT THE INTAKE. TRIPS OF TWO CIRCULATING WATER PUMPS IN THE SAME BAY, AS A RESULT OF THE FOULED INTAKE SCREENS, CAUSED CONDENSER VACUUM TO DECREASE. DUE TO PROBLEMS AT THE INTAKE STRUCTURE AND DECAYING CONDENSER VACUUM, THE REACTOR WAS MANUALLY TRIPPED IN ORDER TO PREVENT UNNECESSARY CHALLENGES TO PLANT SYSTEMS. ROOT CAUSE OF THIS EVENT WAS ENVIRONMENTAL CONDITIONS WHICH CAUSED DEBRIS LOADINGS IN EXCESS OF THE TRAVELING SCREEN REMOVAL CAPACITY. THE ENVIRONMENTAL CONDITIONS WERE HIGH WINDS, AN INCOMING SPRING TIDE COMBINED WITH EXTREMELY CHOPPY WAVES. CORRECTIVE ACTION INCLUDES MODIFICATIONS TO THE TRAVELING SCREEN SYSTEM'S TRASH TROUGH TO INCREASE DEBRIS REMOVAL CAPABILITY THROUGH AN ALTERNATE PATH. A REVIEW OF THE DESIGN CAPACITY OF THE TRAVELING SCREENS, SCREEN WASH PUMPS AND STRAINERS IN RESPECT TO EXTREME WEATHER CONDITIONS WILL BE CONDUCTED.
423 | 4231988028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231988028R00.pdf | 1988-12-29 | QR3 | Reactivity Control Imbalance | [45 empty] | Millstone 3 | P | WE | PO | 75 | POWER LEVEL - 075%. AT 1710 ON 12/29/88, WHILE OPERATING IN MODE 1, 75% POWER 578 DEGREES, 2250 PSIA, A REACTOR TRIP ON NEGATIVE FLUX RATE OCCURRED WHEN LOSS OF THE NORMAL 4160V BUS, 34B, DEENERGIZED ONE OF THE TWO 120V SUPPLY CIRCUITS TO THE CONTROL ROD DRIVE SYSTEM. AN UNDETECTABLE FAILURE EXISTED IN THE OTHER 120V SUPPLY CIRCUITRY SUCH THAT WHEN THE FIRST SUPPLY WAS LOST, CONTROL RODS UNLATCHED. UNIT 4160V ELECTRIC BUSES WERE BEING SUPPLIED BY THE RESERVE STATION SERVICE TRANSFORMERS. THE B EMERGENCY DIESEL GENERATOR WAS STARTED FOR SURVEILLANCE TESTING. WHEN THE B EMERGENCY DIESEL GENERATOR WAS PARALLELED TO THE EMERGENCY 4160V BUS 34D, THE NORMAL TO EMERGENCY BUS TIE BREAKER OPENED ON REVERSE OVERCURRENT TRIP, DEENERGIZING THE NORMAL BUS 34B. PROCEDURES DID NOT PROVIDE ADEQUATE OPERATOR GUIDANCE ON THE REQUIRED ELECTRIC PLANT LINEUP PRIOR TO PARALLELING AN EMERGENCY DIESEL GENERATOR WHEN 4160V BUSES WERE SUPPLIED FROM THE RESERVE STATION SERVICE TRANSFORMER. THE PROCEDURE HAS BEEN CORRECTED. THE FAILURE IN THE CONTROL ROD DRIVE SYSTEM WILL BE CORRECTED DURING THE NEXT REACTOR SHUTDOWN PERIOD.
423 | 4231989008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231989008R00.pdf | 1989-05-06 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Millstone 3 | P | WE | PO | 90 | POWER LEVEL - 090%. ON 5/6/89 AT 0810 HOURS, WITH THE PLANT AT 90% POWER IN MODE 1, A MANUAL REACTOR TRIP WAS INITIATED DUE TO AN ANTICIPATED TURBINE TRIP. PRIOR TO THE TRIP, THE PLANT WAS EXPERIENCING FOULING OF THE TRAVELING SCREENS DUE TO LARGE AMOUNTS OF SEAWEED AT THE INTAKE. ROOT CAUSE OF THIS EVENT WAS DESIGN DEFICIENCY IN THAT THE TRAVELING SCREEN CAPACITY WAS INADEQUATE. RECENT CHANGES TO THE FISH RETURN SYSTEM TO BRING IT INTO COMPLIANCE WITH STATE REGULATIONS HAVE INCREASED THE SEAWEED LOADINGS ON ALL BAYS, ESPECIALLY 'A' AND 'B' BAYS. AS CORRECTIVE ACTION, A PROCEDURE CHANGE HAS BEEN IMPEMENTED WHICH ALLOWS FOR THE ISOLATION OF THE FISH SPRAY SYSTEM WHEN SEAWEED RECIRCULATION IS A CONCERN. RECOMMENDATIONS OF AN INTERNAL TASK FORCE ADDRESSING OPERATIONAL PROBLEMS WITH THE TRAVELING SCREENS WILL BE IMPLEMENTED OVER THE NEXT TWO YEARS.
423 | 4231989009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231989009R01.pdf | 1989-05-11 | QR3 | Reactivity Control Imbalance | [45 empty] | Millstone 3 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1514 ON 5/11/89 WHILE OPERATING IN MODE 1, 100% REACTOR POWER, 557 DEGREES AND 2250 PSIA, A REACTOR TRIP OCCURRED DUE TO A POWER RANGE NEUTRON FLUX HIGH NEGATIVE RATE SIGNAL. UPON DEENERGIZING A ROD DROP TIME RECORDING SYSTEM CONNECTED TO THE CONTROL ROD DRIVE SYSTEM, THE CONTROL RODS UNLATCHED. THE RECORDING SYSTEM HAD BEEN CONNECTED IN PREPARATION FOR TESTS DURING THE SECOND REFUELING OUTAGE, SCHEDULED TO START 5/12/89, ROOT CAUSE OF THE REACTOR TRIP WAS PROCEDURAL INADEQUACY IN THAT THE PROCEDURE DID NOT SPECIFY THAT CONTROL RODS MUST BE UNLATCHED PRIOR TO CONNECTING THE ROD DROP TIME RECORDING SYSTEM. SPURIOUS ROD DROP SIGNALS WERE GENERATED BY THE ROD DROP TIME RECORDING SYSTEM WHILE BEING DEENERGIZED. THIS CONDITION DOES NOT OCCUR EVERY TIME THE SYSTEM IS DEENRGIZED. TO PREVENT RECURRENCE PLANT PROCEDURES WERE CHANGED TO REQUIRE RODS TO BE UNLATCHED BEFORE CONNECTING THE ROD DROP TIME RECORDING SYSTEM. SINCE THIS EVENT OCCURRED WITHIN 48 HOURS OF THE SCHEDULED START OF THE SECOND REFUELING OUTAGE, THE REFUELING OUTAGE COMMENCED IMMEDIATELY AFTER THE TRIP.
423 | 4231990005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990005R00.pdf | 1990-01-18 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 100 | On January 18, 1990, at 0803 hours, while operating in Mode 1 at 100% power, 2250 psia and 587 degrees Fahrenheit, a manual plant trip was initiated in anticipation of an automatic trip on low low level in all four steam generators. <br /><br /> At 0802 hours, the steam flow greater than feed flow mismatch alarm annunciated for all four steam generators, followed by steam generator low level alarms. The motor-driven feedwater pump, 3FWS-P1, did not automatically start because the feedwater pump discharge header pressure did not decrease to the automatic start setpoint. The third condensate pump, 3CNM-P1B, was started prior to starting 3FWS-P1. By the time 3FWS-P1 was manually started, the steam generator levels were too low and an automatic trip on low low steam generator trip was imminent. <br /><br /> The root cause of the event was the failure of the turbine/pump coupling of 3FWS-P2B due to loss of preload on the coupling bolts due to personnel and procedural errors. Contributing causes were the pump and turbine misalignment, and inadequate coupling lubrication. In order to prevent a recurrence of feedwater pump coupling failure, changes have been made to the coupling installation procedure and the vibration alarm setpoint will be lowered.
423 | 4231990009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990009R00.pdf | 1990-03-09 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | On March 9, 1990, at 1653 hours, while operating in Mode 1 at 100% power, 2250 psia and 587 degrees Fahrenheit, an automatic turbine trip with subsequent reactor trip occurred due to high Stator Cooling Water temperature. <br /><br /> The cause of the event was the failure of the mechanical linkage on the Fischer & Porter controller for the Stator Cooling Water temperature control valve due to wear at the linkage connections. The root cause of the event was inadequate design, in that the temperature controller is mounted directly on the temperature control valve, The wear found on the mechanical linkage of the controller was induced from vibration of the temperature control valve. <br /><br /> As short term corrective action, the failed controller was replaced with a spare of the same model. The actions to prevent recurrence include replacing the original model controller with a more reliable controller with manual over-ride capabilities, and relocating the new controller to an area of low vibration.
423 | 4231990011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990011R00.pdf | 1990-03-30 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 80 | On March 30, 1990 at 1328 hours with the plant at 80% power in mode 1, a manual reactor trip was initiated due to an anticipated turbine trip from a loss of condenser vacuum. Prior to the trip, the intake structure screen wash system was removed from service to install a repaired elbow. The installation was planned for three hours. The installation would have restored the second 100% screenwash pump to service before the seasonal (i.e., April 15 - May 30) high seaweed loading began. However, the effort to manually clear the screens was not enough to prevent two Circulation Water Pumps from tripping.<br /><br /> The root cause was the failure to collect the debris from the manual screen washing, The debris recirculated into the intake stream on the tide change. Also, a major factor that prevented clearing the screens rapidly was the inability of operators to manually run the screens at any speed other than slow. In the future, an,, temporary systems used in place of the screen wash will include debris collection. Otherwise, maintenance requiring the screenwash to be turned off will be scheduled during a unit shutdown.
423 | 4231990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990013R00.pdf | 1990-04-16 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 48 | On April 16, 1990, at 1201 hours with the plant at 48% power in Mode 1, a manual reactor trip was initiated because of an anticipated turbine trip due to loss of condenser vacuum. Circulating Water Pump 3CWS-P1B was providing cooling water for Condenser Waterboxes "A" and "B". A rapid buildup of seaweed on "B" Traveling Screen resulted in an automatic trip of 3CWS-P1B due to high screen differential level. As the loss of cooling to two condenser bays would have resulted in a low condenser vacuum, a reactor trip was initiated. The reactor trip caused a Main Turbine and Generator trip in accordance with design. <br /><br /> The root cause of the event was inadequate administrative guidance in that debris was allowed to collect on the trash rack. During trash rack raking, seaweed broke free and clogged "B" Traveling Screen. Higher than normal seaweed influx and 130% flow due to cross connecting A & B waterboxes contributed to the high differential level trip. The severe weather procedure was revised August 1, 1990 to require each circulating water pump to supply only the associated waterbox during severe weather. For corrective action, the trash racks high differential level alarm point has been lowered from 15 inches to 6 inches. Personnel have been instructed to closely monitor the trash rack water levels and clean the racks before levels exceed 4 inches.
423 | 4231990014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990014R00.pdf | 1990-05-10 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 60 | On May 19, 1990 at 2033 hours with the plant in Mode 1 at 60% power, a manual reactor trip was initiated because of an anticipated turbine trip due to loss of condenser vacuum. Circulating Water Pump 3CWS-P1B was providing cooling water for Condenser Waterboxes "A" and "B". A rapid buildup of seaweed on "B" Traveling Screen resulted in an automatic trip of 3CWS-P1B. The plant was in the process of downpowering as a result of weather effects on condenser cooling water equipment in the intake structure. As the loss of cooling to two condenser bays would have resulted in a low condenser vacuum, a reactor trip was initiated. The reactor trip caused a Main Turbine and Generator trip in accordance both design. <br /><br /> Root cause of this event was design deficiency in that the Traveling Screen capacity was inadequate. A contributing cause was the peak seaweed season.<br /><br /> As corrective action, the Traveling Screen units in a number of bays will be redesigned and modified per the recommendations of an internal Task Force. Two of these units will be modified in the next year. Personnel have been instructed to evaluate intake structure conditions more frequently and procedures modified to allow power reductions at a faster rate.
423 | 4231990019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990019R01.pdf | 1990-06-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Millstone 3 | P | WE | PO | 100 | On June 6, 1990, at 0618 hours with the plant in Mode 1 at 100% power, 587 degrees Fahrenheit and 2250 psia, an automatic reactor trip from a negative flux rate signal occurred due to a dropped control rod. <br /><br /> The cause of this event was a broken connection in the stationary gripper coil power cable for rod G13. This single dropped rod resulted in a negative flux rate signal on two Power Range Detectors, thereby resulting in a reactor trip signal. The root cause of the broken connection was corrosion at the conductor/pin interface. <br /><br /> As immediate corrective action control room operators performed the actions required by the applicable emergency operating procedure. The broken connector was replaced. A functional test was performed by fully withdrawing and then inserting the affected rod. Long term corrective action will be to inspect and replace connectors as necessary during the third refueling outage.
423 | 4231990030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231990030R02.pdf | 1990-12-31 | K2 | Feedwater Line Break | [9 empty] | X | X | [26 empty] | X |  | X | [5 empty] | Millstone 3 | P | WE | PO | 86 | On December 31, 1990, at 1636 hours with the plant in Mode 1 at 86% power, 580 degrees Fahrenheit and 2250 psia, a manual reactor trip was initiated due to two 6-inch Moisture Separator Drain line (DSM) piping breaks in the Turbine Building. Following the trip a Main Steam Line Isolation was initiated to minimize the release of steam into the Turbine Building.<br /><br /> The root cause of the event was the failure to enter the affected lines into the computer analysis program that was utilized to determine piping susceptible to erosion/corrosion. The omission from the erosion/corrosion monitoring program resulted in the DSM piping not being inspected prior to the failure downstream of the two level control valves. The wall thickness at the rupture was approximately 0.020 inches. The cause of the severe wall loss was single phase erosion/corrosion. The combination of temperature, high fluid velocity and extremely low oxygen content are the causative factors. The wall loss was localized. <br /><br /> As immediate corrective action, control room operators performed the actions required by the applicable emergency operating procedures. The ruptured pipes were capped and the DSM pumps and piping were isolated to allow continued operation. <br /><br /> During the third refueling outage, which began on February 2, 1991, the piping upstream and downstream of the level control valves was replaced with piping having greater erosion/corrosion resistant properties.
423 | 4231991014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231991014R01.pdf | 1991-06-09 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | At 1125 hours on June 9, 1991, with the plant at 100% power in Mode 1, at 2250 psia and 587 degrees Fahrenheit, a reactor and subsequent turbine trip occurred. The trips were due to a phase to ground fault on a 345 kilovolt (KV) system transmission line (external to the plant) in combination with a faulty switchyard pilot wire relay. The pilot wire relay scheme protects the 345KV transmission zone from the main generator output transformer to the switchyard tie breakers (which connect the plant to the distribution system transmission lines). These faults caused station switchyard breakers to open and resulted in Unit 3 load rejection schemes operating to initiate the trips. <br /><br /> The root cause of the trip was a loose restraint tap on the switchyard pilot wire relay. The tap screw was broken and was not completely tightened on the lug of the tap wire. The loose tap resulted in an open circuit and caused the pilot wire relay to actuate incorrectly to the transmission line fault. The cause of the broken tap screw could not be determined. A Feedwater Isolation and Auxiliary Feedwater actuation occurred as expected following a trip. No other Engineered Safety Feature signals were initiated and the event posed no significant hazard to the health and safety of the public. The broken tap screw and affected wiring were repaired, and the pilot wire relay was returned to service.
423 | 4231992011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231992011R00.pdf | 1992-04-05 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Millstone 3 | P | WE | PO | 100 | On April 5, 1992, at 1715 hours with the plant at 100 percent power, the reactor was manually tripped due to the loss of the operating condensate pumps. Operations had just completed a backwash of the the E circulating water bay. During the backwash, the E Circulating Water (CW) Pump was stopped and a large amount of debris piled up in front of the E Traveling Screen. After the backwash, the E CW Pump was-restarted and the F CW Pump was stopped in preparation for backwashing the F Bay. Shortly after stopping, the F CW Pump, the E CW Pump tripped. As a result, cooling, to one of the three condenser bays was completely lost. This caused hotwell level to fluctuate, and resulted in reaching the low level trip) setpoint for the condensate pumps. <br /><br /> The root cause for this incident is design is deficiency. The E Traveling Water Screen was not capable of running in the reverse direction while performing a thermal backwash. Additionally, the E screen did not have sufficient capacity when operated in the forward direction to handle the influx of debris. Divers removed debris from in front of the travel water screens. The traveling screen units are being replaced with units which have 300% of the debris removal capacity.
423 | 4231992027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231992027R00.pdf | 1992-11-05 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 16 | At 1630 on November 5, 1992, with the plant in Mode 1 at 16% power, an electrical fault protection signal in the zone between the generator and the switchyard resulted in a generator trip, turbine trip and reactor trip. <br /><br /> The cause was a spurious signal from one of two protective relays. Improper operation of either relay could not be repeated. A management review of these possible causes and actions to resolve them was conducted before startup was authorized. A Feed Water Isolation actuation occurred due to low Reactor Coolant System temperature. No other Engineered Safety Feature (ESF) signals were initiated or required and the event posed no significant hazard to the health and safety of the public.
423 | 4231992029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231992029R00.pdf | 1992-11-20 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | At 0403 on November 20, 1992, with the plant in mode 1 at 100% power, a turbine load rejection transient resulted in a reactor trip followed by a turbine trip. <br /><br /> The turbine control valves closed coincidental with an ElectoHydraulic Control (EHC) trouble alarm and a low voltage alarm on the regulated 120 volt instrument busses. While all events are consistent with the fact that degraded voltage was being supplied to the EHC system, no specific component could be found that caused the degraded voltage. A management review of this condition and actions to minimize impact in the event of recurrence was conducted before startup was authorized. The Auxiliary Feedwater System started due to the low low level in one steam generator. A Feedwater Isolation occured due to low Reactor Coolant System average temperature after the reactor trip. No other Engineered Safety Feature (ESF) signals were initiated or required and the event posed no significant hazard to the health and safety of the public.
423 | 4231993004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231993004R01.pdf | 1993-03-31 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | At 0103 on March 31, 1993, with the plant in Mode 1 at 100% power, a turbine valve closure resulted in a reactor trip followed by a turbine trip. <br /><br /> Turbine valve closure was the result of a faulty power supply in the Electo-Hydraulic Control (EHC) system. With the exception of a steam generator code safety valve not completely reseating, the plant responded normally to the transient. <br /><br /> Extensive trouble shooting determined that a power supply in the EHC system was faulty and caused the turbine valves to close. The faulty power supply was replaced. As action to prevent recurrence, the power supplies in the EHC system will be replaced or refurbished on a 10 year period. <br /><br /> Subsequent investigation determined that the steam generator safety valve which did not completely reseat had an incorrect lower adjustment ring setting. Additional inspection revealed that 7 other safety valves also had incorrect settings. Three of these valves indicated that they lifted and reseated during the transient. The other four valves did not open. <br /><br /> The root cause of the improper settings was inadequate work control by the vendor. Crosby Valve and Gage Company, who performed maintenance on the safeties, conducted an investigation and determined that their personnel inadvertently used the wrong procedure to set the lower adjustment rings.
423 | 4231994011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231994011R00.pdf | 1994-09-08 | QL5 | Partial Closure of MSIVs | [45 empty] | Millstone 3 | P | WE | PO | 100 | On September 8, 1994, with the plant at 100% power, a manual reactor trip was initiated. The reactor was manually tripped in anticipation of an automatic trip, due to the 'C' Main Steam Isolation Valve (MSIV) failing closed during surveillance testing. The plant responded normally with the exception that two of the Main Steam safety valves appeared to open momentarily below the Technical Specification tolerance. Feedwater isolation occurred. The auxiliary feedwater pumps started on Low-Low Steam Generator level, and the turbine-driven Auxiliary Feedwater pump tripped off eight seconds after starting. <br /><br /> The manual trip of the reactor protection system is reported under 10CFR50.73(a)(2)(iv). The Main Steam safety valves lifting below their Technical Specification tolerance is reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.<br /><br /> The cause of the MSIV closure was equipment failure. A pin failed in a solenoid on the 'C' MSIV, which resulted in the MSIV failing closed during surveillance testing. The cause of the Main Steam safety valves lifting prematurely is believed to be due to setpoint drift. <br /><br /> As immediate corrective action the control room Operators manually tripped the reactor and performed the actions required by emergency operating procedures. As corrective action, the solenoid and a number of pins were replaced, and the MSIVs were tested satisfactorily. The turbine-driven Auxiliary Feedwater pump was returned to operable status, and two Main Steam safety valves were replaced.
423 | 4231998038 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231998038R00.pdf | 1998-09-15 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | On September 15, 1998, at 17:35, with the Unit in Mode 1 at 100 percent power, a manual reactor trip was initiated when condensate pump discharge conductivity exceeded the limits allowed by the Abnormal Operating Procedure. This event occurred after restoring the Steam Generator (SG) Blowdown System to closed cycle service following maintenance activities. A prompt notification of this reactor trip was made pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System (RPS)...".The root cause of the event was the failure of the implementing procedure to fully address all design conditions in that the procedure utilized to remove the SG blowdown system from service did not provide adequate guidance to prevent a vacuum from being drawn in the Blowdown Receiver Tank as the tank cooled to ambient conditions.The plant responded as expected during the reactor trip. There was minor safety significance associated with this event in that a transient was imposed on the unit due to the conservative chemistry criteria utilized in the Abnormal Operating Procedure. There were no consequences associated with this event. Operator actions were in accordance with operating procedures.Operations Procedure OP 3316C, "Steam Generator Blowdown" was revised to ensure the blowdown receiver tank does not reach vacuum conditions during removal from service. Operating procedures will be revised to incorporate new criteria for manual trip of reactor on high condensate discharge conductivity.
423 | 4231998043 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231998043R00.pdf | 1998-10-28 | QL6 | Condenser Leakage | [45 empty] | Millstone 3 | P | WE | PO | 100 | On October 28, 1998, at approximately 09:20 hours, with the Unit in Mode 1 at 100 percent power, a manual reactor trip was initiated when a leak in the "C" Condenser waterbox allowed saltwater intrusion resulting in Condensate Pump Discharge (CPD) conductivity exceeding the limits allowed by Abnormal Operating Procedure (AOP) 3558, "Condenser Tube Leak." On October 28, at 09:32 hours, a four-hour non-emergency notification of this reactor protection system (RPS) actuation was made pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as"...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System.."The cause of event was the mechanical failure of a Condenser tube within the "C" waterbox.Eddy current testing determined that a tube leak within the "C" Condenser waterbox caused an inflow of salt water from the Circulating Water System into the Condenser resulting in the high conductivity readings. The precise cause of the condenser tube failure has not been determined. The tube was plugged and the unit was returned to operation. The AOP required a manual reactor trip without consideration of the ability of the condensate demineralizers to remove impurities without impacting the steam generators nor allow time to identify and isolate the leak. There was no impact on system chemistry downstream of the condensate demineralizers as they were able to maintain chemistry within normal limits during this event. There was minor safety significance associated with this event in that a transient was imposed on the unit due to the conservative chemistry criteria utilized in the AOP. There were no consequences associated with this event.The leaking Condenser tube in the "C" waterbox was plugged. Operating procedures have been revised to have Chemistry recommend action (including plant shutdown when necessary) based upon chemistry conditions.
423 | 4231998044 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231998044R00.pdf | 1998-11-11 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Millstone 3 | P | WE | PO | 89 | On November 11, 1998, at approximately 0735 hours, with the unit at 89 percent power, a manual Reactor Trip was initiated when the differential pressure (D/P) between the "A" and "B" Circulating Water System (CWS) condensers measured greater than 2 inches water gauge (w.g.). This event occurred while the "A" waterbox was being backflushed due to high differential pressure across the waterbox. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS).The cause of the event is attributed to high levels of debris impinging on the traveling screens due to severe weather resulting in a high D/P across the traveling screens which caused the "B" circulating water pump to trip. Because the "A" circulating water pump was procedurally removed from service to facilitate back-flushing of the "A" waterbox, loss of the "B" pump resulted in a loss of cooling to the "A" condenser. This lack of cooling resulted in a procedurally driven reactor manual trip due to an increase in differential pressure between condensers. A Root Cause Analysis relative to this event is in progress. If the results of the analysis differ from the results presented herein a supplement to this LER will be submitted.Corrective actions include modifying procedures to address NNECO response to adverse weather conditions, repairing inoperable mechanical components i.e. screens and trash conveyor, and reinforcing expectations for severe weather preparation.
423 | 4231998045 | https://lersearch.inl.gov/PDFView.ashx?DOC::4231998045R00.pdf | 1998-12-11 | QL5 | Partial Closure of MSIVs | [45 empty] | Millstone 3 | P | WE | PO | 100 | On December 11, 1998, at approximately 0840 hours, with the Unit in Mode 1 at 100 percent power, Main Steam Isolation Valve (MSIV) 3MSS*CTV27A fully closed while performing partial stroke testing resulting in an automatic reactor trip initiated by low water level in the #1 Steam Generator(SG). The closure of the MSIV was caused by the failure of solenoid valve 3MSS*SV27A1A to fully open during the partial stroke test. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv) as "...any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS) ...".The closure of the MSIV was caused by the failure of solenoid valve 3MSS*SV27A1A to fully open during the partial stroke test. A circumferential through-wall crack in the solenoid valve main piston which reduced the ability to adequately vent the inside of the piston, combined with marginal actuator force, was the cause of the failure. Metallurgical examinations of the microstructure of the solenoid valve piston structure conclusively identified the cracking propagation as stress corrosion cracking.The safety function of main steam isolation provided by MSIV 3MSS*CTV27A was not compromised by the failure of solenoid valve 3MSS*SV27A1A. There were no safety consequences associated with this event. Inspection of the other solenoid valves indicated several had surface indications on their main pistons. Partial stroke testing performed indicated that these indications did not prevent these valves from functioning properly. Considering the common mode implications, the decision was made to replace the solenoid valves.The solenoid valve actuators' material was replaced with material less susceptible to stress corrosion cracking. The solenoid valve actuators were upgraded to provide additional margin on actuator force.
423 | 4232003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232003001R00.pdf | 2002-12-23 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | On December 23, 2002, at approximately 0200 with the plant at 100% power, a reactor trip occurred following a Generator fault. The appropriate alarms were received just prior to the trip. In addition, the trip signal opened a series of breakers and the Turbine and Reactor tripped sequentially. The Turbine Stop Valves closed within one second. The Steam Generator level shrinkage caused a low level in the Steam Generators starting the Auxiliary Feedwater System within 6 seconds, which was an expected occurrence. During and after the plant trip all main and auxiliary equipment functioned as designed and plant operators stabilized the plant in MODE 3.The generator stator fault on phase A was found to be due to an arc to ground associated with the T-4 high voltage bushing. Specifically, stator cooling water was leaking through a pin-hole at the joint area (braze material) of the tubular lead conductor and the cooling water inlet fitting. The leaking cooling water traveled along the bushing body underneath the insulation package where the leaking coolant picked up contaminants (making it more conductive). The leaking contaminated water ultimately traversed the entire bushing to the point of contacting the housing enclosure (ground). Per vendor evaluation, the leak was due to a void/porosity issue with the braze material itself. This was most likely a fabrication deficiency that deteriorated over time.The leak was repaired through re-brazing on the T-4 tubular lead connector and system integrity was confirmed through pressure testing. Other appropriate corrective actions are being addressed in accordance with the Millstone Corrective Action Program.
423 | 4232005002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232005002R00.pdf | 2005-04-17 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Millstone 3 | P | WE | PO | 100 | On April 17, 2005 at 0829, during normal 100% power operating conditions the solid state protection system (SSPS) generated an "A" Train SSPS Steam Line Pressure Low SI/MSI signal that tripped the reactor, closed the main steam isolation valves, and started one train of the emergency core cooling system (ECCS). Following the trip, all control rods inserted and the auxiliary feedwater system actuated automatically as expected, however the turbine driven auxiliary feedwater pump tripped on startup. One of the "B" steam generator safety valves lifted. Control room operators entered the emergency operating procedure network, manually initiated "B" safety injection (SI)actuation so as to have a two-train SI condition, and continued to place the plant in a stable condition. Based on plant indications during the event an NRC emergency classification of Alert was declared (Event No. 41607). Within one hour of event initiation, plant parameters were stabilized and ECCS systems were stopped and placed in a standby condition.The root cause of the event was that diode leads on a universal logic card in the SSPS were coated with a material susceptible to whisker growth that eventually shorted the card output and produced an inadvertent SI signal. Corrective actions included replacing the affected card and inspecting, cleaning and replacing additional cards in the SSPS. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A). In addition, this report satisfies the Technical Specification 3.5.2 special reporting requirement and satisfies the 10 CFR 21 evaluation, notification and reporting obligation.
423 | 4232005003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232005003R00.pdf | 2005-09-29 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | PO | 100 | On September 29, 2005, at approximately 1313 with the unit in Mode 1 at 100 percent power, Millstone Unit 3 reactor was manually tripped due to the loss of two circulating water [CW] pumps in the same condenser section. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System [RPS], actuation Reactor trip.At approximately 1313 on September 29, 2005, Millstone Unit 3 reactor was manually tripped due to the loss of two [CW] pumps in the same condenser section resulting from deteriorating conditions related to a storm consisting of high winds and waves. At approximately 1311, the 'A' CW pump automatically tripped due to high traveling screen differential pressure. At 1313, the 'B' CW pump also automatically tripped due to high traveling screen differential pressure. The operators then tripped the reactor in accordance with operating procedures.The event review team (ERT) concluded that environmental factors such as tide, wave height, wind speed and direction, and debris contributed to the event. Plant systems performed as designed and plant personnel operated the plant in a safe manner following the procedural guidance provided.
423 | 4232005005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232005005R01.pdf | 2005-12-01 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 38 | At approximately 14:45 on December 1, 2005, with Millstone Unit 3 (MP3) in Mode 1 at an indicated power level of 38%, an automatic reactor trip occurred on C Steam Generator Low-Low level (S/G Low-Low level). At the time of the reactor trip, downpower to 30% was in progress to facilitate a containment entry to locate and repair a Reactor Coolant System (RCS) leak. As turbine load and reactor power were reduced, main turbine vibrations increased above allowable limits and the main turbine was manually tripped in accordance with procedure. After the turbine was manually tripped, the reactor automatically tripped on 'C' S/G Low-Low level. All safety systems performed as designed, including auto actuation of the auxiliary feedwater system. The balance of the plant shutdown was uncomplicated.The direct cause of the reactor trip was a Low-Low level in the 'C' S/G that resulted from the shrink in S/G water level created by the manual turbine trip. The plant is designed to maintain the reactor critical following a turbine trip below 45% power. At the time of the trip, the Reactor Protection System S/G Low-Low Level Trip setpoints were being maintained at 27% vice the nominal value of 18% to address Westinghouse identified S/G level inaccuracies associated with the S/G mid-deck plate differential pressure. Operation at the increased set point reduced the margin available to accommodate S/G level transients that occur following a turbine trip at power. The automatic reactor trip and auxiliary feedwater system actuation are reportable in accordance with 10CFR50.73(a)(2)(iv).
423 | 4232008003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232008003R00.pdf | 2008-10-11 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Millstone 3 | P | WE | PO | 30 | On October 11, 2008, while in MODE 1 at approximately 30% power an automatic reactor trip occurred, as Millstone Power Station Unit 3 was reducing power in preparation for the 12th refueling outage. Prior to the reactor trip the plant was experiencing Steam Generator (S/G) level oscillations as the result of removing feedwater system components from service. The operators took manual control of the feedwater system, however, the oscillations increased and the 'A' S/G reached its 'high-high' set point resulting in an automatic turbine trip and feedwater isolation. A reactor trip on 'low-low' S/G level followed. All safety systems operated normally including the automatic start of the auxiliary feedwater pump, and the reactor shut down safely. All secondary systems operated normally.The cause was determined to be the operating crew on shift failed to effectively use the tools necessary to enable an event free shutdown of the plant. The organization with respect to monitoring and measuring crew performance was not effective in implementing programs designed to manage the challenges to the operators.Prior to start up from the refueling outage, training on low power feed station operations for on shift and active licensed operators was conducted. Additionally proper operation of the S/G water level control system and the feedwater regulating valves was verified. Additional corrective actions will be entered into the station's corrective action program.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 50.73(a)(2)(iv)(B).
423 | 4232009002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232009002R00.pdf | 2009-12-19 | QR5 | Turbine Trip | [45 empty] | Millstone 3 | P | WE | PO | 100 | On December 19, 2009 an automatic reactor trip occurred on Millstone Power Station Unit 3 while the unit was in Mode 1, at 100 % power, due to a turbine trip caused by a generator output electrical fault. All control rods fully inserted into the reactor. The auxiliary feedwater pump started as designed and maintained steam generator level. All other post trip actions were standard and all systems operated as expected. A post trip walk-down identified damage to 'C' phase main generator breaker and isophase ducting. There were no radiological challenges as a result of the event.The most probable cause of the ground fault, which resulted in the turbine trip, was determined to be a manufacturing defect in the main generator breaker, 15G-3U-2, 'C' pole contacts. The 'C' pole of the main generator breaker was repaired. All three poles of the breaker will be inspected during the next refueling outage (3R13) to verify the proper geometry of the contacts as well as the security of the fasteners holding the moving contact piston flange in place.This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 4232010002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232010002R00.pdf | 2010-05-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Millstone 3 | P | WE | PO | 17 | On May 17, 2010 an automatic reactor trip occurred on Millstone Power Station Unit 3 (MPS3) while the unit was in Mode 1, at 17 % power, due to a low steam generator (S/G) water level condition in 'C' S/G caused by the inability of the feedwater regulating bypass valve (FRBV) to properly control S/G levels in automatic or manual control. All control rods fully inserted into the reactor. The auxiliary feedwater system started as designed and maintained S/G level. Safety systems functioned as expected based upon the signals received. There were no radiological challenges as a result of the event.The cause of this event was determined to be the inability of the FRBV control system to control S/G levels at low power operations. The control loop was dynamically tuned and the level controller adjusted to improve system control and performance. A design change is being evaluated to improve the performance of the SG level control system during low power operations.This event is being reported in.accordance.with10 CPR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 4232011003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232011003R00.pdf | 2011-11-20 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 3 | P | WE | SU | 2 | On November 20, 2011 at 1758 hours, during power ascension with Millstone Power Station Unit 3 (MPS3) in Mode 2, at 1.7 % reactor power, the operators manually tripped the reactor as required by procedure upon the loss of main condenser vacuum due to the loss of the auxiliary boilers supplying gland sealing steam. All control rods fully inserted into the reactor and all emergency systems functioned as designed. There were no radiological challenges as a result of the event. There were no detrimental effects to station equipment. No limiting safety system settings were exceeded. The operators responded properly to the loss of condenser vacuum and followed the correct procedure flow path. There were no deviations from the procedure guidance in effect.The auxiliary boilers were restarted, auxiliary steam, gland sealing steam, along with main condenser vacuum were re-established, the unit start-up recommenced and the unit placed in service. Additional corrective actions are being taken in accordance with the station's corrective action program.This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 4232013007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232013007R00.pdf | 2013-08-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Millstone 3 | P | WE | PO | 100 | On August 09, 2013 at 2119, while in MODE 1 at 100 percent power, Millstone Power Station Unit 3 experienced an automatic reactor trip on steam generator (SG) low-low water level. The low-low SG water level condition resulted from all main feed water pump recirculation valves failing full open following a loss of power from non safety-related 480 volt load center 32L. This bus powered the instrumentation loops for all three main feedwater pump recirculation valve controllers. Upon the loss of power, the valves went to their failure state of "Recirculation", resulting in a loss of feedwater header pressure and flow to the steam generators causing the unit to automatically trip on low-low steam generator level. The auxiliary feedwater system started as designed and maintained steam generator levels. Safety systems functioned as expected. There were no radiological challenges as a result of the event.<br /><br /> The direct cause of the event was the loss of power to the 480V bus that powered the three main feedwater pump recirculation valve controllers. Troubleshooting efforts did not reveal the cause of the ground that led to the loss of bus 32L. Power to the three main feedwater recirculation valves has been temporarily moved to another power supply.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 3362014006 | https://lersearch.inl.gov/PDFView.ashx?DOC::3362014006R00.pdf | 2014-05-25 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Millstone 3 | P | WE | PO | 100 | On May 25, 2014, with Millstone Power Station (MPS) Unit 2 and 3 (MPS2 and MPS3) in operating MODE 1, operating at 100% reactor power, a total loss of offsite power occurred in the MPS switchyard. Both MPS2 and MPS3 experienced a turbine trip on power to load imbalance followed by an automatic reactor trip. Both units' safety related emergency diesel generators (EDGs) automatically started and supplied power to their respective safety busses. As designed, the motor driven auxiliary feedwater (AFW) pumps automatically started on MPS2 and all AFW pumps automatically started on MPS3.<br /><br /> MPS declared an Unusual Event (UE) following the reactor trips and the NRC was notified (EN50142 for MPS2 and EN 50141 for MPS3). Following stabilization of both MPS2 and MPS3, the UE was terminated.<br /><br /> With both MPS2 and MPS3 at full power and one of the Transmission Owner (TO) 345 kV lines out of service for scheduled work, a phase to ground fault occurred on one of the phases on a motor operated disconnect (MOD) on one of the three remaining TO 345 kV lines. The fault was caused by an insulator failure of a MOD switch at a TO substation (offsite). This fault was also sensed as an instantaneous ground in one of the two remaining TO 345 kV lines resulting in this line also tripping. With three of the four TO 345 kV lines out of service, the MPS total electrical output overloaded the single remaining TO 345 kV Line which then also tripped resulting in a total loss of offsite AC power to MPS.<br /><br /> The TO replaced the faulty components and is investigating additional corrective actions. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B)(1), (6), and (8). Actuations of the reactor protection system, the AFW system, and the EDGs are reportable under this paragraph.
423 | 4232016001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232016001R00.pdf | 2016-01-25 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Millstone 3 | P | WE | PO | 100 | On January 25, 2016 at 0147 hours an automatic reactor trip occurred at Millstone Power Station Unit 3 while the unit was in Mode 1, operating at 100 percent power due to a trip of the 'B' Reactor Coolant Pump. The 'B' Reactor Coolant Pump tripped on a ground fault, which in turn caused the Unit 3 reactor to trip on reactor coolant system low loop flow (Reactor Protection System actuation). All control rods fully inserted into the reactor. The auxiliary feedwater pumps started as designed on low steam generator level and operators maintained steam generator level. All other post trip actions were standard and all safety systems operated as expected. <br /><br /> The 'B' Reactor Coolant Pump trip was caused by failure of one of three motor capacitors on the Reactor Coolant Pump motor. The failed capacitor on the affected Reactor Coolant Pump motor was replaced and the integrity of the motor windings, cabling, breaker, and associated protective relays were verified. Based on an assessment of the event, the risk impact was determined to be very small. There were no radiological challenges and the health and safety of the public were not affected. <br /><br /> The actuation of the reactor protection system and the automatic start of the auxiliary feedwater pumps is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 4232016004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232016004R00.pdf | 2016-05-15 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 3 | P | WE | PO | 74 | On May 15, 2016, with Millstone Power Station Unit 3 (MPS3) operating in MODE 1 at 74% power, the operators observed decreasing hydrogen pressure in the main turbine generator. Upon field investigation it was determined there was an active hydrogen leak from the main generator. The operators manually tripped the reactor and vented the hydrogen from the main generator. The reactor trip was uncomplicated. The auxiliary feedwater (AFW) pumps started as designed on low steam generator level and operators maintained steam generator level. <br /><br /> The active hydrogen leak was the direct cause of the manual reactor trip. The hydrogen leak was caused by a dislodged plug on a port on the main generator. MPS maintenance procedures did not contain adequate procedural guidance in that there was no specific direction for installation, i.e., torque value and verifications. The procedures will be revised to include specific direction to tighten the plugs and applicable verifications (i.e., torque value, peer checking). Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> The actuation of the RPS and the automatic start of the AFW pumps is being reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
423 | 4232016005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4232016005R00.pdf | 2016-06-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Millstone 3 | P | WE | PO | 20 | On June 12, 2016, with Millstone Power Station Unit 3 operating in MODE 1 at 100% power, operators identified the third stage of the "A" Reactor Coolant Pump (RCP) seal had failed, which resulted in an unidentified Reactor Coolant System leak greater than the Technical Specification (TS) limit of 1 gallon per minute. Operators initiated a plant shutdown as required by TS 3.4.6.2 ACTION Statement b. During the downpower, steam generator levels were not adequately maintained and the Engineered Safety Features Actuation System generated a Turbine Trip and Feed Water Isolation on Steam Generator Water Level - High-High being exceeded on the 'B' steam generator. In response, operators manually tripped the reactor at 23:37 (MODE 1, at approximately 20 % power). The auxiliary feedwater system started as designed. Safety systems functioned as expected. There were no radiological challenges as a result of the event. The plant entered COLD SHUTDOWN on June 14, 2016 at 01:29. <br /><br /> The cause of the unidentified leak was a failed third stage on the "A" RCP seal. The seal was replaced. The cause of the feedwater transient and resultant manual reactor trip was due to operator performance in controlling steam generator level. This is being addressed in the Corrective Action Program.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Additionally, the plant shutdown is being reported in accordance with 10 CFR 50. 73 (a)(2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
424 | 4241987008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987008R00.pdf | 1987-03-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Vogtle 1 | P | WE | SU | 3 | POWER LEVEL - 003%. AT 1036 CST ON MARCH 19, 1987 WITH VEGP UNIT 1 AT APPROXIMATELY 2.5% RATED THERMAL POWER, THE REACTOR TRIPPED ON A HIGH POSITIVE FLUX RATE SIGNAL AT STARTUP. THE PLANT WAS PERFORMING LOW POWER PHYSICS TEST 1-600-04, INCORE FLUX MAPPING AT THE ZERO POWER ROD INSERTION LIMIT. A NUCLEAR INSTRUMENTATION (NI) SYSTEM POWER RANGE CHANNEL (1N42) WAS IN THE TRIP CONDITION, PER PROCEDURE, TO ASSIST IN THE FLUX MAPPING. ANOTHER CHANNEL (1N44) RECEIVED A HIGH POSITIVE NEUTRON FLUX RATE SIGNAL CONCURRENT WITH A ONE STEP CONTROL BANK WITHDRAWAL. THE REACTOR TRIPPED ON A 2 OUT-OF 4 COINCIDENCE FOR HIGH POSITIVE NEUTRON FLUX RATE. RODS FULLY INSERTED INTO THE CORE AND PLANT SYSTEMS FUNCTIONED AS REQUIRED. THE CAUSE OF THE TRIP WAS AN IMPROPERLY ADJUSTED SETPOINT FOR NEUTRON FLUX RATE BISTABLE (NM311) ON NI CHANNEL 1N44 AND A HIGHER THAN NECESSARY SETTING FOR THE POWER RANGE SUMMING AND LEVEL AMPLIFIER. CORRECTIVE ACTIONS WERE TO RECALIBRATE THE NEUTRON FLUX RATE BISTABLE AND RECALIBRATE THE GAIN FOR THE SUMMING AND LEVEL AMPLIFIER FOR THE POWER RANGE CHANNEL FOLLOWING LOW POWER PHYSICS TESTING.
424 | 4241987009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987009R00.pdf | 1987-03-20 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vogtle 1 | P | WE | SU | 3 | POWER LEVEL - 003%. DURING THE PERIOD FROM MARCH 20, 1987 TO MARCH 26, 1987, UNIT 1 EXPERIENCED FIVE SHORT DURATION EVENTS RELATED TO STEAM GENERATOR (SG) WATER LEVELS EXCEEDING THE HI-HI WATER LEVEL TRIP SETPOINT. DURING THIS TIME THE PLANT WAS UNDERGOING INITIAL STARTUP TESTING OF THE CONDENSATE AND MAIN FEEDWATER, MAIN STEAM, AND TURBINE BYPASS (STEAM DUMP) SYSTEMS IN PREPARATION FOR STARTUP OF THE TURBINE/GENERATOR. TUNING OF THE AUTOMATIC CONTROL SYSTEMS FOR THE FEEDWATER REGULATING VALVES, STEAM DUMP VALVES, AND SG LEVEL WAS ONGOING. WATER LEVEL OSCILLATIONS IN THE SGS, INITIATED BY ADJUSTMENTS TO THE CONTROL SYSTEMS, RESULTED IN THE ACTUATION OF AUXILIARY FEEDWATER (AN ESF SYSTEM) AND, IN TWO EVENTS, WATER LEVEL WAS NOT RECOVERED IN TIME TO PREVENT ACTUATION OF THE REACTOR TRIP PROTECTIVE FUNCTION. THESE EVENTS, WHICH ARE NOT ATYPICAL OF PRESSURIZED WATER REACTORS DURING INITIAL POWER ASCENSION, WERE CAUSED BY THE INABILITY TO AUTOMATICALLY CONTROL STEAM GENERATOR WATER LEVELS, DURING INITIAL ADJUSTMENT OF THE AUTOMATIC CONTROL SYSTEMS FOR THE STEAM DUMP VALVES AND BYPASS FEEDWATER REGULATING VALVES. CORRECTIVE ACTIONS WERE TAKEN TO PROPERLY ADJUST THE CONTROL SYSTEMS.
424 | 4241987010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987010R00.pdf | 1987-03-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vogtle 1 | P | WE | SU | 3 | POWER LEVEL - 003%. DURING THE PERIOD FROM MARCH 21, 1987 TO MARCH 24, 1987, UNIT 1 EXPERIENCED TWO SHORT DURATION EVENTS RELATED TO STEAM GENERATOR (SG) WATER LEVEL EXCEEDING THE LOW-LOW LEVEL TRIP SETPOINT. DURING THIS TIME THE PLANT WAS UNDERGOING INITIAL STARTUP TESTING OF THE CONDENSATE AND MAIN FEEDWATER, MAIN STEAM, AND TURBINE BYPASS (STEAM DUMP) SYSTEMS IN PREPARATION FOR STARTUP OF THE TURBINE/GENERATOR. TUNING OF THE AUTOMATIC CONTROL SYSTEMS FOR THE FEEDWATER REGULATING VALVES, STEAM DUMP VALVES, AND SG LEVEL WAS ONGOING. WATER LEVEL OSCILLATIONS IN THE SGS, INITIATED BY ADJUSTMENTS TO THE CONTROL SYSTEMS, RESULTED IN THE ACTUATION OF THE REACTOR PROTECTION SYSTEM (RPS) REACTOR TRIP PROTECTIVE FUNCTION, AND ALSO INCLUDED ACTUATION OF ENGINEERED SAFETY FEATURE (ESF) SYSTEMS. THESE EVENTS, WHICH ARE NOT ATYPICAL OF PRESSURIZED WATER REACTORS DURING INITIAL POWER ASCENSION, WERE CAUSED BY THE INABILITY TO AUTOMATICALLY CONTROL STEAM GENERATOR WATER LEVELS, DURING INITIAL ADJUSTMENT OF THE AUTOMATIC CONTROL SYSTEMS FOR THE STEAM DUMP VALVES AND BYPASS FEEDWATER REGULATING VALVES. CORRECTIVE ACTIONS WERE TAKEN TO PROPERLY ADJUST THE CONTROL SYSTEMS.
424 | 4241987009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987009R00.pdf | 1987-03-23 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vogtle 1 | P | WE | SU | 3 | POWER LEVEL - 003%. DURING THE PERIOD FROM MARCH 20, 1987 TO MARCH 26, 1987, UNIT 1 EXPERIENCED FIVE SHORT DURATION EVENTS RELATED TO STEAM GENERATOR (SG) WATER LEVELS EXCEEDING THE HI-HI WATER LEVEL TRIP SETPOINT. DURING THIS TIME THE PLANT WAS UNDERGOING INITIAL STARTUP TESTING OF THE CONDENSATE AND MAIN FEEDWATER, MAIN STEAM, AND TURBINE BYPASS (STEAM DUMP) SYSTEMS IN PREPARATION FOR STARTUP OF THE TURBINE/GENERATOR. TUNING OF THE AUTOMATIC CONTROL SYSTEMS FOR THE FEEDWATER REGULATING VALVES, STEAM DUMP VALVES, AND SG LEVEL WAS ONGOING. WATER LEVEL OSCILLATIONS IN THE SGS, INITIATED BY ADJUSTMENTS TO THE CONTROL SYSTEMS, RESULTED IN THE ACTUATION OF AUXILIARY FEEDWATER (AN ESF SYSTEM) AND, IN TWO EVENTS, WATER LEVEL WAS NOT RECOVERED IN TIME TO PREVENT ACTUATION OF THE REACTOR TRIP PROTECTIVE FUNCTION. THESE EVENTS, WHICH ARE NOT ATYPICAL OF PRESSURIZED WATER REACTORS DURING INITIAL POWER ASCENSION, WERE CAUSED BY THE INABILITY TO AUTOMATICALLY CONTROL STEAM GENERATOR WATER LEVELS, DURING INITIAL ADJUSTMENT OF THE AUTOMATIC CONTROL SYSTEMS FOR THE STEAM DUMP VALVES AND BYPASS FEEDWATER REGULATING VALVES. CORRECTIVE ACTIONS WERE TAKEN TO PROPERLY ADJUST THE CONTROL SYSTEMS.
424 | 4241987010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987010R00.pdf | 1987-03-24 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vogtle 1 | P | WE | SU | 3 | POWER LEVEL - 003%. DURING THE PERIOD FROM MARCH 21, 1987 TO MARCH 24, 1987, UNIT 1 EXPERIENCED TWO SHORT DURATION EVENTS RELATED TO STEAM GENERATOR (SG) WATER LEVEL EXCEEDING THE LOW-LOW LEVEL TRIP SETPOINT. DURING THIS TIME THE PLANT WAS UNDERGOING INITIAL STARTUP TESTING OF THE CONDENSATE AND MAIN FEEDWATER, MAIN STEAM, AND TURBINE BYPASS (STEAM DUMP) SYSTEMS IN PREPARATION FOR STARTUP OF THE TURBINE/GENERATOR. TUNING OF THE AUTOMATIC CONTROL SYSTEMS FOR THE FEEDWATER REGULATING VALVES, STEAM DUMP VALVES, AND SG LEVEL WAS ONGOING. WATER LEVEL OSCILLATIONS IN THE SGS, INITIATED BY ADJUSTMENTS TO THE CONTROL SYSTEMS, RESULTED IN THE ACTUATION OF THE REACTOR PROTECTION SYSTEM (RPS) REACTOR TRIP PROTECTIVE FUNCTION, AND ALSO INCLUDED ACTUATION OF ENGINEERED SAFETY FEATURE (ESF) SYSTEMS. THESE EVENTS, WHICH ARE NOT ATYPICAL OF PRESSURIZED WATER REACTORS DURING INITIAL POWER ASCENSION, WERE CAUSED BY THE INABILITY TO AUTOMATICALLY CONTROL STEAM GENERATOR WATER LEVELS, DURING INITIAL ADJUSTMENT OF THE AUTOMATIC CONTROL SYSTEMS FOR THE STEAM DUMP VALVES AND BYPASS FEEDWATER REGULATING VALVES. CORRECTIVE ACTIONS WERE TAKEN TO PROPERLY ADJUST THE CONTROL SYSTEMS.
424 | 4241987011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987011R00.pdf | 1987-03-26 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Vogtle 1 | P | WE | PO | 11 | POWER LEVEL - 011%. ON MARCH 26, 1987 AT 2259 CST, MAIN FEEDWATER (MFW) OR STEAM GENERATOR FEED PUMP 'B' TRIPPED ON LOW SUCTION PRESSURE DUE TO DECREASING WATER LEVEL IN THE CONDENSER HOTWELL. THE TRIP OF THIS PUMP IN CONJUNCTION WITH MFW PUMP 'A' NOT BEING IN OPERATION COMPLETED THE 2 OUT-OF 2 LOGIC FOR ACTUATION OF THE AUXILIARY FEEDWATER (AFW) SYSTEM. CONTROL ROOM OPERATORS ATTEMPTED TO MAINTAIN THE STEAM GENERATOR LEVELS BUT AT 2301 CST, THE LEVEL IN SG #2 REACHED THE LOW-LOW LEVEL SETPOINT, INITIATING A REACTOR TRIP. THE OPERATORS RECOVERED SG LEVELS AND RESTORED THE PLANT TO NORMAL CONDITIONS. THE IMMEDIATE CAUSE OF THE EVENT WAS LOW CONDENSATE PRESSURE DUE TO LOW WATER LEVEL IN THE CONDENSER HOTWELL. THE ROOT CAUSE OF THE EVENT WAS THE FAILURE OF LEVEL TRANSMITTER LT-4415. THE EVENT'S INTERMEDIATE CAUSE WAS INADEQUATE INDICATION OF THE CONDENSER HOTWELL WATER LEVEL DUE TO LEVEL INDICATORS (1LG-4403, 1LG-4404, AND 1LG-4405) NOT HAVING LEVEL MARKINGS ON THEIR SIGHT GLASSES THAT CORRESPONDED TO THE NORMAL (OR ZERO) LEVEL INDICATED IN THE CONTROL ROOM BY THE CONDENSER HOTWELL LEVEL TRANSMITTER (1LG-4415). CORRECTIVE ACTIONS INCLUDED REPAIRING HOTWELL LEVEL TRANSMITTER 1LG-4415 AND PLACING TEMPORARY MARKINGS ON THE SIGHT GLASSES TO INDICATE HIGH, NORMAL (OR ZERO), AND LOW LEVELS THAT CORRESPOND TO THOSE DISPLAYED IN NORMAL (OR ZERO) THE CONTROL ROOM BY LT-4415.
424 | 4241987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987012R00.pdf | 1987-04-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 23 | POWER LEVEL - 023%. ON APRIL 5, 1987 AT 1355 CDT, WHILE IN MODE 1 AT 22.7% REACTOR POWER, A REACTOR TRIP OCCURRED WHEN THE WATER LEVEL IN STEAM GENERATOR 4 REACHED THE LOW-LOW LEVEL TRIP SETPOINT. THE ROOT CAUSE OF THE TRIP WAS THE OVERFEEDING OF STEAM GENERATOR 2 WHILE IN MANUAL CONTROL. STEAM GENERATOR 2 MAIN FEEDWATER REGULATING VALVE (MFRV) WAS IN THE MANUAL MODE OF OPERATION DUE TO OSCILLATIONS EXPERIENCED IN THE 'AUTO' MODE FOLLOWING A MAIN GENERATOR/TURBINE TRIP WHICH HAD OCCURRED AT 1321 CDT. ATTEMPTS TO CONTROL WITH THE NO. 2 MFRV IN 'MANUAL' WERE EVENTUALLY INEFFECTIVE AND A FEEDWATER ISOLATION (FWI) OCCURRED AT 1353 CDT WHEN STEAM GENERATOR 2 LEVEL REACHED THE HI-HI LEVEL SETPOINT. SUBSEQUENT INVESTIGATIONS HAVE REVEALED THAT, IN ADDITION TO THE LOW POWER LEVELS, A CONTRIBUTING FACTOR TO THE DIFFICULTY EXPERIENCED IN CONTROLLING MANUALLY WITH THE NO. 2 MFRV WAS A JUMPER WHICH WAS INCONSISTENTLY INSTALLED ON A CONTROL CARD FOR THIS VALVE. THE FWI RESULTED IN A RAPID DECREASE IN STEAM GENERATOR WATER LEVELS WHICH INITIATED THE REACTOR TRIP. A FAILURE OF THE MAIN FEEDWATER PUMP 'B' TO AUTOMATICALLY TRIP ON THE FWI ALSO OCCURRED. OPERATORS MANUALLY TRIPPED THE MAIN FEEDWATER PUMP AND ESTABLISHED STABLE PLANT CONDITIONS FOLLOWING THE REACTOR TRIP. CORRECTIVE ACTIONS HAVE BEEN TAKEN TO PERFORM FURTHER GAIN ADJUSTMENTS OF THE AIR BOOSTER FOR THE NO. 2 MFRV AND TO CORRECT THE POSITIONING OF THE JUMPER.
424 | 4241987013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987013R00.pdf | 1987-04-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 34 | POWER LEVEL - 034%. ON APRIL 10, 1987 AT 1256 CDT WITH THE REACTOR OPERATING AT APPROXIMATELY 34% REACTOR POWER, A REACTOR TRIP OCCURRED WHEN STEAM GENERATOR (SG) NO. 3 WATER LEVEL REACHED THE LOW-LOW LEVEL TRIP SETPOINT. THE REACTOR TRIP WAS CAUSED BY THE MALFUNCTIONING OF THE MAIN FEEDWATER (MFW) PUMP 'A' DISCHARGE VALVES. THESE FAILURES PROVIDED A RECIRCULATION FLOW PATH OUT OF MFW PUMP 'B' BACK TO THE SUCTION OF MFW PUMP 'B'. THIS CAUSED THE LEVELS FOR ALL THE STEAM GENERATORS TO DECREASE. MANUAL LEVEL CONTROL OF STEAM GENERATORS NOS. 1, 3 AND 4 WAS ACHIEVED; HOWEVER, THE MAIN FEEDWATER REGULATING VALVE (MFRV) FOR STEAM GENERATOR NO. 2 DID NOT RESPOND TO ITS CONTROLLER AS DID THE OTHER MFRVS TO THEIR CONTROLLERS, RESULTING IN A FEEDWATER ISOLATION (FWI) AND SUBSEQUENTLY, A REACTOR TRIP. THE INCIDENT INVESTIGATION REVEALED THAT THE CONTROL CARD FOR MFRV NO. 2 CONTRIBUTED TO THE DIFFICULTY OF MANUALLY CONTROLLING THIS VALVE. THE CORRECTIVE ACTIONS TAKEN WERE TO ADJUST THE PACKING FOR THE MFW PUMP 'A' DISCHARGE MOV, TO REPLACE THE HINGE PIN FOR THE DISC IN MFW PUMP 'A' DISCHARGE CHECK VALVE, AND TO CORRECT THE CONTROL CARD FOR MFRV NO. 2.
424 | 4241987014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987014R00.pdf | 1987-04-11 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 21 | POWER LEVEL - 021%. ON APRIL 11, 1987 AT 0320 CDT WHILE IN MODE 1 AT 21% REACTOR POWER, A REACTOR TRIP OCCURRED WHEN STEAM GENERATOR NO. 1 REACHED THE LOW-LOW WATER LEVEL TRIP SETPOINT. THE PLANT OPERATORS WERE IN THE PROCESS OF TRANSFERRING FEEDWATER FLOW FROM THE BYPASS FEEDWATER REGULATING VALVES (BFRV) TO THE MAIN FEEDWATER REGULATING VALVES (MFRVS). DURING THE FEEDWATER TRANSFER, THE NO. 2 MFRV DID NOT RESPOND AS PROMPTLY TO ITS CONTROLLER AS DID THE OTHER MFRVS TO THEIR CONTROLLERS. INVESTIGATION OF THIS INCIDENT REVEALED THAT A JUMPER CONFIGURATION ON A CONTROL CARD FOR THE NO. 2 MFRV WAS IN A DIFFERENT CONFIGURATION THAN FOR THE OTHER MFRVS. THIS CONFIGURATION CAUSED THE MFRV TO RESPOND IN A LOGARITHMIC MANNER, WHICH WAS DIFFERENT THAN THE LINEAR RESPONSE EXHIBITED BY THE OTHER MFRV'S. MANUAL CONTROL OF THE NO. 2 MFRV WAS INEFFECTIVE, WHICH RESULTED IN STEAM GENERATOR NO. 2 REACHING THE HI-HI LEVEL SETPOINT. A FEEDWATER ISOLATION (FWI) OCCURRED AT 0318 CDT. THE FWI AUTOMATICALLY INITIATED THE MOTOR DRIVEN AUXILLIARY FEEDWATER PUMPS; PLANT OPERATORS MANUALLY STARTED THE TURBINE DRIVEN AUXILLIARY FEEDWATER PUMP. A RAPID DECREASE IN STEAM GENERATOR WATER LEVELS OCCURRED BECAUSE OF THE FWI. THIS RESULTED IN STEAM GENERATOR NO. 1 REACHING ITS LOW-LOW SETPOINT WHICH RESULTED IN THE REACTOR TRIP.
424 | 4241987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987018R00.pdf | 1987-04-29 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 74 | POWER LEVEL - 074%. ON APRIL 29, 1987, AT 1406 CDT, UNIT 1 WAS IN MODE 1 AT 74% OF RATED THERMAL POWER (RTP). PLANT PERSONNEL WERE PERFORMING CALIBRATIONS ON CHANNEL 4 OF THE REACTOR PROTECTION SYSTEM (RPS), WHEN A REACTOR TRIP WAS INITIATED BY THE OVER-POWER AND OVER-TEMPERATURE DELTA TEMPERATURE BISTABLE ON CHANNEL 2. WITH ONE CHANNEL BEING TESTED, THE 2 OUT OF 4 COINCIDENT LOGIC WAS SATISFIED, WHICH CAUSED THE TRIP TO OCCUR. ON MAY 4, 1987, AT 1216 CDT, UNIT 1 WAS IN MODE 1 AT 75% OF RTP. PLANT PERSONNEL WERE SURVEILLANCE TESTING CHANNEL 3 OF THE RPS, WHEN A REACTOR TRIP WAS AGAIN INITIATED BY THE OVER-POWER AND OVER-TEMPERATURE DELTA- TEMPERATURE BISTABLES ON CHANNEL 2. FOLLOWING BOTH EVENTS, THE PLANT WAS RETURNED TO NORMAL CONDITIONS (MODE 3). THESE EVENTS WERE CAUSED BY A FAULTY CIRCUIT BOARD SENDING ERRATIC VOLTAGE SIGNALS TO THE BISTABLES OF THE CHANNEL 2 INSTRUMENTS. THE CIRCUIT BOARD WAS REPLACED. BENCH TESTING WILL BE PERFORMED TO DETERMINE THE FAILURE MODE.
424 | 4241987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987018R00.pdf | 1987-05-04 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 74 | POWER LEVEL - 074%. ON APRIL 29, 1987, AT 1406 CDT, UNIT 1 WAS IN MODE 1 AT 74% OF RATED THERMAL POWER (RTP). PLANT PERSONNEL WERE PERFORMING CALIBRATIONS ON CHANNEL 4 OF THE REACTOR PROTECTION SYSTEM (RPS), WHEN A REACTOR TRIP WAS INITIATED BY THE OVER-POWER AND OVER-TEMPERATURE DELTA TEMPERATURE BISTABLE ON CHANNEL 2. WITH ONE CHANNEL BEING TESTED, THE 2 OUT OF 4 COINCIDENT LOGIC WAS SATISFIED, WHICH CAUSED THE TRIP TO OCCUR. ON MAY 4, 1987, AT 1216 CDT, UNIT 1 WAS IN MODE 1 AT 75% OF RTP. PLANT PERSONNEL WERE SURVEILLANCE TESTING CHANNEL 3 OF THE RPS, WHEN A REACTOR TRIP WAS AGAIN INITIATED BY THE OVER-POWER AND OVER-TEMPERATURE DELTA- TEMPERATURE BISTABLES ON CHANNEL 2. FOLLOWING BOTH EVENTS, THE PLANT WAS RETURNED TO NORMAL CONDITIONS (MODE 3). THESE EVENTS WERE CAUSED BY A FAULTY CIRCUIT BOARD SENDING ERRATIC VOLTAGE SIGNALS TO THE BISTABLES OF THE CHANNEL 2 INSTRUMENTS. THE CIRCUIT BOARD WAS REPLACED. BENCH TESTING WILL BE PERFORMED TO DETERMINE THE FAILURE MODE.
424 | 4241987025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987025R01.pdf | 1987-05-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vogtle 1 | P | WE | PO | 80 | POWER LEVEL - 080%. ON MAY 9, 1987 AT 0332 CDT WHILE IN MODE 1 AT 80% REACTOR POWER, AN AUTOMATIC REACTOR TRIP OCCURRED WHEN STEAM GENERATOR (SG) #4 WATER LEVEL REACHED THE LOW-LOW LEVEL TRIP SETPOINT. THE PLANT WAS CONDUCTING STARTUP TEST PROCEDURE 1-6SC-02 'LOAD SWING TEST' AND WAS PERFORMING THE 10% STEP LOAD INCREASE PART OF THE TEST WHEN THE TRIP OCCURRED. A MAIN TURBINE LOAD LIMITER POTENTIOMETER WAS INCORRECTLY SET AND ALLOWED TURBINE LOADING TO OVERSHOOT TO 82% REACTOR POWER DURING THE LOAD INCREASE. WITH A SINGLE MAIN FEEDWATER (MFW) PUMP OPERATING IN AUTOMATIC, THE OPERATOR COULD NOT MAINTAIN STEAM GENERATOR WATER LEVEL IN THE OPERATING BAND. THIS RESULTED IN A REACTOR TRIP ON STEAM GENERATOR LOW-LOW WATER LEVEL. THE TRIP WAS CAUSED BY PROCEDURAL INADEQUACY. THE TEST PROCEDURE DID NOT CONTAIN THE NECESSARY INSTRUCTIONS TO CORRECTLY ADJUST THE TURBINE LOAD LIMITER POTENTIOMETER AND DID NOT CONTAIN INSTRUCTIONS TO THE OPERATORS CONCERNING CORRECTIVE ACTIONS FOR AN OVERSHOOT CONDITION. CORRECTIVE ACTIONS WERE TAKEN TO CLARIFY THE TEST PROCEDURE TO ENSURE THAT THE MAIN TURBINE LOAD LIMITER IS CORRECTLY ADJUSTED AND APPROPRIATE OPERATOR ACTIONS ARE TAKEN.
424 | 4241987027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987027R00.pdf | 1987-05-13 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 1 | P | WE | PO | 90 | POWER LEVEL - 090%. ON MAY 13, 1987 AT 0304 CDT WHILE IN MODE 1 AT 90% RATED THERMAL POWER, A REACTOR TRIP OCCURRED WHEN STEAM GENERATOR (SG) #1 REACHED ITS LOW-LOW WATER LEVEL SETPOINT. THE REACTOR TRIP WAS CAUSED BY THE INADVERTENT CLOSURE OF THE CORRESPONDING OUTBOARD MAIN STEAM ISOLATION VALVE (MSIV) DURING MAINTENANCE. (VOGTLE HAS TWO MSIVS IN SERIES ON EACH MAIN STEAM SUPPLY LINE.) THE CLOSURE OF THE MSIV CAUSED A RAPID PRESSURE INCREASE IN SG #1 WHICH PRODUCED AN IMMEDIATE DECREASE IN THE LEVEL OF SG #1 TO THE LOW- LOW WATER LEVEL SETPOINT, INITIATING A REACTOR TRIP. THE CORRESPONDING ATMOSPHERIC RELIEF VALVE OPENED TO CONTROL PRESSURE IN SG #1. OPERATORS CLOSED THE REMAINING TRAIN 'B' MSIVS TO SLOW THE COOLDOWN RATE OF THE REACTOR COOLANT SYSTEM AND RESTORED THE PLANT TO STABLE CONDITIONS BY 0322 CDT. THE TRIP WAS CAUSED BY INADEQUATE WORK INSTRUCTIONS FOR PERFORMING MAINTENANCE ON THE MSIVS. CORRECTIVE ACTION WAS TAKEN TO ESTABLISH WRITTEN GUIDELINES DESCRIBING PROPER METHODS TO MAINTAIN VALVE POSITION WHILE PERFORMING MAINTENANCE.
424 | 4241987029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987029R00.pdf | 1987-05-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 7 | POWER LEVEL - 007%. ON MAY 24, 1987, AT 0025 CDT WITH UNIT 1 IN MODE 1 AT 7% OF RATED THERMAL POWER, THE REACTOR TRIPPED ON SG #3 LOW-LOW LEVEL WHILE OPERATORS WERE IN THE PROCESS OF TRANSFERRING STEAM GENERATOR (SG) FEEDWATER FLOW FROM THE AUXILIARY FEEDWATER (AFW) SYSTEM TO THE MAIN FEEDWATER (MFW) SYSTEM. AT 0024 CDT, SG #1 EXCEEDED ITS HI-HI WATER LEVEL SETPOINT INITIATING A FEEDWATER ISOLATION (FWI), A TRIP OF BOTH MFW PUMPS AND SUBSEQUENT ACTUATION OF THE MOTOR-DRIVEN AFW PUMPS. PRIOR TO THE FWI AND THE REACTOR TRIP, THE PLANT OPERATOR HAD ATTEMPTED TO STABILIZE A DECREASING LEVEL IN SG #3 BY INCREASING THE SPEED OF THE MFW PUMPS. THIS CAUSED THE LEVEL IN THE OTHER SGS TO RISE AS THE LEVEL IN SG #3 CONTINUED TO DECREASE. INVESTIGATION REVEALED THAT A MANUAL VALVE IN THE LOOP #3 BYPASS FEEDWATER REGULATING VALVE PIPING HAD BEEN INCORRECTLY CLOSED DURING A MAINTENANCE CHECK AND LEFT CLOSED AFTERWARDS. THIS PREVENTED NORMAL FEEDWATER FLOW AFTER THE TRANSFER AND RESULTED IN THE DROP IN SG #3 WATER LEVEL. THE CLOSED VALVE WAS RESTORED TO ITS PROPER POSITION. ADDITIONAL CORRECTIVE ACTION INCLUDED: A PROCEDURE CHANGE TO REQUIRE AN INDEPENDENT VERIFICATION OF FEEDWATER VALVE ALIGNMENTS, ESTABLISHMENT OF AN OPERATING ORDER TO REQUIRE WRITTEN INSTRUCTIONS FOR ANY VALVE MANIPULATION NOT COVERED BY PROCEDURE, AND OPERATOR COUNSELLING.
424 | 4241987030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987030R00.pdf | 1987-06-03 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JUNE 3, 1987 AT 1604 CDT, THE REACTOR TRIPPED FROM 100% OF RATED THERMAL POWER DUE TO THE AUTOMATIC TRIP OF THE MAIN TURBINE. THE ENSUING TRANSIENT LED TO A FEEDWATER ISOLATION (FWI) WHEN T-AVERAGE REACHED 564 DEGREES FAHRENHEIT AND AN AUXILIARY FEEDWATER (AFW) ACTUATION WHICH OCCURRED FROM A LOW-LOW STEAM GENERATOR (SG) WATER LEVEL FROM ALL FOUR SGS. THE OPERATORS RECOVERED SG LEVELS AND RESTORED THE PLANT TO NORMAL SHUTDOWN CONDITIONS. THE REACTOR TRIPPED ON A MAIN TURBINE TRIP INITIATED BY GENERATOR UNIT SECONDARY DIFFERENTIAL RELAY 487-U2 WHICH ACTUATED WHEN A GROUND FAULT OCCURRED ON THE 230 KV TRANSMISSION LINE NEAR VOGTLE. THE ROOT CAUSE OF THE EVENT WAS THE FAILURE TO REMOVE VENDOR SHIPMENT GROUNDS FROM PHASES A AND B OF THE GENERATING UNIT CURRENT TRANSFORMER (CT) SECONDARY WINDING DURING CONSTRUCTION TESTING. THE VENDOR SHIPMENT GROUNDS WERE REMOVED FROM THE CT AND OTHER CTS (I.E., THOSE THAT PROVIDE SIGNALS TO THE DIFFERENTIAL RELAYS) WERE INSPECTED TO ENSURE ONLY ONE COMMON GROUND CONNECTION EXISTED.
424 | 4241987033 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987033R00.pdf | 1987-06-07 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 18 | POWER LEVEL - 018%. ON JUNE 7, 1987, AT 0225 CDT WHILE IN MODE 1 AT 18% OF RATED THERMAL POWER, THE REACTOR TRIPPED ON STEAM GENERATOR (SG) #4 LOW-LOW WATER LEVEL. PLANT OPERATORS WERE TRANSFERRING FEEDWATER FLOW FROM THE BYPASS FEEDWATER REGULATING VALVES (BFRVS) TO THE MAIN FEEDWATER REGULATING VALVES (MFRVS). THE SHIFT SUPERVISOR, WHO WAS ASSISTING THE OPERATOR, MANUALLY OPENED THE SG #2 MFRV TOO FAR. THIS ACTION CAUSED THE WATER LEVEL IN SG #2 TO INCREASE TO ITS HIGH-HIGH WATER LEVEL SETPOINT. A FEEDWATER ISOLATION (FWI), TURBINE TRIP, AND TRIP OF BOTH MAIN FEEDWATER PUMPS AND ACTUATION OF THE MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS OCCURRED. THE FWI CAUSED A RAPID DECREASE IN SG WATER LEVELS TO THE POINT THAT A REACTOR TRIP OCCURRED ON SG #4 LOW-LOW LEVEL. THE EVENT WAS CAUSED BY THE SHIFT SUPERVISOR OPENING THE MFRV TOO FAR. CONTRIBUTING TO THE EVENT WAS A PROCEDURE THAT ALLOWED THE BFRV TO MFRV TRANSFER AT TOO HIGH OF A REACTOR POWER. THE UNIT OPERATING PROCEDURE HAS BEEN REVISED TO REDUCE THE ALLOWABLE MAXIMUM REACTOR POWER LEVEL FOR THE TRANSFER. THE SHIFT SUPERVISOR REVIEWED HIS ERROR AND WAS COUNSELED. AN ADDITIONAL OPERATOR HAS BEEN ASSIGNED TO ASSIST DURING PLANT STARTUP OPERATIONS INVOLVING FEEDWATER FLOW TRANSFER FROM THE BFRVS TO MFRVS.
424 | 4241987034 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987034R00.pdf | 1987-06-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | SU | 4 | POWER LEVEL - 004%. ON JUNE 7, 1987, AT 2022 CDT WITH UNIT 1 IN MODE 2 AT APPROXIMATELY 4.5% OF RATED THERMAL POWER, THE REACTOR TRIPPED ON STEAM GENERATOR (SG) #4 LOW-LOW WATER LEVEL. FEEDWATER TO SGS 1,2 AND 4 WAS BEING SUPPLIED BY THE 'B' MAIN FEEDWATER (MFW) PUMP ONLY. SG #3 WAS BEING SUPPLIED BY THE 'B' MOTOR-DRIVEN AUXILIARY FEEDWATER PUMP. THE SG LOW-LOW LEVEL WAS DUE TO A REDUCED FEEDWATER FLOW CAUSED BY THE PARTIAL DIVERSION OF FEEDWATER THROUGH THE 'A' MFW PUMP. THIS FLOW PATH WAS CREATED BY AN 'A' MFW PUMP DISCHARGE CHECK VALVE FAILURE AND AN 'A' MFW PUMP DISCHARGE MOTOR-OPERATED VALVE (MOV) BREAKER TRIP WHILE THE MOV WAS IN AN OPEN POSITION. THE CHECK VALVE FAILURE HAS BEEN ATTRIBUTED TO INADEQUATE HINGE PIN DESIGN. THE MOV BREAKER TRIP ON OVERCURRENT WAS CAUSED BY THE RECEIPT OF A CLOSURE SIGNAL WHILE THE VALVE WAS OPENING. REDESIGNED HINGE PINS HAVE BEEN INSTALLED IN THE MFW PUMP DISCHARGE CHECK VALVES. INSPECTION OF THE REDESIGNED HINGE PINS IS EXPECTED TO BE PERFORMED BEFORE OR DURING THE FIRST REFUELING OUTAGE. ADDITIONALLY, THE LOGIC FOR THE DISCHARGE MOVS HAS BEEN MODIFIED AND THE APPROPRIATE OPERATING PROCEDURE IS BEING REVISED TO PRECLUDE THE OCCURRENCE OF A BREAKER TRIP AND REDUCE THE NUMBER OF CHALLENGES TO THE CHECK VALVES.
424 | 4241987035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987035R00.pdf | 1987-06-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 97 | POWER LEVEL - 097%. ON JUNE 14, 1987, AT 1724 CDT WITH UNIT 1 IN MODE 1 AT 97% OF RATED THERMAL POWER, THE REACTOR TRIPPED ON STEAM GENERATOR NO. 4 LOW-LOW WATER LEVEL. THE REACTOR PROTECTION SYSTEM INITIATED A REACTOR TRIP, AND STARTED THE MOTOR-DRIVEN AUXILIARY FEEDWATER PUMPS. A TURBINE TRIP AND FEEDWATER ISOLATION (FWI) OCCURRED. THE FWI CAUSED A TRIP OF BOTH MAIN FEEDWATER (MFW) PUMPS. PLANT OPERATORS RESPONDED PROPERLY TO ENSURE PLANT SAFETY. THE EVENT WAS CAUSED BY THE FAILURE OF A HYDRAULIC TUBING CONNECTION. FAILURE TO INSTALL A FERRULE IN THE CONNECTION EVENTUALLY LED TO ITS FAILURE. THE RESULTANT LOW HYDRAULIC PRESSURE CAUSED A MFW PUMP TURBINE CONTROL VALVE TO PARTIALLY CLOSE, LEADING TO A SLOWDOWN IN PUMP SPEED AND A DECREASE IN FEEDWATER TO THE STEAM GENERATORS. THE FAULTY HYDRAULIC TUBING CONNECTION WAS REPLACED AND SIMILAR CONNECTIONS WERE INSPECTED TO ENSURE THEIR INTEGRITY.
424 | 4241987041 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987041R00.pdf | 1987-06-23 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 94 | POWER LEVEL - 094%. ON JUNE 23, 1987, WHILE IN MODE 1 A REACTOR TRIP OCCURRED DUE TO THE AUTOMATIC TRIP OF THE MAIN TURBINE. THE REACTOR TRIP AND SUBSEQUENT TRANSIENT RESULTED IN A FEEDWATER ISOLATION AND ACTUATION OF THE AUXILIARY FEEDWATER SYSTEM. THE OPERATORS RECOVERED SG LEVELS AND RESTORED THE PLANT TO STABLE CONDITIONS. THE MAIN TURBINE TRIP WAS INITIATED BY A GENERATOR TRIP FROM A GENERREX VOLTAGE REGULATOR TROUBLE TRIP. THE HIGH VOLTAGE SWITCHYARD 500 KV INDUCTIVE REACTORS HAD BEEN CLOSED TO REDUCE GRID VOLTAGE. AN EXCESSIVE FIELD CURRENT SIGNAL RESULTING FROM AN IMPROPERLY CALIBRATED FIELD EXCITATION TRANSDUCER CAUSED THE GENERATOR TRIP. THE EVENT WAS CAUSED BY THE FAILURE TO USE THE FIELD CURRENT TRANSDUCER CALIBRATION PROCEDURE. CORRECTIVE ACTIONS INCLUDED THE RECALIBRATION OF FIELD CURRENT TRANSDUCERS, THE PERFORMANCE OF A 'NO-LOAD' FIELD CURRENT CHECK OF THE GENERATOR TO VERIFY DESIGN, AND RESTRICTIONS TO ENSURE THAT TRANSMATION DEVICES ARE USED ONLY WITH CALIBRATED MEASURING AND TEST EQUIPMENT. INSTRUMENT AND CONTROLS SUPERVISION WERE COUNSELLED REGARDING IN-PROGRESS AND POST-WORK REVIEWS, AND THE CONTROL OF ENGINEERS AND CONTRACTOR PERSONNEL.
424 | 4241987047 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987047R00.pdf | 1987-07-08 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 8, 1987, AT 1739 CDT, AND ON JULY 22, 1987, AT 1538 CDT, THE REACTOR TRIPPED FROM 100% OF RATED THERMAL POWER DUE TO AN AUTOMATIC TRIP OF THE MAIN TURBINE. FOLLOWING BOTH TRIPS, THE OPERATORS STABILIZED THE PLANT AT NORMAL SHUTDOWN CONDITIONS. THE REACTOR TRIPPED ON A MAIN TURBINE TRIP INITIATED BY A GENERATOR STATOR COOLING SYSTEM (GSCS) PROTECTION CIRCUIT ACTUATED BY A HIGH TEMPERATURE SIGNAL. THE CAUSE FOR THE JULY 8 EVENT WAS NOT CONCLUSIVELY DETERMINED UNTIL THE JULY 22 EVENT OCCURRED. A MERCOID MERCURY 'WET TYPE' SWITCH, WHICH WAS ACTUATED BY VIBRATION AT A LOWER TEMPERATURE VALUE (APPROXIMATELY 140 DEGREES FAHRENHEIT) THAN THE TRIP SETPOINT (180 DEGREES FAHRENHEIT) VALUE, CAUSED THE TURBINE TRIP. CORRECTIVE ACTIONS INCLUDED REPLACING THE SWITCH WITH A MERCOID 'SNAP TYPE' SWITCH AND RELOCATING TO A NEW LOCATION. A TWO OUT-OF-THREE LOGIC WAS ALSO DEVELOPED UTILIZING THE TEMPERATURE SWITCH, A SPARE UNUSED RTD, AND THE HIGH TEMPERATURE ALARM DETECTOR.
424 | 4241987047 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987047R00.pdf | 1987-07-22 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 8, 1987, AT 1739 CDT, AND ON JULY 22, 1987, AT 1538 CDT, THE REACTOR TRIPPED FROM 100% OF RATED THERMAL POWER DUE TO AN AUTOMATIC TRIP OF THE MAIN TURBINE. FOLLOWING BOTH TRIPS, THE OPERATORS STABILIZED THE PLANT AT NORMAL SHUTDOWN CONDITIONS. THE REACTOR TRIPPED ON A MAIN TURBINE TRIP INITIATED BY A GENERATOR STATOR COOLING SYSTEM (GSCS) PROTECTION CIRCUIT ACTUATED BY A HIGH TEMPERATURE SIGNAL. THE CAUSE FOR THE JULY 8 EVENT WAS NOT CONCLUSIVELY DETERMINED UNTIL THE JULY 22 EVENT OCCURRED. A MERCOID MERCURY 'WET TYPE' SWITCH, WHICH WAS ACTUATED BY VIBRATION AT A LOWER TEMPERATURE VALUE (APPROXIMATELY 140 DEGREES FAHRENHEIT) THAN THE TRIP SETPOINT (180 DEGREES FAHRENHEIT) VALUE, CAUSED THE TURBINE TRIP. CORRECTIVE ACTIONS INCLUDED REPLACING THE SWITCH WITH A MERCOID 'SNAP TYPE' SWITCH AND RELOCATING TO A NEW LOCATION. A TWO OUT-OF-THREE LOGIC WAS ALSO DEVELOPED UTILIZING THE TEMPERATURE SWITCH, A SPARE UNUSED RTD, AND THE HIGH TEMPERATURE ALARM DETECTOR.
424 | 4241987050 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987050R00.pdf | 1987-07-28 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 28, 1987, AT APPROXIMATELY 0941 CDT WITH THE UNIT IN MODE 1 AND AT 100% OF RATED THERMAL POWER, AN AUTOMATIC REACTOR TRIP OCCURRED AS A RESULT OF THE EMERGENCY TRIP HYDRAULIC FLUID PRESSURE TRANSMITTERS SENSING A LOW PRESSURE AND GENERATING A REACTOR TRIP SIGNAL. THIS REACTOR TRIP WAS CAUSED BY PERSONNEL ERROR. AN INSTRUMENT TECHNICIAN EMPLOYED AN IMPROPER TECHNIQUE FOR MAKING TEST CONNECTIONS. CONTRIBUTING TO THIS EVENT WAS AN INADEQUATE ENGINEERING REVIEW BY THE RESPONSIBLE SYSTEM ENGINEER. CORRECTIVE ACTIONS INCLUDED THE DISCIPLINING OF THE INSTRUMENT TECHNICIAN, HIS FOREMAN AND THE SYSTEM ENGINEER. SHOP MEETINGS WERE HELD TO DISCUSS THIS EVENT WITH INSTRUMENT TECHNICIANS. ENGINEERING SUPPORT PERSONNEL RECEIVED EXTENSIVE COUNSELING CONCERNING THIS EVENT.
424 | 4241987063 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987063R00.pdf | 1987-11-05 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON NOVEMBER 5, 1987, PLANT PERSONNEL WERE WORKING ON LEVEL THREE (3) OF THE TURBINE BUILDING. AT 0940 CST WITH UNIT 1 AT 100% RATED THERMAL POWER, A TURBINE TRIP OCCURRED WHEN A TURBINE VIBRATION MONITOR ACTUATED. THE TURBINE TRIP GENERATED A REACTOR TRIP SIGNAL. THE MAIN FEEDWATER SYSTEM ISOLATED AND THE AUXILIARY FEEDWATER SYSTEM ACTUATED. PLANT EQUIPMENT RESPONDED AS DESIGNED AND PLANT OPERATORS STABILIZED THE STEAM GENERATOR WATER LEVELS BY 1001 CST. THE APPARENT CAUSE OF THIS EVENT WAS THE ACTUATION OF VIBRATION MONITOR XE6371. THE ACTUATION WAS CAUSED WHEN THE MONITOR'S CABLING WAS MOVED BY PLANT PERSONNEL PERFORMING WORK ON NEARBY COMPONENTS. CORRECTIVE ACTION INCLUDES LABELING THE CABLES TO ADVISE PLANT PERSONNEL OF THE CABLING'S POTENTIAL TO TRIP THE PLANT.
424 | 4241987066 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241987066R00.pdf | 1987-11-11 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON NOVEMBER 11, 1987, AT 0344 CST WITH UNIT 1 IN MODE 1 (POWER OPERATION) AT 100 PERCENT RATED THERMAL POWER, AN UNPLANNED ACTUATION OF THE REACTOR PROTECTION SYSTEM OCCURRED. PLANT PERSONNEL WERE CONDUCTING A SURVEILLANCE TEST OF THE TRAIN 'A' REACTOR TRIP BREAKERS AS REQUIRED BY THE UNIT'S TECHNICAL SPECIFICATIONS. AS PART OF THIS TEST, THE TRAIN 'A' REACTOR TRIP BREAKERS HAD BEEN OPENED. A SHIFT TECHNICAL ADVISOR (STA) DEPRESSED A SHUNT TRIP TEST PUSHBUTTON ON THE OPPOSITE TRAIN (TRAIN 'B') TRIP BREAKER PANEL CABINET AND A REACTOR TRIP OCCURRED. THE TRAIN 'B' MOTOR DRIVEN AUXILIARY FEEDWATER (MDAFW) PUMP AUTOMATICALLY STARTED. THE TRAIN 'A' MDAFW PUMP WAS MANUALLY STARTED BECAUSE ITS AUTOMATIC INITIATION CIRCUIT WAS BLOCKED AS PART OF THE REACTOR TRIP BREAKERS SURVEILLANCE TESTING. THE TURBINE DRIVEN AFW PUMP AUTOMATICALLY STARTED ON LOW-LOW STEAM GENERATOR WATER LEVEL. OPERATORS STABILIZED PLANT CONDITIONS IN MODE 3 FOLLOWING THE REACTOR TRIP. THIS EVENT WAS CAUSED BY PERSONNEL ERROR, IN THAT AN STA OPENED THE WRONG TRIP BREAKER CABINET AND PUSHED THE OPPOSITE TRAIN'S SHUNT TRIP TEST PUSHBUTTON. CORRECTIVE ACTION INCLUDES BETTER LABELING OF EACH CABINET, REVISING THE SURVEILLANCE PROCEDURE TO INCLUDE SPECIFIC PANEL AND PUSHBUTTON NUMBERS, AND POSITIVE DISCIPLINE OF APPROPRIATE INDIVIDUALS.
424 | 4241988001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988001R00.pdf | 1988-01-17 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 17, 1988, AT 1902 CST, THE REACTOR TRIPPED FROM 100% OF RATED THERMAL POWER DUE TO A LOW FLOW TRIP SIGNAL. THE LOW FLOW TRIP SIGNAL OCCURRED WHEN A NON-SAFETY RELATED SYSTEM PROTECTION RELAY, TYPE K-10, TRIPPED THE REACTOR COOLANT PUMP (RCP) #2. THE KD-10 RELAY IS USED TO PROVIDE FOR FAST CLEARING DURING STALLED ROTOR OR PROLONGED STARTING CONDITIONS AND ALSO PROVIDES REDUNDANT INSTANTANEOUS FAULT DETECTION. IT WAS DETERMINED THAT THE KD-10 RELAY (1NAB06-221) MALFUNCTIONED, SINCE A TRIP CONDITION DID NOT ACTUALLY EXIST. THE RELAY WAS REPLACED AND A CALIBRATION TEST WAS PERFORMED. A DESIGN MODIFICATION HAS BEEN INSTALLED TO ADD SUPERVISORY FAULT DETECTION IN ADDITION TO THE EXISTING KD-10 RELAY SCHEME. FURTHER TESTING FOR THE KD-10 RELAY THAT MALFUNCTIONED IS SCHEDULED TO BE COMPLETED BY MARCH 1, 1988.
424 | 4241988006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988006R00.pdf | 1988-02-15 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON FEBRUARY 15, 1988 AT 1655 CST, A REACTOR TRIP OCCURRED ON UNIT 1 WITH THE PLANT AT APPROXIMATELY 100 PERCENT OF RATED THERMAL POWER. THE REACTOR TRIP WAS INITIATED BY A TURBINE TRIP WHICH RESULTED WHEN A GENERATOR FIELD GROUND TRIPPED THE MAIN GENERATOR. THE FIELD GROUND WAS CAUSED BY A MAINTENANCE ELECTRICIAN PLACING A CONDUCTIVE PROBE ON THE COLLECTOR BRUSH RIGGING WHILE TAKING VIBRATION READINGS. THIS EVENT OCCURRED BECAUSE THE MAINTENANCE FOREMAN FAILED TO ADEQUATELY IMPLEMENT THE MAINTENANCE WORK ORDER INSTRUCTIONS AND FAILED TO PROVIDE ADEQUATE WORK INSTRUCTIONS TO THE MAINTENANCE ELECTRICIAN. CORRECTIVE ACTIONS INCLUDE THE COUNSELING OF THE MAINTENANCE FOREMAN.
424 | 4241988008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988008R00.pdf | 1988-04-07 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 0838 CDT ON APRIL 7, 1988, WITH UNIT 1 OPERATING AT 100 PERCENT RATED THERMAL POWER, A STATOR COOLANT SYSTEM ALARM WAS RECEIVED IN THE CONTROL ROOM. A PLANT EQUIPMENT OPERATOR (PEO) WAS DISPATCHED TO INVESTIGATE AND FOUND SYSTEM WATER TEMPERATURE TO BE INCREASING. CONTROL ROOM OPERATORS PROMPTLY BEGAN TO REDUCE THE TURBINE-GENERATOR/REACTOR LOAD WHILE THE PEO ATTEMPTED TO START THE SECOND STATOR COOLING WATER PUMP. THESE ACTIONS WERE UNABLE TO PREVENT THE TURBINE TRIPPING ON HIGH STATOR COOLANT WATER TEMPERATURE WHICH, IN TURN, CAUSED A REACTOR TRIP AT 0846 CDT. ALL CONTROL RODS INSERTED AND AUXILIARY FEEDWATER (AFW) SYSTEM ACTUATED WHEN THE STEAM GENERATORS (SG'S) REACHED THEIR LOW WATER LEVEL SETPOINTS. THE CAUSE OF THIS EVENT WAS A MANUFACTURING ERROR IN USING AN UNDERSIZED LINKAGE SHAFT ON A STATOR COOLING WATER VALVE (1TCV-6800) TEMPERATURE CONTROLLER. VIBRATION OF THE UNDERLYING EQUIPMENT SKID LED THE UNDERSIZED LINKAGE SHAFT TO STRIP THE MINIMALLY ENGAGED THREADS AND DROP OUT OF A NYLON THUMB NUT, GIVING A SIGNAL FOR VALVE 1TCV-6800 TO CLOSE. CORRECTIVE ACTION INCLUDED REPLACEMENT OF THE TEMPERATURE CONTROLLER.
424 | 4241988013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988013R00.pdf | 1988-04-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON APRIL 24, 1988, AT 0922 CDT, A MANUALLY INITIATED REACTOR TRIP OCCURRED ON UNIT 1 WITH THE REACTOR PLANT AT APPROXIMATELY 100% OF RATED THERMAL POWER. THE LOOP 4 MAIN FEED ISOLATION VALVE (MFIV) FAILED CLOSED AND WOULD NOT RESPOND TO AN OPEN SIGNAL. DUE TO THE STEAM FLOW - FEEDWATER FLOW MISMATCH, THE NO. 4 STEAM GENERATOR (SG) WATER LEVEL WAS DECREASING. THE MANUAL TRIP WAS INITIATED IN ANTICIPATION OF RECEIVING A SG LOW LEVEL SETPOINT AUTOMATIC REACTOR TRIP. THE DIRECT CAUSE OF THE EVENT WAS THAT NO. 4 MFIV FAILED CLOSED. THE MOST PROBABLE ROOT CAUSE IS THAT AN INTERMITTENT FAILURE OF AN AIR SOLENOID VALVE COIL LED TO THE CLOSURE OF NO. 4 MFIV. CORRECTIVE ACTIONS INCLUDED REPLACING EACH COMPONENT, WHICH REASONABLY COULD HAVE CAUSED THE VALVE TO FAIL CLOSED.
424 | 4241988022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988022R01.pdf | 1988-07-14 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 14, 1988, AT 1901 CDT, A GENERATOR/TURBINE/REACTOR TRIP OCCURRED AS A RESULT OF AN OVEREXCITATION CONDITION ON THE GENERATOR FIELD. CONTROL RODS INSERTED. THE MAIN FEEDWATER SYSTEM ISOLATED AND THE AUXILIARY FEEDWATER SYSTEM ACTUATED. CONTROL ROOM OPERATORS RESPONDED PROPERLY TO ASSIST IN PLANT STABILIZATION. AN INVESTIGATION REVEALED THAT THE FAILURE OF A POTENTIAL TRANSFORMER CAUSED AN ELECTRICAL TRANSIENT WHICH LED TO CIRCUIT BOARD FAILURES IN THE GENERATOR CONTROL SYSTEM AND AN INCREASE IN EXCITATION VOLTAGE. CORRECTIVE ACTION INCLUDES REPLACEMENT OF THE FAILED POTENTIAL TRANSFORMER AND CIRCUIT BOARDS.
424 | 4241988024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988024R00.pdf | 1988-07-30 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 30, 1988 AT 1524 CDT, A REACTOR TRIP OCCURRED ON UNIT 1 WITH THE PLANT AT APPROXIMATELY 100% OF RATED THERMAL POWER. THE REACTOR TRIP WAS INITIATED BY A TURBINE TRIP, WHICH RESULTED FROM A GENERATOR TRIP. THE GENERATOR TRIP WAS INITIATED BY PROTECTIVE RELAYS DUE TO A FAULT ON THE PHASE 'A' SECTION OF THE DISCONNECT SWITCH OF THE MAIN TRANSFORMER OUTPUT. THERE WAS A FAILURE (BLOWOUT) OF A TERMINAL PAD WHERE THE 230KV TRANSMISSION LINE CONNECTS TO THE DISCONNECT SWITCH. EVIDENCE INDICATES THAT A CRACK OCCURRED IN THE PAD WHICH LED TO ARCING AND OVERHEATING CAUSING THE BLOWOUT OF THE CONNECTOR. SEVERAL CORRECTIVE ACTIONS WERE TAKEN WHICH INCLUDE THE FOLLOWING. THE FAILED AND DAMAGED PARTS WERE REPLACED. AN INFRARED SCAN WAS PERFORMED ON OTHER CONNECTION POINTS TO IDENTIFY ANY HOT SPOTS. ALSO THE DISCONNECT SWITCH IS SCHEDULED TO BE REPLACED WITH A NEWER TYPE DURING THE REFUELING PERIOD.
424 | 4241988025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988025R02.pdf | 1988-07-31 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 16 | POWER LEVEL - 016%. ON 7-31-88, AT 2014 CDT, LIGHTNING STRUCK THE CONTAINMENT BUILDING AND A REACTOR TRIP OCCURRED. THE MAIN FEEDWATER SYSTEM WAS ISOLATED AND THE AUXILIARY FEEDWATER SYSTEM ACTUATED. CONTROL ROOM PERSONNEL RESPONDED IN ACCORDANCE WITH PLANT PROCEDURES. AN INVESTIGATION REVEALED THAT THE ELECTRICAL SURGE FROM THE LIGHTNING STRIKE SHUTDOWN THE OUTPUT OF THE CONTROL ROD DRIVE MECHANISM POWER SUPPLIES, ALLOWING THE RODS TO DROP INTO THE CORE, AS DESIGNED. SEVERAL OTHER PLANT SYSTEMS WERE AFFECTED BY THE LIGHTNING STRIKE BUT THESE HAD NO MAJOR IMPACT ON PLANT OPERATIONS. CORRECTIVE ACTION INCLUDED PERFORMANCE OF AN EVALUATION OF THE PLANT SURGE PROTECTION WHICH RECOMMENDED THE INSTALLATION OF SURGE SUPPRESSORS IN THE ROD CONTROL POWER CIRCUITS.
424 | 4241988043 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988043R00.pdf | 1988-12-15 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Vogtle 1 | P | WE | PO | 99 | POWER LEVEL - 099%. ON DECEMBER 15, 1988, AT APPROXIMATELY 1340 CST, WHILE PERFORMING A FUNCTIONAL TEST OF THE SERVICE AIR DRYER, INSTRUMENT AIR WAS ISOLATED FROM THE TURBINE BUILDING. THIS RESULTED IN A REDUCTION OF MAIN FEEDWATER FLOW AND DECREASING WATER LEVEL IN THE STEAM GENERATORS. LOAD WAS REDUCED; HOWEVER, STEAM GENERATOR WATER LEVELS CONTINUED TO DECREASE. WHEN WATER LEVELS REACHED 25 PERCENT, THE REACTOR WAS MANUALLY TRIPPED AT THE DIRECTION OF THE UNIT SHIFT SUPERVISOR. THIS EVENT OCCURRED BECAUSE THE SET POINT OF THE PRESSURE SWITCH FOR TURBINE BUILDING INSTRUMENT AIR ISOLATION WAS 15 POUNDS ABOVE NORMAL. THIS RESULTED IN THE ISOLATION OF TURBINE BUILDING INSTRUMENT AIR PRIOR TO THE ISOLATION OF SERVICE AIR. A CONTRIBUTING CAUSE WAS A SCREW HEAD WHICH BLOCKED CONTROL AIR TO THE BLOWDOWN AND INLET ISOLATION VALVES OF THE SERVICE AIR DRYER AND ALLOWED AN OPEN PATH TO THE ATMOSPHERE CORRECTIVE ACTIONS INCLUDED CHANGING THE FREQUENCY OF CALIBRATION OF APPLICABLE PRESSURE SWITCHES, COUNSELING OPERATORS ON THE USE OF PROCEDURES, ADDING PRECAUTIONS TO PROCEDURES THAT MAY CHALLENGE THE AIR SYSTEM, AND ISSUING A MEMO TO OPERATORS ON LESSONS LEARNED FROM THIS EVENT.
424 | 4241988044 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241988044R00.pdf | 1988-12-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | SU | 4 | POWER LEVEL - 004%. ON DECEMBER 17, 1988, ESF AND RPS ACTUATIONS OCCURRED DURING POWER ASCENSION ACTIVITIES. AT 4 PERCENT POWER, THE STEAM GENERATOR (SG) WATER SUPPLY WAS SWITCHED FROM THE AUXILIARY FEEDWATER (AFW) SYSTEM TO THE MAIN FEEDWATER (FW) SYSTEM. THE FW SYSTEM'S BYPASS FEEDWATER REGULATING VALVE (BFRV) FOR SG #1 OPENED NORMALLY BUT DID NOT PROPERLY REGULATE FEEDWATER FLOW. WATER LEVEL INCREASED IN SG #1 UNTIL THE HIGH-HIGH LEVEL SETPOINT WAS REACHED AT 0114 CST. THIS INITIATED A FW ISOLATION AND AN AFW ACTUATION. AN INVESTIGATION FOUND A MALFUNCTIONING BFRV VOLUME BOOSTER WHICH WAS REPLACED AND TESTED PRIOR TO RESUMPTION OF POWER ASCENSION. AT 16 PERCENT POWER, THE SAME BFRV UNEXPECTEDLY CLOSED, CAUSING SG #1 WATER LEVEL TO DROP RAPIDLY. THE REACTOR OPERATOR INITIATED A MANUAL REACTOR TRIP AT 1742 CST, WHEN IT BECAME APPARENT THAT WATER LEVEL COULD NOT BE RECOVERED. ALL RODS INSERTED, FW ISOLATED AND AFW ACTUATED TO RESTORE AND CONTROL SG WATER LEVELS. AN INVESTIGATION FOUND A MALFUNCTIONING SOLENOID VALVE WHICH CONTROLS THE CLOSING OF THE BFRV. THE SOLENOID VALVE WAS REPLACED.
424 | 4241989005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241989005R00.pdf | 1989-02-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 2-10-89, AT APPROX. 0050 CST, CONTROL ROOM OPERATORS RECEIVED MAIN FEEDWATER PUMP TURBINE (MFPT)' A' HIGH VIBRATION ALARMS. A CHECK OF THE VIBRATION MONITOR SYSTEM SHOWED A VIBRATION OF ONLY 1.2 MILS. (THE VIBRATION SYSTEM ALARMS AT 3 MILS AND TRIPS AT 5 MILS). AT APPROX. 0051 CST MFP 'A' TRIPPED. STEAM/FEEDWATER FLOW MISMATCH ALARMS WERE RECEIVED ON ALL 4 STEAM GENERATORS (SG). TURBINE LOAD WAS MANUALLY REDUCED TO APPROXIMATELY 700 MWE AND CONTROL RODS PLACED IN AUTO TO FOLLOW LOAD. STEAM DUMP VALVE CONTROLLERS WERE MANUALLY OPERATED TO ATTEMPT TO MATCH STEAM/FEED FLOW. AT APPROXIMATELY 0053 CST, SG #4 REACHED 20% LEVEL AND THE SHIFT SUPERVISOR DIRECTED THE REACTOR TO BE MANUALLY TRIPPED. FEEDWATER ISOLATION AND START OF AUXILIARY FEEDWATER (AFW) PUMPS OCCURRED AS EXPECTED. HOWEVER, THE TURBINE DRIVEN AFW (TDAFW) PUMP TRIPPED ON OVERSPEED AFTER STARTING. THE CAUSE OF THE MFPT HIGH VIBRATION TRIP CANNOT BE POSITIVELY IDENTIFIED. THE CAUSE OF THE TDAFW PUMP OVERSPEED TRIP, ALTHOUGH NOT POSITIVELY IDENTIFIED, MAY HAVE BEEN CAUSED BY PARTICULATE CONTAMINATION OF THE LUBE OIL, WHICH SERVES AS THE CONTROL SYSTEM HYDRAULIC FLUID. CORRECTIVE ACTIONS INCLUDE TEMPORARILY INSTALLING VIBRATION INSTRUMENTATION TO COLLECT MFP VIBRATION DATA. ADDITIONAL SURVEILLANCES WERE ALSO PERFORMED ON THE TDAFW PUMP TO ENSURE OPERABILITY.
424 | 4241989012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241989012R00.pdf | 1989-05-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 5/9/89, AT APPROX. 0905 CDT, THE UNIT BEGAN EXPERIENCING MAIN FEEDWATER PUMP (MFP) 'B' HIGH VIBRATION ALARMS (6 ALARMS IN 15 SECONDS), WHICH WOULD IMMEDIATELY CLEAR. THE TURBINE BUILDING OPERATOR (TBO) REPORTED NO UNUSUAL NOISE AT THE PUMP. THE ADVANCED TURBINE SUPERVISORY INSTRUMENTATION (ATSI) WAS CHECKED AND READINGS WERE FOUND TO BE BELOW ALARM LEVELS. AT THIS TIME IT WAS THOUGHT THAT PAINTERS, WORKING IN THE AREA, HAD MOVED CABLES CAUSING THE ALARM. ALARMS WERE AGAIN RECEIVED AT 1013 CDT AND A CHECK OF THE ATSI AND A REPORT FROM THE TBO DID NOT INDICATE ANYTHING ABNORMAL. BEARING METAL AND LUBE OIL TEMPERATURES WERE CHECKED ON THE MAIN COMPUTER, AND THE READINGS WERE ACCEPTABLE. ASSISTANCE WAS REQUESTED FROM MAINTENANCE AND ENGINEERING. ADDITIONAL ALARMS WERE RECEIVED BETWEEN 1028 AND 1040 CDT. THE INDIVIDUALS INVESTIGATING THE PROBLEM DID NOT DETECT ANY UNUSUAL VIBRATION OF THE MFP. AT 1040 CDT, MFP 'B' TRIPPED ON HIGH VIBRATION. CONTROL ROOM OPERATORS ATTEMPTED RECOVERY FROM THE PUMP TRIP, BUT WERE NOT ABLE TO PREVENT A REACTOR TRIP AT 1042 CDT DUE TO STEAM GENERATOR #4 LOW-LOW LEVEL. THE CAUSE OF THE FEEDWATER PUMP TRIP WAS A BROKEN SOLDER CONNECTION ON A TEST JACK IN THE ATSI VIBRATION CARD FOR THE LOW PRESSURE BEARING. A CONTRIBUTING CAUSE TO THE REACTOR TRIP WAS A FAILED BISTABLE IN THE CONTROL ROD DRIVE CIRCUITRY.
424 | 4241989016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241989016R01.pdf | 1989-07-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 7/8/89, AT 0327 CDT, A MANUALLY INITIATED REACTOR TRIP OCCURRED ON UNIT 1 WITH THE REACTOR AT 100% OF RATED THERMAL POWER. THE MANUAL TRIP WAS INITIATED BECAUSE THE LOOP 4 MAIN FEEDWATER ISOLATION VALVE (MFIV) FAILED CLOSED RESULTING IN A DECREASE IN THE NO. 4 STEAM GENERATOR LEVEL. THE PLANT WAS STABILIZED IN MODE 3 FOLLOWING THE REACTOR TRIP. TROUBLESHOOTING FOLLOWING THE MANUAL TRIP FAILED TO IDENTIFY THE EXACT CAUSE OF THE SPURIOUS CLOSURE; HOWEVER, 2 POTENTIAL FAILURE MECHANISMS WERE EVALUATED; SOLENOID FAILURE AND AUXILIARY RELAY FAILURE. CORRECTIVE ACTIONS FOR THE 7/8/89 EVENT INCLUDED TROUBLESHOOTING OF THE VALVE CONTROL CIRCUITRY, REPAIR OF THE ASSOCIATED HANDSWITCH FOR A PROBLEM NOTED DURING TROUBLESHOOTING BUT UNRELATED TO THE FAILURE, AND CONTINUED CONTROL LOOP MONITORING WITH A MULTI-CHANNEL RECORDER. ON 8/3/89, THE LOOP 4 MFIV SPURIOUSLY CLOSED AND THE RESULTING DECREASE IN FEEDWATER LED THE OPERATOR TO TRIP THE REACTOR AT 1445 CDT. CONTROL ROOM OPERATORS ACHIEVED STABLE PLANT CONDITIONS BY 1505 CDT. CORRECTIVE ACTION FOR THIS EVENT CONSISTED OF REPLACING A FAILED SOLENOID VALVE AND RETURNING THE VALVE TO THE VENDOR FOR FAILURE ANALYSIS.
424 | 4241989016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241989016R01.pdf | 1989-08-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 7/8/89, AT 0327 CDT, A MANUALLY INITIATED REACTOR TRIP OCCURRED ON UNIT 1 WITH THE REACTOR AT 100% OF RATED THERMAL POWER. THE MANUAL TRIP WAS INITIATED BECAUSE THE LOOP 4 MAIN FEEDWATER ISOLATION VALVE (MFIV) FAILED CLOSED RESULTING IN A DECREASE IN THE NO. 4 STEAM GENERATOR LEVEL. THE PLANT WAS STABILIZED IN MODE 3 FOLLOWING THE REACTOR TRIP. TROUBLESHOOTING FOLLOWING THE MANUAL TRIP FAILED TO IDENTIFY THE EXACT CAUSE OF THE SPURIOUS CLOSURE; HOWEVER, 2 POTENTIAL FAILURE MECHANISMS WERE EVALUATED; SOLENOID FAILURE AND AUXILIARY RELAY FAILURE. CORRECTIVE ACTIONS FOR THE 7/8/89 EVENT INCLUDED TROUBLESHOOTING OF THE VALVE CONTROL CIRCUITRY, REPAIR OF THE ASSOCIATED HANDSWITCH FOR A PROBLEM NOTED DURING TROUBLESHOOTING BUT UNRELATED TO THE FAILURE, AND CONTINUED CONTROL LOOP MONITORING WITH A MULTI-CHANNEL RECORDER. ON 8/3/89, THE LOOP 4 MFIV SPURIOUSLY CLOSED AND THE RESULTING DECREASE IN FEEDWATER LED THE OPERATOR TO TRIP THE REACTOR AT 1445 CDT. CONTROL ROOM OPERATORS ACHIEVED STABLE PLANT CONDITIONS BY 1505 CDT. CORRECTIVE ACTION FOR THIS EVENT CONSISTED OF REPLACING A FAILED SOLENOID VALVE AND RETURNING THE VALVE TO THE VENDOR FOR FAILURE ANALYSIS.
424 | 4241989018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241989018R00.pdf | 1989-10-02 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 1 | P | WE | PO | 87 | POWER LEVEL - 087%. ON 10-2-89, AT APPROXIMATELY 0136 CDT, THE NO. 1 STEAM GENERATOR (SG) TRAIN 'A' MAIN STEAM ISOLATION VALVE (MSIV) FAILED CLOSED. AT 0137 CDT, AN AUTOMATIC REACTOR TRIP OCCURRED DUE TO SG NO. 1 REACHING ITS LOW-LOW WATER LEVEL SETPOINT. A TURBINE TRIP, MAIN FEEDWATER ISOLATION AND AUXILIARY FEEDWATER ACTUATION OCCURRED AS DESIGNED FOLLOWING THE TRIP. THE MSIV CLOSED DUE TO A BLOWN FUSE IN THE CONTROL LOGIC POWER SUPPLY. INVESTIGATIONS REVEALED THAT GROUNDING PROBLEMS EXISTED IN THE 125VDC CONTROL POWER DISTRIBUTION PANEL AND INDICATED THAT A GROUND COULD HAVE EXISTED IN A MSIV LIMIT SWITCH WHICH SHOWED SIGNS OF INTERNAL MOISTURE RELATED DETERIORATION AND ARCING. THE COMBINATION OF THE GROUNDS IN THE CONTROL POWER DISTRIBUTION PANEL AND THE SUSPECT GROUND IN THE MSIV LIMIT SWITCH LIKELY CAUSED THE FUSE TO BLOW. THE GROUNDING PROBLEMS WERE CORRECTED AND THE MSIV LIMIT SWITCH AND FUSE REPLACED. CORRECTIVE ACTION TO PREVENT RECURRENCE INCLUDES COMPLETING A PREVIOUSLY IDENTIFIED TASK OF SEALING THE MSIV LIMIT SWITCHES DURING THE NEXT REFUELING OUTAGE TO PREVENT WATER INTRUSION.
424 | 4241990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241990001R00.pdf | 1990-01-24 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 1 | P | WE | PO | 90 | On 1-24-90, partial stroke testing of a Main Steam Isolation Valve (MSIV) was in progress. During a previous test, the valve had failed to reopen automatically at the 10% closed position as designed. As a result, plant personnel were prepared to install a jumper to reopen the valve if it failed to reopen automatically. The test began and an indicator illuminated at approximately 10% closed; however, unknown to the personnel involved, there were two limit switches which were not adjusted to actuate concurrently. Consequently, when the indicator illuminated, the other limit switch had not yet actuated and it appeared that the valve would not reopen automatically. The jumper was installed to initiate valve reopening; however, position indication was lost and the MSIV went fully closed. MSIV closure resulted in a rapid decrease in water level in Steam Generator (SG) #4 to the low-low level setpoint and an automatic reactor trip occurred at 0133 CST. <br /><br /> An investigation determined that when the jumper was installed, the MSIV control fuses failed, which caused the valve to close. <br /><br /> Corrective actions include: a) fuse replacement, b) procedure revision to include a caution that the indicator may light prior to the valve receiving the reopen signal, and, c) limit switch adjustment to obtain concurrent actuation.
424 | 4241990011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241990011R00.pdf | 1990-04-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 82 | On 4-25-90, at 1257 CDT, the Unit 1 reactor was manually tripped due to decreasing level in steam generator (SG) No. 2. Prior to the trip, a "Steam Generator 2 Flow Mismatch Alarm" annunciator was received and feedwater flow to SG No. 2 was observed to be decreasing rapidly. The Balance of Plant Operator attempted to increase the feedwater flow by increasing the demand signals to Main Feedwater Regulating Valve (MFRV) No. 2 and Bypass Feedwater Regulating Valve No. 2. However, SG No. 2 level continued to fall which forced initiation of the reactor trip. The Auxiliary Feedwater System actuated as designed following the reactor trip to maintain SG levels. By 1310 CDT, the Unit was stabilized in Mode 3.<br /><br /> Subsequent investigation indicated that MFRV No. 2 had closed and caused the event. The MFRV apparently closed when workers installing insulation on the MFRV inadvertently bumped into and mispositioned the local control levers located on the side of the valve positioner. Mispositioning of the local control levers interrupted the control air supply to the valve positioner. Since the local control levers are not used for normal operations, corrective action to prevent recurrence has been taken to remove these levers from both the Unit 1 and Unit 2 MFRVs.
424 | 4241990016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241990016R00.pdf | 1990-07-23 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Vogtle 1 | P | WE | PO | 100 | On 7-23-90 at 0600 CDT, Unit 1 was operating in Mode 1 at 100% power when a 4160/480 volt non-1E transformer (1NB01) experienced an internal fault, causing a trip of the associated feeder breaker. This transformer was supplying power to the speed control circuitry for both of the Main Feedwater Pump (MFP) turbines. The MFPs tripped, the Steam Generator (SG) water levels decreased to 24%, narrow range level, and the reactor operator initiated a manual reactor trip at 0602 CDT. The Main Feedwater System isolated and the motor-driven Auxiliary Feedwater (AFW) pumps started, as expected, when the reactor trip occurred. The turbine driven AFW pump started when two of the four SG's reached their low-low level setpoint. Normal plant conditions were established in Mode 3 (Hot Standby) at 0656 CDT. <br /><br /> The cause of the event was an internal fault in the 1NB01 transformer. Further investigation of the cause of the fault is in progress.
424 | 4241990023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241990023R00.pdf | 1990-12-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On 12-18-90 at 1936 CST, Unit 1 was operating at 100% power when a 4160/480 volt non-1E transformer (1NB10X) experienced an internal fault. This failure resulted in a loss of power for the speed control circuitry for the 1B Main Feedwater Pump (MFP) turbine and certain support systems for emergency diesel generator 1B. Feedwater pump speed, feedwater flow, and Steam Generator (SG) levels decreased. The Reactor Operator initiated a manual reactor trip at 1937 CST after efforts to maintain SG levels were unsuccessful. All safety related functions occurred per design following the reactor trip; however, a non-1E 4160 volt bus failed to automatically transfer to the reserve auxiliary transformers causing a temporary loss of various non-1E house loads. Transfer of the 4160 volt bus was completed manually and normal plant conditions were established for Hot Standby by 1956 CST. <br /><br /> The root cause for the transformer failure is indeterminate; however, several similar transformer failures have occurred at VEGP (reference LER 50-424/1990-016). The involved transformers are GE Class AA/FA, three phase, dry type transformers. The failed transformer has been replaced and further study of possible factors which may have led to the failure is in progress.
424 | 4241992008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241992008R00.pdf | 1992-09-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On September 14, 1992 at 1926 EDT, Unit 1 was operating normally when a steam flow/feed flow mismatch alarm was received. Main feedwater pump (MFP) A speed and discharge pressure rapidly reduced, and the operators manually increased the speed of MFP B to its maximum. Abnormal operating procedure steps were taken to reduce reactor power and turbine power to attain plant operation within the capability of one feedpump. However, a manual reactor trip was initiated at 1928 EDT prior to steam generator (SG) water level reaching the low-low level setpoint. When the SG low-low water level setpoint was reached, the auxiliary feedwater (AFW) pumps started, and normal SG levels were regained.<br /><br /> Troubleshooting determined that the cause of this event was the failure of the MFP A speed controller tracker/driver circuit card. This card supplies power to a slave controller within the automatic speed controller. The card failure caused the slave controller and the automatic speed controller to allow MFP A to slow down due to the loss of speed regulation. The failed circuit card was replaced and will be returned to the vendor for failure analysis.
424 | 4241993008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241993008R00.pdf | 1993-05-03 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 98 | On May 3, 1993, at 0406 EDT, a turbine/reactor trip occurred due to low electrohydraulic control (EHC) system pressure. The main feedwater (MFW) system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Control room personnel observed the actuations and stabilized the steam generator (SC) water levels. Normal unit operation resumed in Mode 3 (Hot Standby). <br /><br /> The direct cause of this event was a failure of the 'A' EHC pump, along with the failure of the standby EHC pump to auto start at the correct pressure. The combination of the two failures prevented the EHC pumps from properly maintaining EHC pressure. The 'A' EHC pump pressure compensator was found to intermittently stick in the unloaded condition.<br /><br /> Additionally, the standby pump automatic start pressure switch was out of calibration, causing the pump to start at a pressure lower than required to maintain EHC pressure above the trip setpoint. The defective pump was replaced, and the low EHC pressure standby pump auto start pressure switch was calibrated and adjusted to the correct setpoint.
424 | 4241993009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241993009R00.pdf | 1993-07-28 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On July 28, 1993, technicians replaced pressurizer pressure transmitter 1PT-457 after it had displayed signs of failure. Following calibration, personnel initiated action to place the new transmitter in service by opening the transmitter's isolation valve, prior to pressurizing the sensing line and transmitter. This caused the pressure in the sensing line, which is shared with transmitter 1PT-458, to drop low enough to trip the 1PT-458 bistable for low pressurizer pressure. Because the bistable for 1PT-457 was already tripped due to the transmitter being out of service, the required 2 of 4 logic for a reactor trip now existed and a trip occurred at 2350 EDT. Upon recovery from the reactor trip, normal unit operations resumed in Mode 3 (Hot Standby). <br /><br /> The cause of this event was a cognitive personnel error on the part of the technicians and their foreman in not returning 1PT-457 to service in accordance with procedural requirements. Certain steps in the procedure that would have ensured that the sensing line and transmitter were pressurized were omitted during performance of the evolution. The technicians and foreman involved were disciplined and reminded of the importance of procedural compliance.
424 | 4241994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241994001R00.pdf | 1994-02-02 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On February 2, 1994, personnel were replacing a pressurizer pressure transmitter in the containment building. During the work, the transmitter swung on one of its mounting bolts and impacted the handle of the isolation valve for its sensing line, causing the valve to open enough to momentarily vent pressure from the sensing line. This sensing line is shared with another pressure transmitter. The momentary venting of the sensing line caused the second pressure transmitter to sense a false low pressure, which completed a two out of four logic for initiating a reactor trip and a safety injection (SI), at 0557 EST. Within seconds, the technician performing the work closed the isolation valve. Control room operators responded to the reactor trip and SI using the emergency operating procedures (EOPs) and the SI signal was reset at 0607 EST. A Notification of Unusual Event (NOUE) was declared at 0610 EST, due to the safety injection into the reactor vessel. The unit was stabilized and normal operation resumed in Mode 3 (hot standby). The NOUE was terminated at 0750 EST. <br /><br /> The cause of this event was a cognitive personnel error by the technician involved when he lost physical control of the pressure transmitter, such that it swung and bumped open the instrument isolation valve, initiating the sequence of events. Appropriate personnel are being briefed regarding this event, with emphasis being placed on attention to detail when performing work on critical plant components.
424 | 4241995002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241995002R00.pdf | 1995-07-23 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On July 23, 1995, at 1803 EDT during a severe thunderstorm, multiple lightning strikes occurred in the immediate vicinity of the plant site with at least one direct lightning strike on the plant. Twenty-one of fifty-three reactor control rods on Unit 1 and all control rods on Unit 2 dropped into the cores. Approximately 1.5 seconds later, both reactors received a trip signal for low pressurizer pressure. The reactor trip breakers opened, dropping the remaining Unit 1 control rods. The main turbines tripped, the main feedwater systems isolated and the auxiliary feedwater systems actuated as expected. Control room personnel responded to transition the plant to stable operation in Mode 3 (hot standby). <br /><br /> The cause of this event was voltage surges in the rod control systems of both units. Voltage surges, initiated by the lightning strikes, affected low voltage circuitry in both rod control systems, causing some of the control rod drive mechanisms (CRDMs) on Unit 1 and all CRDMs on Unit 2 to lose power to stationary gripper coils. This allowed the control rods to drop into the core and both reactors immediately went subcritical. Continued steam demand from the main turbines caused temperature and pressure in the reactor coolant systems to lower until both units tripped on low pressurizer pressure. An evaluation of the rod control systems susceptibility to voltage surges (particularly those induced by lightning strikes) and proposed corrective actions are expected by October 1, 1995.
424 | 4241996006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241996006R01.pdf | 1996-05-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On May 25, 1996, the balance of plant operator (BOP) noticed feedwater trouble alarms for steam generator (SG) #1. The BOP attempted to increase feedwater flow. Concurrently, the shift superintendent (SS) noted a lack of indication lights for SG #1 main feedwater isolation valve (MFIV) 1HV-5227. As SG #1 water level continued to decline, the reactor operator manually tripped the reactor at 0253 EDT. (AFW) actuation occurred as designed. Control room operators responded to stabilize SG water levels and transition the unit to stable operation in Mode 3 (hot standby). <br /><br /> The cause of this event was the failure of a fuse in the control circuit of 1HV-5227. The fuse was replaced and the unit was restarted and returned to power. An analysis of the failed fuse was performed, and no cause for fuse failure at normal operating conditions could be found. However, analysis of a similar fuse from warehouse stock found an inadequate solder joint that could lead to premature fuse failure. Replacement of similar fuses in the same type of application will take place during each unit's next refueling outage.
424 | 4241996012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241996012R00.pdf | 1996-11-27 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On November 27, 1996, a technician was working in the stator cooling water/hydrogen seal oil panel to recalibrate a hydrogen low pressure switch. The technician moved a metal valve tag that shorted across an exposed terminal strip, blowing a fuse in the stator cooling water system. Two temperature switches lost power which initiated a turbine/reactor trip at 0846 EST. The unit was stabilized in Mode 3 (hot standby). <br /><br /> The root causes of this event were the proximity of the conducting metal tag to the electrical terminal, which significantly increased the probability of this event occurring, and poor lighting in the panel which contributed to the technician's inability to recognize the terminal strip under the metal tag. The fuse was replaced and metal tags near terminal strips in the stator cooling water/hydrogen seal oil panel were removed. In addition, the panel's interior light will be replaced when the unit is shutdown.
424 | 4242000002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242000002R00.pdf | 2000-06-05 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On June 5, 2000, at 1140 EDT, the main steam isolation valve (MSIV) for steam generator (SG) #4 closed. Control room operators observed the valve's trouble alarm and also observed the water level decreasing in SG #4. The reactor operator manually tripped the reactor and all rods fully inserted. The unit was stabilized in mode 3 (hot standby). The direct cause of the reactor trip was the closure of the MSIV which was the result of a blown fuse. The investigation into the cause of the blown fuse found no electrical ground in the circuit or evidence of an overcurrent condition. The area around the valve was also checked for signs of water, loose connections or visible damage, with none found. Therefore, the cause of the fuse failure is unknown. The blown fuse and other fuses were replaced and the unit was returned to service. Other actions including component testing and evaluations are planned to determine the cause and prevent recurrence.
424 | 4242000004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242000004R00.pdf | 2000-12-09 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On December 9, 2000, plant personnel were conducting a test of the solid state protection system (SSPS), Train B, per procedure 14421-1, "Solid State Protection System And Reactor Trip Breaker Train B Operability Test." The Balance of Plant operator (BOP) proceeded through the procedure steps in an orderly fashion to section 5.3. When the BOP performed step 5.3.1, "PLACE the MEMORIES Switch to Position 9," an automatic reactor trip occurred at 1015 EST.The root cause of this event was a procedure inadequacy. A recent change to procedure 14421-1 had moved a portion of the testing from procedure section 5.8 to section 5.3. However, this change bypassed a procedure step to place the Input Error Inhibit switch in the "Inhibit" position, which had previously been performed prior to beginning the section 5.8 testing. The failure to place this switch into "Inhibit" allowed the reactor trip test signals to enter SSPS trip logic and complete an actual reactor trip. Procedure 14421-1 was revised to move the section 5.3 testing back to section 5.8 and testing was completed satisfactorily.
424 | 4242001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242001001R01.pdf | 2001-08-24 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On August 24, 2001, with the unit at 100% power, personnel were returning to service the Main Generator Rectifier Bridge 1 after performing corrective maintenance. Upon closure of the disconnect switch, a trip of the main generator occurred on loss of field excitation, causing an automatic turbine/reactor trip at 2307 EDT. All control rods were observed to fully insert, and control room operators acted properly to control steam generator water levels and stabilize the unit in mode 3 (hot standby).An investigation found that, upon returning Rectifier Bridge 1 to service, silicon controlled rectifiers (SCRs) in Rectifier Bridge 4 failed due to a short circuit. This led directly to the loss of the generator excitation field and the generator/turbine/reactor trip. The malfunctioning rectifier bridges were repaired and the unit was returned to service. The failed SCRs that were removed from the rectifier bridges were sent to a laboratory for failure analysis. The analysis was unable to determine the root cause of the failure.
424 | 4242002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242002003R00.pdf | 2002-04-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Vogtle 1 | P | WE | PO | 30 | On April 20, 2002, power ascension was in progress following a refueling outage. At 0500 EDT, a control room alarm was received due to the water level decreasing in steam generator (SG) #4. The reactor operator (RO) increased the speed of the A main feedwater pump (MFP). Almost simultaneously, the balance-of-plant operator recognized that the A MFP mini-flow valve was open and an operator in the turbine building was directed to shut it. Water levels in all four SGs began to rise rapidly, and operators lowered the MFP speed and throttled the main feedwater regulating valves. However, at 0509 EDT, SG #4 reached its high level setpoint which led to a turbine trip, a main feedwater isolation, and an auxiliary feedwater system actuation. The shift superintendent ordered a manual reactor trip, which occurred at 0510 EDT.The causes of this event are: the failure to increase MFP speed in normal increments to correspond with increased water demand as reactor power was rising, and an inadequate response to the SG water levels when it was recognized that levels had dropped too low. The operating crew involved has been counseled on the expectations of managing evolutions and performed just-in-time training prior to assuming the next shift.
424 | 4242004001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242004001R00.pdf | 2004-03-27 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 35 | On March 27, 2004, at 2110 EST, control room operators tied the generator to the grid. At 2150 EST, an operator observed steam flow/feed flow mismatch alarms and noticed that the speed of the inservice main feed pump, MFP B, was increasing. The feed pump speed control was switched from automatic to manual, but to no effect. Operators then changed speed control systems. This also had no effect on the increasing speed, and steam generator (SG) water levels began to fluctuate. Operators manually tripped the reactor at 2205 EST. The operators then tripped MFP B and the auxiliary feedwater system (AFW) actuated. The unit was stabilized in Mode 3 (Hot Standby) at 2209 EST.The cause of this event was a control valve hydraulic operating cylinder sticking in the open position so that the speed of the feed pump turbine could not be controlled. The valve stuck open due to misalignment of the hydraulic cylinder shaft with bushings in the cylinder cover. The bushings were properly aligned, the feed pump returned to service, and the reactor returned to normal power operations.
424 | 4242005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242005001R00.pdf | 2005-01-11 | QR5 | Turbine Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On January 11, 2005, an automatic turbine trip/reactor trip occurred due to a main generator protective relay lockout. A normal reactor trip sequence ensued and the control room staff responded by transitioning the unit to operation in Mode 3 (Hot Standby). A continuity check of field connections for the protective relay showed very high resistance through an auxiliary potential transformer which is connected to the secondary of the generator neutral grounding transformer. Inspection of the connection revealed that a wire on a terminal strip in the secondary circuit wiring of the auxiliary potential transformer had failed and disconnected when touched. The high resistance measurement at the potential transformer was apparently due to this failed connection. An analysis of the failed connection determined there was prior damage to the wire at the point where the lug was attached. The damage most likely occurred when the lug was first installed prior to initial plant startup. Over time, the remaining conductors fatigued due to vibration until the high resistance connection developed. As a result of the high resistance the relay sensed an invalid fault. The connection was repaired and the unit was returned to power operation.
424 | 4242005003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242005003R00.pdf | 2005-04-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On April 29, 2005, operators responded to closure of loop 1 feed water regulating valve, 1FV-510, by taking manual control in accordance with the abnormal operating procedure. Trouble shooting determined the cause to be a failed controller card. Replacement of the failed card was initiated in accordance with a card replacement procedure.During maintenance, the loop 1 feedwater regulating valve unexpectedly shut. As steam generator water level approached the low-low setpoint, operators took action to trip the reactor. However, an automatic reactor trip on low-low steam generator water level occurred V4 second before the manual trip at 2155 EDT. Operators responded properly to stabilize the plant at normal operating temperature and pressure in Mode 3 (Hot Standby). The causes of this event were: a) technical inaccuracies and incomplete information in the procedure used for controller card replacement, and b) inadequate technician training regarding replacement procedure limitations for recent design changes. The failed card was replaced and the unit returned to power. Further corrective actions have been taken to clarify the procedure for intended purpose and limitations and to clarify technical training for the intended purpose of the procedure. Corrective actions are in progress to revise procedures to include replacement directions for the card failure that was experienced and train appropriate personnel on the replacement procedure for the failure that was experienced.
424 | 4242005004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242005004R00.pdf | 2005-10-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On October 17, 2005, at 1816 EDT, Unit 1 was manually tripped from 100% power due to a rapidly decreasing Steam Generator (SG) #2 water level. The Loop 2 Main Feedwater Regulating Valve (MFRV), 1FV0520, closed unexpectedly and could not be re-opened from the control room.A review found that 1FV0520 closed due to an electronic circuit board failure resulting from moisture intrusion into the air operated valve's electro-pneumatic transducer. The transducer was mounted in an inverted manner that did not prevent water ingress and allow drainage. Washdown activities in this area allowed moisture into the transducer, causing the subsequent failure.The failed transducer was replaced and mounted in the upright configuration. Furthermore, the appropriate procedure has been revised to ensure that electro-pneumatic transducers are mounted in the preferred position, and all washdowns within the power block have been halted until proper administrative controls have been established.
424 | 4242006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242006001R00.pdf | 2006-04-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 33 | On April 15, 2006, while at 100% power, the Unit 1 Control Room crew was challenged by an erratic response of the Loop 3 Main Feed Regulating Valve (MFRV), 1FV0530, while operating in automatic. The crew was able to stabilize the valve in manual mode, however, over the next 24 hours the control of the valve continued to degrade. On April 16, 2006, it was decided that Unit 1 would be taken to Mode 3 for investigation of the control issue with 1FV0530. On April 17, 2006, at 0026 EDT, Unit 1 was manually tripped at 33% power when Steam Generator number 3 water level was observed to be slowly increasing with 1FV0530 unable to control level in either automatic or manual.A review found that 1FV0530 operated erratically due to a failed I/P transducer, which resulted in the inability to reduce feedwater flow requiring a manual reactor trip. Based on the results of the observations and failure analysis performed on the I/P transducer, two failures were identified. One failure was the supply air input connector and the resultant electrical to pneumatic conversion process for a valve internal to the controller, and the second failure was the electronic circuit board. The failed transducer and the remaining Unit 1 MFRV I/P transducers were replaced with different make and model I/P transducers prior to the unit restart.
424 | 4242009002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242009002R00.pdf | 2009-12-07 | QL7 | Degraded condenser vacuum | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On December 7, 2009, at approximately 18:01 hours Eastern Standard Time (EST) with Unit 1 operating at 100 percent rated thermal power, an automatic turbine trip occurred due to low main condenser vacuum. In response to the turbine trip, the Reactor Protection System (RPS) actuated and automatically opened the reactor trip breakers. All control rods fully inserted into the core and all safety systems responded per design. Both Motor Driven Auxiliary Feedwater pumps and the Turbine Driven Auxiliary Feedwater pump started in accordance with plant design due to lo-lo steam generator water level in two steam generators. The unit was stabilized in Mode 3.The cause of the low condenser vacuum was determined to be inadvertent operation of a control room handswitch that resulted in a de-energization of a non-lE 480 volt switchgear. The loss of power to the non-lE 480 volt switchgear resulted in the defeat of an interlock on the loop seal drain valve for the standby Steam Jet Air Ejector (SJAE) which allowed the valve to open. Once the water in the loop seal had drained to the main condenser, a path between the condenser and the atmosphere was established and the main condenser vacuum started to decline. Approximately nine minutes elapsed from the time the handswitch was inadvertently opened until the low main condenser vacuum turbine trip setpoint was reached which resulted in the automatic turbine trip and subsequent automatic reactor trip.
424 | 4242009003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242009003R00.pdf | 2009-12-09 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Vogtle 1 | P | WE | PO | 24 | On December 09, 2009 at approximately 23:10 hours Eastern Standard Time (EST), during power ascension from an unplanned shutdown, with the unit operating at approximately 24 percent rated thermal power, the reactor was manually tripped. As preparations were being made to synchronize the main generator to the grid, high vibrations were experienced on the high pressure turbine. Due to the high vibrations on the turbine, the turbine was manually tripped. As the turbine was coasting down vibration levels continued to increase. Therefore condenser vacuum was broken to slow the turbine to minimize any potential damage. Prior to breaking condenser vacuum and in anticipation of the trip of the operating main feedwater pump due to low condenser vacuum, the control room operators manually tripped the reactor.Once condenser vacuum had decreased below the main feedwater pump trip setpoint, the main feedwater pump tripped and the motor driven auxiliary feedwater (AFW) pumps automatically started. All control rods fully inserted and all safety systems responded in accordance with plant design. The plant was stabilized in Mode 3.
424 | 4242011001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242011001R00.pdf | 2011-04-20 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On April 20, 2011 with Unit 1 operating in Mode 1 at 100 percent rated thermal power at approximately 1734 hours Eastern Daylight Time, reactor trip breaker 1A unexpectedly opened. This initiated a turbine trip and subsequent trip of the 1B reactor trip breaker. Feedwater isolation occurred on low average reactor coolant system temperature and an auxiliary feedwater system actuation occurred on low steam generator level as expected. All rods fully inserted and the plant was stabilized in Mode 3.Extensive troubleshooting was performed to identify the cause of the 1A reactor trip breaker spuriously opening. However, the exact cause was not identified. Consequently, as a precautionary measure the reactor trip breaker, the under voltage driver card and shunt trip relay were all replaced. Additionally, recorders were installed to monitor voltages at various components in the breaker UV trip circuit in an attempt to identify the source of the spurious signal, should another trip occur.
424 | 4242011002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242011002R00.pdf | 2011-08-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On August 31, 2011 with Unit 1 operating in Mode 1 at 100 percent rated thermal power at approximately 0906 hours Eastern Daylight Time, the Unit 1 reactor automatically tripped. In preparation for maintenance on the controls for the main feedwater regulating valve (MFRV) on steam generator (S/G) 2, the valve was placed on an air gag. The air gag maintains the MFRV in position and allows minor changes in steam generator water level to be controlled by the bypass feedwater regulating valve (BFRV). However, shortly after the air gag was installed, feedwater flow to S/G 2 increased beyond the capability of the BFRV to control. The increase in feedwater flow to S/G 2 resulted in water level on S/G 2 exceeding the Hi-Hi nominal trip setpoint (NTS). This caused a main feedwater isolation, turbine trip and subsequent reactor trip in accordance with plant design.The cause of the event was due to increased air pressure being supplied to the MFRV when the valve was placed on the air gag. The first corrective action was revising the procedure to ensure calibrated test gauges are used to determine the pressure setting of the regulator for the air gag and for an operator to be present while the MFRV is controlled by the air gag. The second corrective action is to replace the contact type potentiometer used in the MFRV control circuit which has been proven unreliable.
424 | 4242012002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242012002R00.pdf | 2012-04-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On April 14, 2012, at approximately 1346 Eastern Daylight Time (EDT) time, with Unit 1 operating in Mode 1 at 100 percent rated thermal power, Unit 1 operators initiated a manual reactor trip due to the loss of flow from the 1B Main Feedwater Pump (MFP). The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the loss of 1B MFP flow was the failure of a "Position 5" circuit board in the feed pump turbine speed control circuit. This board failure is preliminarily attributed to component aging.The failed board has been shipped to a vendor for a detailed failure analysis. Upon review of the detailed failure analysis, the conclusions, if different than component aging, will be provided in a Supplemental LER. The controller board is obsolete and no longer has original manufacturer support. The prompt corrective action was to replace the subject circuit board.The safety significance of this event is low. There were no adverse effects on the health and safety of the public.
424 | 4242014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242014002R00.pdf | 2014-04-12 | QR6 | Manual Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 28 | On 4/12/14 at 20:08, Unit 1 Reactor was manually tripped from 28 percent power. The manual trip occurred during power ascension following the 1R18 refueling outage. Control room operators received a Loop 1 Train B main steam isolation valve (MSIV) trouble annunciator followed by the MSIV not fully open annunciator. Control room operators recognized steam generator 1 level and loop 1 steam flow lowering and manually tripped the reactor.<br /><br /> Unit 1 was stabilized in Mode 3. Plant systems responded as expected with decay heat removal via Auxiliary Feedwater and steam discharge to the Main Condenser. Unit 2 was unaffected and there were no adverse effects on plant safety or on the health and safety of the public. This incident is of very low safety significance.
424 | 4242014004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242014004R00.pdf | 2014-07-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On July 27, 2014 at approximately 1409 Eastern Daylight Time, Vogtle Unit 1 was operating in Mode 1 at 100 percent power. While surveillance testing was being performed on the Main Feed Pump A (MFP A) a control oil leak developed in the lockout solenoid valve. The reduced control oil pressure resulted in a reduction of feed pump speed. Control Room Operators observed lowering feedwater flow to the Steam Generators and manually actuated the Reactor Protection System (RPS) system which resulted in a turbine-generator trip. All rods fully inserted into the core, the Main Feedwater Isolation system and the Auxiliary Feedwater system automatically actuated as expected. The unit was stabilized in Mode 3 and decay heat was discharged to the condenser. The cause of the event was a failure of the trip lockout solenoid valve which led to reduced pressure on the trip relay for MFP-A which reduced the speed of the pump and consequently the total feed flow to the Steam Generators.<br /><br /> The safety significance of the event is very low. Unit 2 was not affected and there were no adverse effects on the health and safety of the public.
424 | 4242017001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242017001R00.pdf | 2017-02-03 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 1 | P | WE | PO | 100 | On February 03, 2017 at 1545 EST, Vogtle Unit 1 was operating in Mode 1 at 100 percent power when the Loop 1 Outboard Main Steam Isolation Valve (MSIV)[ISV], 1HV30066, began drifting closed due to hydraulic oil leak. Operating crew identified the issue and initiated a manual reactor trip due to the MSIV[ISV] drifting closed. All control rods fully inserted and all equipment actuated as designed. <br /><br /> Unit 1 was stabilized in Mode 3 with the heat sink being maintained by Auxiliary Feedwater (AFW)[BA] and through the Atmospheric Relief Valves (ARVs)[RV]. The Loop 1 MSIV[ISV] closing was caused by an o-ring failure that led to a loss of hydraulic oil used to maintain the MSIV[ISV] in the open position. This event had no adverse effect on the health and safety of the public, and is of very low safety significance. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv)(A) due to manual and automatic actuation of a systems listed in 10CFR50.739(a)(2)(iv)(B). Unit 2 was unaffected.
424 | 4242018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4242018001R00.pdf | 2018-07-03 | QR6 | Manual Reactor Trip | [45 empty] | Vogtle 1 | P | WE | PO | 100 | At 0954 EDT on July 3, 2018, with Unit 1 in Mode 1, 100 percent power, the reactor was manually tripped due to high steam generator water level. The high steam generator water level was caused by a controller failure on Heater Drain Tank B which led to a feedwater oscillation on the secondary side of the plant. This oscillation caused steam generator water levels to increase. Control Room operators monitored this increase and manually tripped the plant prior to reaching the automatic trip setpoint. <br /><br /> The unit was stabilized in Mode 3 with decay heat removed through the main steam lines through the steam dumps and into the condenser. <br /><br /> This event had no adverse effects on the health and safety of the public and is of very low safety significance. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). Unit 2 was not affected.
425 | 4251989019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989019R00.pdf | 1989-05-02 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 63 | POWER LEVEL - 063%. ON 5-2-89, PERSONNEL WERE PERFORMING A CHECK OF TURBINE TRIP DEVICES PER PROCEDURE 14286-2, 'WEEKLY TURBINE TRIP DEVICE OPERABILITY TEST', PRIOR TO PLACING THE TURBINE IN STANDBY. AN OVERSPEED TRIP DEVICE TEST MALFUNCTIONED AND, AFTER CONSULTING THE TURBINE VENDOR REPRESENTATIVE, THE OPERATOR ATTEMPTED TO RESET THE MALFUNCTION USING THE 'STOP/GO NORMAL' BUTTON. WHEN THIS BUTTON WAS PUSHED AND RELEASED, AT 1102 CDT, THE TURBINE TRIPPED WHICH RESULTED IN A REACTOR TRIP. PRIOR TO THE TURBINE TRIP, A DEFECTIVE WELD IN A ONE INCH STEAM LINE WAS RELEASING STEAM INTO AN AREA UNDER THE TURBINE FRONT STANDARD WHERE THE TURBINE TRIP DEVICE CONTROLS ARE LOCATED. THE CAUSE OF THE TURBINE TRIP HAS NOT BEEN DETERMINED DESPITE EXTENSIVE TROUBLESHOOTING. HOWEVER, IT COULD BE POSTULATED THAT THE STEAM LEAK AFFECTED MECHANICAL OR ELECTRICAL COMPONENTS TO PRODUCE THE TRIP. FOLLOWING THE TRIP, THE WELD WAS REPAIRED AND THE TRIP DEVICE OPERABILITY TESTS WERE REPEATED SEVERAL TIMES BUT THE TURBINE TRIP DEVICE MALFUNCTION COULD NOT BE DUPLICATED.
425 | 4251989020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989020R00.pdf | 1989-05-12 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 78 | POWER LEVEL - 078%. ON 5-12-89, WHILE PERSONNEL WERE PERFORMING SURVEILLANCE OF NUCLEAR INSTRUMENT CHANNEL N44, A 2 OUT OF 4 HI FLUX RATE TRIP COINCIDENCE SIGNAL WAS RECEIVED, CAUSING AN AUTOMATIC REACTOR TRIP. POWER RANGE CHANNEL N43 EXPERIENCED A MOMENTARY LOSS OF POWER, WHICH TRIPPED THE RATE TRIP BISTABLE ON N43. THE CONTROL ROOM OPERATOR ACKNOWLEDGED THE ALARM FOR THE TRIPPED BISTABLE, BUT FAILED TO NOTICE THAT THE WRONG BISTABLE HAD TRIPPED FOR THE WORK BEING PERFORMED. A STEP OF THE SURVEILLANCE PROCEDURE, WHICH WAS BEING PERFORMED FOR N44, REQUIRES THE FUSES TO BE PULLED. THIS TRIPPED THE RATE TRIP BISTABLE FOR N44. THE N43 AND N44 BISTABLES SATISFIED THE 2 OUT OF 4 LOGIC FOR A POWER RANGE TRIP. THE REACTOR TRIP BREAKERS OPENED, TRIPPING THE REACTOR AT 1429 CDT. ALL AUTOMATIC SYSTEMS FUNCTIONED AS DESIGNED. THE CONTROL ROOM OPERATORS BROUGHT THE PLANT TO STABLE CONDITIONS IN MODE 3 (HOT STANDBY). THE CAUSES OF THIS EVENT WERE THE LOSS OF POWER TO CHANNEL N43 AND THE FAILURE OF CONTROL ROOM OPERATORS TO NOTICE THAT THE WRONG BISTABLE HAD TRIPPED. TROUBLESHOOTING CHANNEL N43 DID NOT REVEAL THE CAUSE FOR THE LOSS OF POWER. A COPY OF THIS LER WILL BE PLACED IN THE OPERATION REQUIRED READING BOOK.
425 | 4251989021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989021R01.pdf | 1989-05-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 12 | POWER LEVEL - 012%. ON 5-22-89, PREPARATIONS WERE UNDERWAY TO START UP THE MAIN TURBINE. AT APPROXIMATELY 1547 CDT, STEPS WERE IN TO BRING THE TURBINE SPEED UP TO 180 AT 1605 CDT, INDICATIONS OF A STEAM/FEED MISMATCH PROBLEM WERE SEEN ON STEAM GENERATOR (SG) #2 AND THE REACTOR OPERATOR (RO) OBSERVED A DECREASE IN TAVE GREATER THAN EXPECTED. BECAUSE SG LEVELS AND PRESSURE WERE DECREASING, THE BALANCE OF PLANT OPERATOR TRIPPED THE TURBINE AT 1606 CDT. FEED TO THE STEAM GENERATORS WAS INCREASED AND THE STEAM DUMPS WERE MANUALLY CLOSED. HOWEVER, AT 1607 CDT, AN AUTOMATIC REACTOR TRIP OCCURRED ON LOW-LOW LEVEL IN SG #2. CONTROL ROOM OPERATORS TOOK APPROPRIATE ACTIONS TO STABILIZE THE UNIT IN MODE 3 (HOT STANDBY). THE DIRECT CAUSE OF THE EVENT WAS THE FAILURE OF THE INTERCEPT VALVES TO OPEN AND A CONTRIBUTING CAUSE WAS OPERATOR OVERSIGHT IN NOT RECOGNIZING THE INTERCEPT VALVES' FAILURE TO OPEN AS TURBINE SPEED WAS INCREASED. WHEN THE MAIN TURBINE REACHED 1800 RPM, THE CONTROL VALVES OPENED FURTHER TO MAINTAIN A CONSTANT TURBINE SPEED CREATING A LARGE STEAM LOAD. THIS CAUSED PRESSURIZATION OF THE HIGH PRESSURE TURBINE AND MOISTURE SEPARATOR REHEATERS (MSR), EVENTUALLY LIFTING THE 'B' MSR RELIEF VALVE. THE OPERATOR TRIPPED THE MAIN TURBINE, SG WATER LEVELS LOWERED AND A REACTOR TRIP OCCURRED. CORRECTIVE ACTIONS INCLUDED ADJUSTMENT OF THE CLOSING BIAS VOLTAGE ON THE INTERCEPT VALVE CIRCUIT CARDS.
425 | 4251989024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989024R00.pdf | 1989-07-26 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 7-26-89, AT 0136 CDT, WHILE PERSONNEL WERE PERFORMING CORRECTIVE MAINTENANCE ON POWER RANGE NUCLEAR INSTRUMENTATION CHANNEL 2N43, A 2 OUT OF 4 OVERTEMPERATURE DELTA-T (OTDT) TRIP SIGNAL WAS RECEIVED AND CAUSED AN AUTOMATIC REACTOR TRIP FOR VEGP UNIT 2. THE CORRECTIVE MAINTENANCE ON 2N43 REQUIRED THE CHANNEL 111 OTDT REACTOR TRIP BISTABLE TO BE TRIPPED AS A PART OF THE REMOVAL FROM SERVICE PROCESS. A LOSS OF INPUT FROM PRESSURIZER PRESSURE CHANNEL 2P458 THEN OCCURRED AND CAUSED THE CHANNEL IV OTDT REACTOR TRIP BISTABLE TO TRIP. THIS COMPLETED THE 2 OUT OF 4 LOGIC REQUIRED FOR REACTOR TRIP ON OTDT. BY 0156 CDT, THE PLANT HAD BEEN STABILIZED IN MODE 3. THE FAILURE OF CHANNEL 2P458 WAS CAUSED BY THE FAILURE OF AN OPERATIONAL AMPLIFIER IN THE NON-ISOLATED SECTION OF AN NLP2 PROCESS CARD. THIS CHANNEL HAD SPIKED LOW ON TWO SEPARATE OCCASIONS SEVERAL DAYS EARLIER BUT TROUBLESHOOTING FAILED TO IDENTIFY THE EXACT CAUSE OF THE PROBLEM UNTIL AFTER THE REACTOR TRIP. AN ADDITIONAL SPIKING PROBLEM HAD ALSO BEEN EXPERIENCED ON CHANNEL 2N43 AND WAS STILL BEING INVESTIGATED AT THE TIME OF THE EVENT. CORRECTIVE ACTION CONSISTED OF REPLACING THE DEFECTIVE NLP2 CARD FOR CHANNEL 2P458 AND REPLACING A SUSPECT CARD FOR CHANNEL 2N43.
425 | 4251989027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989027R00.pdf | 1989-10-11 | QR3 | Reactivity Control Imbalance | [45 empty] | Vogtle 2 | P | WE | PO | 58 | POWER LEVEL - 058%. ON 10/11/89, AT 2333 CDT, AN AUTOMATIC REACTOR TRIP OCCURRED WITH THE REACTOR IN STABLE OPERATION AT 58% OF RATED THERMAL POWER. REQUIRED AND THE REACTOR WAS STABILIZED IN MODE 3 WITHOUT INCIDENT. NO ANNUNCIATOR OR OTHER WARNING OF A PROBLEM PRECEDED THE REACTOR TRIP. FOLLOWING A REVIEW OF COMPUTER PRINTOUTS OF DATA ASSOCIATED WITH THE TRIP, THE FIRST OUT ANNUNCIATOR WAS IDENTIFIED AS A HIGH FLUX RATE TRIP ANNUNCIATOR. OPERABILITY TESTING OF THE CONTROL RODS THEN INDICATED THAT A PROBLEM EXISTED WITH ROD K-2 IN CONTROL BANK B. INVESTIGATION OF THE CONTROL ROD CIRCUITRY IDENTIFIED A FAILED DIODE WHICH HAD APPARENTLY RESULTED IN A LOSS OF CURRENT TO THE STATIONARY GRIPPER COIL. THIS ALLOWED THE ROD TO DROP INTO THE CORE AND INITIATE A NEGATIVE FLUX RATE TRIP. CORRECTIVE ACTION INCLUDED REPLACING THE DIODE FOR ROD K-2.
425 | 4251989029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989029R00.pdf | 1989-11-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 11-5-89, PLANT PERSONNEL WERE RETURNING A HEATER DRAIN TANK HIGH LEVEL DUMP VALVE, 2LV-4333, TO SERVICE FOLLOWING REPLACEMENT OF VALVE PACKING AND GASKETS. THE VALVE WAS ISOLATED FROM THE HEATER DRAIN TANK AND OPERATORS NOTICED IT INDICATED 30% OPEN. TO CHECK OPERABILITY, THE OPERATORS ISOLATED THE AIR LINE TO THE VALVE, WHEREUPON IT WENT FULL OPEN, AS EXPECTED. ATTRIBUTING THE 30% OPENING TO A VALID DEMAND SIGNAL, OPERATORS BEGAN TO OPEN THE VALVES WHICH HAD ISOLATED 2LV-4333. AT THIS POINT, THE OPERATORS NOTICED STEAM AND WATER COMING FROM THE PACKING. THE 30% OPEN VALVE CAUSED THE HEATER DRAIN TANK TO DUMP TO THE MAIN CONDENSER. THIS RESULTED IN LOW MAIN FEEDWATER PUMP SUCTION PRESSURE WHICH CAUSED THE PUMP TO TRIP. IN ADDITION, THE STANDBY CONDENSATE PUMP FAILED TO START ON LOW FEEDWATER PUMP SUCTION PRESSURE. THE REDUCED FEEDWATER FLOW RESULTED IN A RAPID DECREASE IN STEAM GENERATOR WATER LEVELS. ANTICIPATING AN AUTOMATIC REACTOR TRIP, CONTROL ROOM OPERATORS INITIATED A MANUAL REACTOR TRIP WITH STEAM GENERATOR LEVELS AT 19% (NARROW RANGE INDICATOR) AT 1223 CST. VALVE 2LV-4333 MOVED TO THE 30% OPEN POSITION DUE TO A DEFECTIVE O-RING (WHICH WAS REPLACED) IN THE VALVE ACTUATOR. THE STANDBY CONDENSATE PUMP FAILURE TO START WAS DUE TO ITS BREAKER BEING IMPROPERLY RACKED IN. THE BREAKER WAS RACKED IN PROPERLY AND THE PUMP TESTED SUCCESSFULLY.
425 | 4251989031 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251989031R00.pdf | 1989-12-02 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 12-2-89, PLANT PERSONNEL WERE RELEASING A CLEARANCE ON HEATER DRAIN TANK (HDT) HIGH LEVEL DUMP VALVE 2LV-4334. THE HIGH LEVEL DUMP VALVE FOR MOISTURE SEPARATOR REHEATER (MSR)'D', 2LV-4525, WAS IN A 50% JACKED-OPENED POSITION DUE TO 2LV-4334 BEING ISOLATED. UPON OPENING THE VALVE WHICH ISOLATED 2LV-4334, IT BECAME EVIDENT THAT 2LV-4334 WAS NOT CLOSED. THE HDT LEVEL DECREASED AND THE NORMAL LEVEL CONTROL VALVE, 2LV-4332, CLOSED. THE ISOLATION VALVE WAS RECLOSED AND HDT LEVEL ROSE; HOWEVER, 2LV-4332 FAILED TO REOPEN RESULTING IN RISING FEEDWATER HEATER LEVELS AND, DUE TO THE CONFIGURATION OF 2LV-4525, MSR D LEVEL ROSE AS WELL. AT 0341 CST, MSR D LEVEL REACHED THE HIGH LEVEL SETPOINT GIVING A TURBINE/REACTOR TRIP. THE ROOT CAUSE FOR THE EVENT WAS COGNITIVE PERSONNEL ERROR INVOLVING REASSEMBLY OF 2LV-4334. THE VALVE WAS REASSEMBLED SUCH THAT ITS POSITION INDICATION SHOWED CLOSED WHEN IT WAS ACTUALLY FULL OPEN. FOR 2LV-4332, THE LEVEL CONTROL SENSING LINES WERE DISCOVERED TO BE CLOGGED WHICH RESULTED IN ITS MALFUNCTION. ACTIONS TO PREVENT RECURRENCE INCLUDE DISCUSSING THIS EVENT IN MAINTENANCE SHOP MEETINGS, IMPLEMENTATION OF A PERIODIC TASK TO BLOWDOWN THE LEVEL CONTROL SENSING LINES ASSOCIATED WITH 2LV-4332, AND INCLUSION OF THIS EVENT IN OPERATOR CONTINUING TRAINING.
425 | 4251990002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251990002R00.pdf | 1990-03-20 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On 3-20-90, at 0820 CST, a Unit 2 generator primary differential relay energized causing a generator trip, turbine trip, and reactor trip. The relay energized upon a phase to ground fault which occurred when a truck operator backed into a support pole for a 230kv phase C "switcher" feeder line for Unit 1 Reserve Auxiliary Transformer (RAT) A. The 230kv line came in contact with the ground causing a fault which also tripped Unit 1 RAT A and Unit 2 RAT B. Diesel Generator 2B started automatically and restored power to emergency bus 2BA03. A loss of power to certain non-1E busses resulted in a trip of Reactor Coolant Pumps 2 and 4. At 1035 CST, normal operating procedures were entered after the Unit was stabilized in Mode 3. <br /><br /> Although the initiating event was the truck backing into the 230kv support pole, causing a phase to ground fault, the Unit should not have tripped on the ground fault current recorded during this event. Investigation determined the cause for the actuation of the generator primary differential relay was incorrect tap settings for variable ratio current transformers located on the generator main output breakers. A contributing cause was the failure to test the relay to verify that it was receiving the proper voltage and current signals from the current transformers. <br /><br /> The tap settings for the current transformers were corrected and the remaining protective relays will be tested to verify they are receiving proper voltage and current signals.
425 | 4251990007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251990007R00.pdf | 1990-05-06 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On 5-6-90, at 2039 CDT, control room operators received trouble alarms indicating closure of Main Steam Isolation Valve (MSIV) 2HV-3026A and Steam Generator (SG) #3 low-low water level. An automatic reactor trip ensued. The Main Feedwater System isolated and the Auxiliary Feedwater System started as designed. Unit conditions were stabilized in Mode 3 at 2050 CDT.<br /><br /> The direct cause of this event was the closure of the MSIV, which resulted in the reactor trip when SG #3 reached its low-low water level setpoint. An investigation of the MSIV controls found that the air solenoid to the valve's hydraulic pump was not energized so that air pressure was not available to drive the pump motor. Further investigation revealed that the AX1 relay had failed. The AX1 relay energizes both the air supply solenoid and the hydraulic dump solenoid to hold the MSIV open. When the AX1 relay failed, the loss of hydraulic fluid pressure to the valve caused the MSIV to close. The failure of the relay was the root cause for this event. <br /><br /> The failed relay was replaced and the MSIV was tested and verified to operate satisfactorily. The failed relay has been returned to the vendor for analysis.
425 | 4251990008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251990008R00.pdf | 1990-06-28 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 2 | P | WE | PO | 87 | On 6-28-90, indication was received in the control room that Main Steam Isolation Valve (MSIV) 2HV-3026A was closing. Operators who were dispatched to investigate found hydraulic fluid spraying from the valve. After an unsuccessful attempt to keep the valve open, a manual reactor trip was initiated at 1906 CDT due to decreasing level in Steam Generator No. 3. A feedwater isolation and an auxiliary feedwater actuation occurred per design. By 1947 CDT, the unit had been stabilized in Mode 3 without incident. <br /><br /> The cause for the MSIV closure was the failure of an o-ring which seals the connection of the "non-pump side" manifold assembly to a boss on the actuator cylinder. Factors which could have contributed to the o-ring failure included a slight misalignment of the cylinder boss and manifold assembly, a small low spot at the edge of the actuator cylinder boss, and evidence that the o-ring may have been pinched on installation. As a temporary modification, a spacer and a smaller diameter o-ring have been installed to ensure the o-ring seating surface is not too close to the outside diameter of the boss. The proposed permanent modification is to machine the boss to provide a better seating surface.
425 | 4251990009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251990009R00.pdf | 1990-06-30 | QP5 | Excessive Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 18 | On 6-30-90, a prolonged delay was experienced in rolling the Unit 2 turbine and synchronizing the generator to the grid. During this delay, reactor power was allowed to increase steadily due to xenon burnout. Since synchronization appeared imminent and to avoid production of liquid radwaste, the Shift Superintendent (SS) decided not to borate to hold power within the normal range for synchronization but rather to proceed with the transfer of Steam Generator (SG) level control to the Main Feedwater Regulating Valves (MFRV's). This action did not follow the normal sequence provided for by the Unit Operating Procedure (UOP) and, due to a further delay in synchronization, SG level control became difficult. Subsequently, a feedwater isolation and a turbine trip occurred when a SG reached its high-high level setpoint. SG levels then fell rapidly and forced initiation of a manual reactor trip at 1150 CDT.<br /><br /> All systems responded appropriately and by 1204 CDT the unit had been stabilized in Mode 3.<br /><br /> The root cause for the event was a cognitive personnel error by the SS. The SS was aware of the difficulty that could be expected in controlling SG levels with the turbine unloaded and reactor power continuing to rise. However, he elected to operate in this configuration and authorized the sequence deviation involving the transfer to the MFRV's. <br /><br /> The SS has been counseled and the UOP will be revised to identify procedural steps which must be performed in the specified sequence unless authorization is obtained from the Manager Operations or higher authority.
425 | 4251991005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251991005R00.pdf | 1991-02-18 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On 2-18-91 at 0747 CST, the control room operators observed loss of feedwater and steam flow/feed flow mismatch annunciators, determined that a slowdown of Main Feedpump (MFP) "A" had occurred, and saw that steam generator (SG) water levels were dropping. The reactor control rods were inserted, and the turbine load was reduced. The operators attempted to increase MFP "B" speed in order to maintain the SG water levels. However, MFP "B" speed was locked-in due to the signal memory function and did not increase. An automatic reactor trip occurred due to SG 1 reaching its low-low water level trip setpoint. The Auxiliary Feedwater (AFW) System actuated, and the operators took action to throttle flow to the SGs in order to stabilize SG water levels and maintain a normal Reactor Coolant System temperature. Both MFPs were tripped, and at 0839 CST the turbine-driven AFW pump was secured. The motor-driven AFW pumps remained in service to supply normal feedwater needs with the plant in Mode 3. <br /><br /> An investigation found a faulty component on a circuit board in the MFP "A" speed control which allowed pump speed to decrease to its minimum value after an apparent power fluctuation. The circuit board with the faulty component was replaced and preventive maintenance is being instituted.
425 | 4251991006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251991006R00.pdf | 1991-02-23 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On 2-23-91, with the overpower delta-T (OPDT) and overtemperature delta-T (OTDT) bistables for reactor protection channel IV tripped for surveillance testing purposes, Reactor Coolant Loop 1 narrow range average temperature (T-avg) failed low. Personnel performing the surveillance on protection channel IV were promptly directed to back out of their procedure and restore the channel to service. However, before any action could be taken, the OPDT and OTDT bistables for protection channel I tripped, and a reactor trip occurred at 1138 CST on OTDT since the required 2 out of 4 logic was satisfied. With the exception of a steam-dump-to-condenser valve that failed open, no equipment malfunctions or abnormalities occurred following the reactor trip and by 1158 CST the plant had been stabilized in Hot Standby.<br /><br /> A subsequent review of computer data indicated that after failing low, Loop 1 T-avg returned to near normal immediately prior to the reactor trip. Utilizing the plant simulator, it was demonstrated that if the signal from the Loop 1 T-hot narrow range temperature instrument failed low slowly and then returned to normal, the channel I OPDT and OTDT bistables would trip due to the apparent sudden increase in temperature. Troubleshooting of the Loop 1 T-hot instrument channel found that a power supply on a Westinghouse 7300 Series RTD Amplifier (NRA) card had failed. <br /><br /> The NRA card was replaced and the channel IV surveillance was completed before returning the reactor to power.
425 | 4251991007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251991007R00.pdf | 1991-05-07 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On 5-7-91 at 0948 CDT, several annunciators and alarms were received on the electrical auxiliary board in the Unit 2 control room. Immediately after receipt of the alarms, an automatic reactor trip occurred due to a trip of the Unit 2 turbine. Except for the tripping of non-1E breakers which supply turbine building lighting and the malfunction of a steam-dump-to-condenser valve, no other equipment malfunctions or abnormalities occurred following the reactor trip, and by 1010 CDT the plant was stabilized in Hot Standby. <br /><br /> A post-trip review of computer data, the plant fault recorder, and the protection relay panel revealed that a generator loss of field occurred just prior to the event, causing a generator trip which then caused the turbine/reactor trip. The root cause for the generator loss of field is indeterminate. Extensive troubleshooting under the direction of a General Electric (GE) representative was performed on 5-8-91 with the generator shut down and on 5-9-91 with the generator at rated speed and voltage. No problem with the generator field excitation circuitry was found, and at 1941 CDT on 5-9-91 the generator was tied to the grid. Continuous monitoring via installed recorders was then performed with the generator online. After no abnormality was detected that might have caused the event, the recorders were removed on 5-19-91.<br /><br /> Subsequently, one recorder has been reinstalled to provide further monitoring of four points.
425 | 4251992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251992002R00.pdf | 1992-03-09 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 2 | P | WE | PO | 80 | On March 9, 1992, 125 volt dc switchgear trouble alarms began to intermittently annunciate in the control room. The control building operator (CBO) was dispatched to investigate. In the the switchgear room, the CBO looked for trouble indications but found none. While scanning the breakers, the CBO noticed that two of the circuit breakers had a yellow dot that he had not seen before. Suspecting that the dots were either stick-on tabs used for labeling or indication flags, the CBO depressed the yellow dot on breaker No. 8. The dot recessed, and the breaker switch went to the tripped position. <br /><br /> When breaker No. 8 tripped, 125 volt DC control power was lost to the electrical Train A main steam isolation valves (MSIVs), main feedwater isolation valves (MFIVs), and bypass feedwater isolation valves (BFIVs). These valves failed closed, as designed, isolating feedwater flow to and steam flow from the steam generators (SGs). Within seconds, the reactor coolant system (RCS) pressurizer pressure rose to its trip setpoint, due to the loss of a heat sink, and a reactor trip occurred. <br /><br /> The cause of this event was a cognitive personnel error by the CBO. Although the CBO had not been taught that the yellow dot was a trip test pushbutton, operator training advises personnel to request direction from supervision when unsure of how to proceed. The CBO was counseled.
425 | 4251992010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251992010R00.pdf | 1992-05-14 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 98 | On May 14, 1992, personnel were testing the main generator power system stabilizer (PSS) following the unit's return to service after a refueling outage. After completion of the testing, test personnel removed a test lead from a pin on an extender board in the regulator cubical and inadvertently touched another pin. This grounded the 15-volt dc power supply which supplies circuit board control power, disabling both the direct control and automatic control equipment. Generator excitation was lost, and a turbine trip occurred followed by a reactor trip at 1347 EDT. <br /><br /> The causes of this event include: the use of test leads that, while they are commonly used, were not adequately insulated and a personnel error on the part of a vendor technician in making an inadvertent pin contact. Insulated test leads will be utilized for future testing of this type.
425 | 4251993004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251993004R00.pdf | 1993-06-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 99 | On June 28, 1993, at 0456 EDT, Unit 2 was operating normally when a steam flow/feed flow mismatch alarm was received for steam generators (SG) 2, 3, and 4. Operators observed SG 2 feedwater flow at approximately zero, narrow range (NR) level instrumentation trending down to approximately 45 percent, and main feedwater regulating valve (MFRV) 2 closed. All main feedwater isolation valves (MFIV) and bypass feedwater isolation valves (BFIV) were verified open. With SC water level dropping at a fast rate, the unit shift supervisor (USS) directed the reactor operator (RO) to manually trip the reactor at 0457 EDT. Appropriate procedural steps were implemented to return SG levels to normal and place the unit in a stable condition.<br /><br /> Troubleshooting determined that the cause of this event was the failure of the MFRV 2 tracking/driver card. This card supplies the control signal for MFRV valve position. The card failure caused the valve demand signal to fail low, and MFRV 2 closed, resulting in reduced feed flow to SG 2. The failed circuit card was replaced and will undergo failure analysis.
425 | 4251993006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251993006R00.pdf | 1993-09-08 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Vogtle 2 | P | WE | PO | 79 | On September 8, 1993, a quality control (QC) inspector was performing fuse monitoring per an ongoing QC monitoring program. When he attempted to open the cabinet door housing the circuit breaker for the loop 4 reactor coolant pump (RCP), the inspector found that the door was stuck along the bottom edge due to paint buildup on the floor. While holding the door, the inspector used a screwdriver to pry open the door's bottom edge. When the door opened at 1739 EDT, the inspector heard a click, and in the control room operators received various annunciators, including those for a single loop low flow condition and a reactor trip due to low flow in loop 4. A normal unit trip and response ensued. <br /><br /> The cause of this event was a personnel error in prying open the cabinet door which resulted in an inadvertent actuation of a loop 4 RCP breaker relay. The relay, which is mounted on the inside of the cabinet door opened by the QC inspector, is believed to have been jarred by opening the door, initiating a trip of the loop 4 RCP breaker. Unit 2 entered a scheduled refueling outage following the reactor trip. The loop 4 RCP breaker was reset so that the RCP and steam generator could be used as a heat sink during the initial stage of the outage. Closer examination of the cabinet door and relay will be performed later in the refueling outage.
425 | 4251994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251994001R00.pdf | 1994-01-07 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On January 7, 1994, at 2253 EST, the Unit 2 reactor automatically tripped as a result of a generator/turbine trip. The initiating event for this reactor trip was the operation of a differential relay on a shunt reactor in the high voltage switchyard (HVS) which resulted in the trip of two 500 kV air blast circuit breakers (ACB), one of which is the Unit 2 main generator ACB. After operation, the two ACBs had low air pressure indications which served as a permissive in the breaker failure protective relaying scheme. This resulted in simultaneously tripping of the back-up breakers, including the remaining Unit 2 main generator ACB. The shunt reactor was removed from service pending further testing and analysis. With air pressure restored to normal levels, the breakers operated properly. The main generator ACBs were returned to service, allowing unit startup to commence. <br /><br /> The causes of this event were the operation of a differential relay on a shunt reactor and the failure of the 500 kV ACB compressed air refill pressure system switches to operate properly and maintain adequate air pressure prior to breaker tripping. This activated a breaker failure protective relaying scheme which tripped back-up breakers including the remaining Unit 2 main generator ACB and, ultimately, tripped the turbine and reactor. A loss of off-site power (LOSP) did not occur and the safety busses remained energized throughout the event.
425 | 4251994002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251994002R00.pdf | 1994-01-19 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On January 19, 1994, at 0938 EST, control room personnel received an alarm for a trip of the 'B' heater drain tank (HDT) pump. Personnel immediately initiated a power reduction and started a third condensate pump to make up for the loss of feedwater from the HDT. However, at 0940 EST, with reactor power at 98.5 percent power, a turbine/reactor trip occurred due to high water levels in the 'C' and 'D' moisture separator reheaters (MSRs). <br /><br /> The initiating cause of this event was the loss of the 'B' HDT pump, likely caused by the spurious actuation of a low level sensor. The 'B' HDT high level dump valve was out of service for maintenance, and when the HDT high level switch actuated, the normal drain valves for the 'C' and 'D' moisture separator drain tanks (MSDTs) closed, as designed. Malfunctions of the MSDTs level controllers and switches allowed overflow from the MSDTs to enter into the 'C' and 'D' MSRs where level switches initiated a turbine trip. <br /><br /> A steam leak on the upper tap of the HDT low level sensor was repaired. The 'B' HDT high level dump valve was returned to service. The MSDT level controllers were recalibrated and level switches and sensing lines were cleaned and tested to verify correct operation.
425 | 4241995002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4241995002R00.pdf | 1995-07-23 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On July 23, 1995, at 1803 EDT during a severe thunderstorm, multiple lightning strikes occurred in the immediate vicinity of the plant site with at least one direct lightning strike on the plant. Twenty-one of fifty-three reactor control rods on Unit 1 and all control rods on Unit 2 dropped into the cores. Approximately 1.5 seconds later, both reactors received a trip signal for low pressurizer pressure. The reactor trip breakers opened, dropping the remaining Unit 1 control rods. The main turbines tripped, the main feedwater systems isolated and the auxiliary feedwater systems actuated as expected. Control room personnel responded to transition the plant to stable operation in Mode 3 (hot standby). <br /><br /> The cause of this event was voltage surges in the rod control systems of both units. Voltage surges, initiated by the lightning strikes, affected low voltage circuitry in both rod control systems, causing some of the control rod drive mechanisms (CRDMs) on Unit 1 and all CRDMs on Unit 2 to lose power to stationary gripper coils. This allowed the control rods to drop into the core and both reactors immediately went subcritical. Continued steam demand from the main turbines caused temperature and pressure in the reactor coolant systems to lower until both units tripped on low pressurizer pressure. An evaluation of the rod control systems susceptibility to voltage surges (particularly those induced by lightning strikes) and proposed corrective actions are expected by October 1, 1995.
425 | 4251996006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251996006R00.pdf | 1996-10-14 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Vogtle 2 | P | WE | PO | 53 | On October 14, 1996, power ascension was in progress following a refueling outage. The steam generator (SG) #3 main feedwater regulating valve (MFRV) went from being mostly open to the 25 percent open position and SG #3 water level began to decrease. Personnel were unsuccessful in attempts to re-open the MFRV. At 1925 EDT, SG #3 level had dropped to 43 percent (narrow range) and a manual reactor trip was initiated. Isolation of the main feedwater system and actuation of the auxiliary feedwater system occurred as designed. Operators stabilized SG water levels and transitioned the unit to normal operation in Mode 3 (hot standby). <br /><br /> The cause of this event was a failure of the MFRV positioner mechanism. The positioner was replaced and the valve was returned to service.
425 | 4251996008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251996008R00.pdf | 1996-10-23 | K1 | Steam Line Break Outside Containment | [9 empty] | X | X |  |  | X | [22 empty] | X |  |  |  | X |  |  |  | X | Vogtle 2 | P | WE | PO | 64 | On October 23, 1996, at 1707 EDT, an automatic turbine/reactor trip signal was received in the control room while personnel were returning main feed pump turbine B (MFPTB) to service. The main feedwater system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Operators responded by stabilizing steam generator water levels and transitioning the unit to normal operation in Mode 3 (hot standby). <br /><br /> The cause of this event was a procedure that did not address proper steam supply valve sequencing when restoring a main feed pump turbine to service. Opening the steam supply above seat drain valves to the MFPTB, prior to opening an exhaust line, resulted in rupture of MFPTB's 15 psig rupture disk. When the drain valves were subsequently closed, outside air was inducted through the ruptured disk, past a leaking exhaust line valve, and into the condenser, where a low vacuum condition led to the turbine/reactor trip. The procedure was changed, the rupture disk replaced, and MFPTB was returned to service.
425 | 4251998003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251998003R00.pdf | 1998-05-09 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On May 8, 1998, a thunderstorm was in progress. At 0401 EDT, a lightning strike on phase A of the West MacIntosh 500 kV line resulted in damage to the phase A main step-up transformer in the low voltage switchyard. The damage to the transformer actuated a protection relay, which, in turn, tripped the main generator. This resulted in an automatic turbine/reactor trip. The main feedwater system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Control room operators acted to throttle AFW flow to the steam generators and the unit was stabilized in mode 3 (hot standby).The turbine/reactor trip was caused by a main generator trip resulting from the damage to the phase A main step-up transformer. A spare step-up transformer was placed into service and the unit was returned to power on May 14, 1998.
425 | 4251998005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251998005R01.pdf | 1998-06-09 | QP4 | Partial Loss of Condensate Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Vogtle 2 | P | WE | PO | 100 | On June 9, 1998, at 0857 EDT, the 2C condensate pump failed, the main generator tripped and a turbine/reactor trip occurred. Non-1E busses did not transfer to offsite power, leaving motor operated moisture separator reheater (MSR) steam supply valves fully opened, drawing approximately 1 million lbs/hr of steam. This, and other factors, led to a rapid reactor coolant system (RCS) cooldown and drop in pressure. Control room operators manually isolated main steamlines to limit the RCS cooldown rate. However, an automatic safety injection (SI) occurred at 0900 EDT, due to low pressurizer pressure. Operators responded properly to the SI, restored power to the appropriate non-1E busses, and stabilized the unit in mode 3 (hot standby).The direct causes of this event were an electrical fault in the surge capacitor of the 2C condensate pump motor, along with the tripping of its associated 13.8 kV bus on overcurrent. Due to improper breaker relay tap settings, the breaker tripping scheme tripped the generator output breakers to clear the fault in such a manner that transfer from onsite to offsite busses was prevented. This led to both the turbine/reactor trip and the open condition of the MSR steam supply valves. The root cause of this event was inadequate design documentation that resulted in personnel incorrectly setting the relay taps. This is believed to have occurred during original plant startup. Relay tap settings for the breaker relays were corrected. The 2C condensate pump was removed from service for repairs and the unit was returned to power.
425 | 4251998007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251998007R01.pdf | 1998-08-24 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On August 24, 1998, at 1731 EDT, an inverter failure led operators to transfer 120-volt instrument panel 2NY1N to its alternate power supply. After the transfer, operators noticed that the 26-volt primary power supply to process control rack #3 had not re-energized and the control rack was operating off its 24-volt backup power supply. The operators prepared to initiate troubleshooting. At 1823 EDT, the backup power supply to control rack #3 failed. Several control loops lost power and the steam generator (SG) #3 main feedwater regulating valve, 2FV-530, closed. Operators observed water level decreasing in SG #3 and manually tripped the reactor. Other than minor discrepancies, a normal reactor trip evolution and recovery ensued.Loss of feed water flow to SG #3 was caused by consecutive failures of primary and backup power supplies to process control rack #3. The manual reactor trip was performed in anticipation of low water level in SG #3. SG low water level is a condition for automatic reactor trip. The inverter was repaired and both process control rack #3 power supplies were replaced. A design change is in progress to install a new type of power supply in the process control and protection cabinets in both units over the next two years.
425 | 4251998008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251998008R00.pdf | 1998-09-04 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Vogtle 2 | P | WE | PO | 100 | On September 4, 1998, the balance of plant operator (BOP) was performing solid state protection system (SSPS) slave relay testing. At 0024 EDT, both main feedwater pumps tripped. As steam generator (SG) water levels decreased toward their low level setpoints, the reactor operator (RO) performed a manual reactor trip. The main feedwater system isolated and auxiliary feedwater actuated, as designed. Control room personnel acted appropriately to stabilize the unit in Mode 3 (hot standby).The causes of this event were: 1) the test circuit contains an inherent design weakness. Simultaneously depressing multiple test lamps allowed additive currents to actuate the relay that trips both main feedwater pumps; 2) the BOP exhibited a poor practice in simultaneously depressing more than one test lamp; and, 3) the test procedure did not contain a caution against simultaneously depressing more than one test lamp. A modification will change the test circuit to prevent feedwater pump tripping due to simultaneous lamp testing. A shift briefing item was initiated to advise operators of this event and the need to avoid simultaneous depressing of the test lamps when conducting this testing. Test procedures have been revised to include a precaution against simultaneous lamp testing.
425 | 4251999001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4251999001R00.pdf | 1999-03-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On March 2, 1999, two plant equipment operators (PEOs) were given a clearance package to install Unit 1 clearances in support of the ongoing Unit 1 refueling outage. The PEOs went to the control room and witnessed the reactor operator place the required tags on the handswitches. Next, they went to level A of the control building and pulled fuses in Unit 1 panels. Finally, they proceeded to level 2, intending to enter into the cable spreading room above the Unit 1 control room. However, they instead went into the adjacent cable spreading room above the Unit 2 control room. The clearance required main feedwater isolation valve (MFIV) fuses to be pulled from cabinet 1BCPT20. The PEOs located the identical Unit 2 panel, 2BCPT20, and pulled the loop 3 MFIV fuses, allowing the MFIV to close. In the Unit 2 control room, personnel received steam/feed flow mismatch alarms and noticed steam generator (SG) level decreasing with low feed flow. Due to the loss of feedwater flow to SG #3, the unit shift supervisor (USS) ordered a manual reactor trip, which occurred at 0206 EST. A normal trip response occurred with the unit stabilizing in Mode 3 (hot standby).The direct cause of the reactor trip was personnel erroneously pulling the MFIV control power fuses in the wrong unit. The root cause of the error is attributed to inappropriate work practices. Various corrective actions addressing human performance are being implemented.
425 | 4252001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252001001R00.pdf | 2001-04-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Vogtle 2 | P | WE | PO | 46 | On April 7, 2001, Unit 2 was reducing power, preparing to enter a refueling outage. While steam generator (SG) feedwater pump A was out of service, personnel were testing the SG feedwater pump turbine (SGFPT) A trip signal. However, upon simulating a SG high water level signal, a trip of SGFPT B occurred. This resulted in both SGFPTs being out of service. Therefore, control room operators performed a manual reactor trip at 2123 EDT. A normal trip sequence ensued and plant operators transitioned the unit to stable operation in Mode 3 (hot standby).An investigation of this event found that, prior to the SGFPT B trip, I&C technicians had opened a sliding link to disable the feed pump trip signal. A review determined that the sliding link had not been fully opened, thereby leading to the SGFPT B trip when a simulated high water level signal was processed. The root cause of the event was the man-machine interface that prohibited the technicians from visually determining the link position. The link position could only be determined by feel using a nut driver. Corrective actions include performing an engineering review to determine if the link should be moved to a more accessible location in the cabinet. Additionally, until completion of this review, this surveillance will only be performed when the SGFPTs are out of service.
425 | 4252002002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252002002R00.pdf | 2002-11-13 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Vogtle 2 | P | WE | PO | 21 | On November 13, 2002, power ascension was in progress following a refueling outage. At approximately 0354 EST, the licensed operator designated as the steam generator water level control operator (SGWLCO) began to transfer steam generator feedwater control from the bypass feedwater regulating valves (BFRVs) to the main feedwater system regulating valves (MFRVs). A series of water level transients commenced in each of the four steam generators (SGs) that culminated in the SG #3 water level increasing to its Hi-Hi level setpoint at 0405 EST. The main feedwater system isolated, the main feedwater pump tripped, and the auxiliary feedwater system actuated, as designed. As SG water levels decreased to their low level setpoints, a manual reactor trip was initiated at 0405 EST, and SG water levels were stabilized in Mode 3 (hot standby).The root cause of this event was the failure of the SGWLCO to follow procedure by having all BFRVs and MFRVs open simultaneously. A secondary cause of this event was less than adequate supervisory oversight by the Unit Shift Supervisor in verifying procedure compliance during feedwater control operations. The policy for implementing unit operating procedures is being reviewed to determine if the level of flexibility and/or interpretation is appropriate. Expectations of command and control issues are also being evaluated.
425 | 4252004004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252004004R01.pdf | 2004-11-20 | QR8 | Spurious Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On November 20, 2004, `B' Train Solid State Protection System Testing was in progress with the `B'Train in the "inhibit mode" for testing. Operators performing the test erroneously operated the `A'Train Solid State Protection multiplexer test switch which disabled `A' Train SSPS completing thelogic for an automatic reactor trip at 1140 EST. Subsequent to the trip, the Loop 2 Tavg instrumentchannel failed at its full power value causing a full-open steam dump demand. Control roompersonnel responded to the decreasing reactor coolant system (RCS) temperature by initiating a MainSteamline Isolation, but the pressure drop was sufficient to result in an automatic Safety Injection (SI)actuation. As designed, the SI signal initiated a Control Room Isolation, a Containment VentilationIsolation, start of both Emergency Diesel Generators and a Phase A Containment Isolation . AfterRCS pressure recovered, control room personnel secured Safety Injection and transitioned the unit tonormal operation in Mode 3 (Hot Standby).The cause of the reactor trip was human error in that the operator erroneously manipulated a test switchon the `A' Train SSPS. The cause of the SI was the failure of a lead-lag circuit card that lead to thefailure of the Loop 2 Tavg circuitry and subsequent full opening of the steam dump valves and RCSpressure drop. A number of actions were implemented to address the human performance errors and thefailed lead-lag card was replaced and tested satisfactorily.
425 | 4252006003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252006003R00.pdf | 2006-08-27 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On August 27, 2006, at 0631 EDT, Unit 2 experienced an automatic reactor trip from 100% power. The Loop 4 Reactor Coolant Pump (RCP) tripped and the Reactor Protection System (RPS) actuated on "Reactor Coolant System Low Flow." The post-trip investigation revealed that, inside the RCP motor junction box, a degraded current transformer (CT) wire was in contact with a degraded surge arrestor cable shield. The degraded CT wire was grounded in the CT wiring junction box, creating a ground path that resulted in a fault in the RCP #4 motor junction box that caused the pump to trip.Investigation determined that the cause of this event was an inadequate design change package. Contributing causes were inadequate procedures, work instructions, and installation practices. Prior to restart, the Loop 4 RCP junction box CT wiring and CTs were replaced as well as the surge arrestor wiring and the differential protective relay in the feeder breaker cubicle for RCP #4.
425 | 4252007002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252007002R00.pdf | 2007-04-23 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 54 | On April 23,2007, at 1024 EDT, Unit 2 experienced an automatic reactor trip from approximately 54% powerduring power ascension following completion of refueling outage 2R12. The main generator neutral overcurrentrelay actuated resulting in a Generator/Turbine/Reactor trip. The post-trip investigation revealed that a groundfault had occurred on the main generator 'A' phase bushing. The bushing fault was a result of stator waterleaking out of the tang area of the main generator 'A' phase bushing and saturating the bushing insulation. The wet insulation provided the ground fault path that caused the main generator neutral overcurrent relay to actuate.Investigation determined that the primary cause of this event was the design of the main generator bushing tangassembly due to it being a cast copper component utilizing a braze material that is susceptible to crevicecorrosion. Prior to restart, the leak was repaired in the main generator 'A' phase bushing tang assembly, ahelium tracer gas test was performed on all three main generator tang assemblies, and the Generator Gas Systemoperating procedure was revised to ensure main generator hydrogen pressure is maintained at a higher pressurethan stator water.
425 | 4252009001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252009001R00.pdf | 2009-12-23 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Vogtle 2 | P | WE | PO | 100 | On December 23, 2009 at approximately 15:25 hours Eastern Standard Time (EST), Vogtle Electric Generating Plant (VEGP), Unit 2 was manually tripped from 100% power due to a loss of instrument air to the turbine building. Instrument air low pressure alarms were received in the control room and secondary side valves responded to the loss of instrument air. Due to the loss of air pressure, several secondary side valves positioned to their fail safe position. This ultimately led to a decrease in suction pressure to one of the main feedwater pumps causing the main feedwater pump to trip on low suction pressure. In anticipation of loss of feedwater flow to the steam generators, the control room operators manually tripped the reactor in accordance with the Abnormal Operating Procedure (AOP) for a main feedwater malfunction. All control rods fully inserted and the motor driven auxiliary feedwater pumps automatically started on low steam generator water level in one of the steam generators in accordance with plant design. All of the control rods fully inserted and the plant was stabilized in Mode 3.
425 | 4252013001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252013001R00.pdf | 2013-02-26 | QR6 | Manual Reactor Trip | [45 empty] | Vogtle 2 | P | WE | PO | 94 | On February 26, 2013, at approximately 2302 Eastern Daylight Time (EDT) time, with Unit 2 operating in Mode 1 at 94 percent rated thermal power and End of Life (EOL) Coastdown in progress, Unit 2 operators initiated a manual reactor trip due to Reactor Coolant Pump (RCP) #4 number one seal leakoff flow exceeding the operating limits. The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the event was the addition of air into the Chemical Volume Control System (CVCS) charging system as a result of less than adequate filling and venting of the Reactor Coolant System filter.<br><br> The safety significance of this event is low. Unit 1 was unaffected and there were no adverse effects on the health and safety of the public.
425 | 4252013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252013002R00.pdf | 2013-10-19 | QR5 | Turbine Trip | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On October 19, 2013 at approximately 0645 Eastern Daylight Time (EDT), Vogtle Unit 2 was operating in Mode 1 at 100% power. The main generator excitation system experienced a failure which tripped the Main Generator which subsequently tripped the Turbine and Reactor. The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the event was a failure of the Main Generator excitation system. <br /><br /> The safety significance of this event is very low. Unit 1 was not affected and there were no adverse effects of the health and safety of the public.
425 | 4252013003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252013003R00.pdf | 2013-10-22 | QL7 | Degraded condenser vacuum | [45 empty] | Vogtle 2 | P | WE | PO | 100 | Unit 2 Reactor was manually tripped at 11:44 on 10-22-13 due to lowering condenser vacuum. The Unit was undergoing power ascension in Mode 1 at 25 percent power. At the time of the reactor trip, maintenance was in progress on Main Feedwater Pump (MFP) B. Prior to work commencing the possibility of impacting condenser vacuum due to maintenance activities was discussed and operational limits were established. After the MFP B pump steam chest lift was initiated, condenser vacuum began lowering and maintenance was directed to lower the MFP B steam chest. Condenser vacuum approached the predetermined operational limit of 23 inches of mercury vacuum and the Shift Supervisor directed a manual reactor trip of the Unit 2 reactor. Unit 2 was stabilized in Mode 3 on Auxiliary Feedwater with the Main Condenser available for decay heat removal. All systems responded as expected. The primary cause of the event was air in leakage past the MFP B turbine exhaust valve to the Main Condenser. <br /><br /> The safety significance of this incident is very low and there were no adverse effects on the health and safety of the public.
425 | 4252014001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252014001R00.pdf | 2014-04-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On April 8, 2014 at approximately 04:30 Eastern Standard Time, Vogtle Unit 2 was operating at Mode 1 at 100 percent power when Unit 2 received a Steam Generator 3 narrow range low-low level automatic Reactor Protection System actuation as a result of the Loop 3 Main Feedwater Regulating Valve failing closed. The RPS actuation resulted in a trip of the turbine-generator. All rods fully inserted into the core, the Main Feedwater Isolation system and the Auxiliary Feedwater system automatically actuated as expected. The plant was stabilized in Mode 3 and the decay heat was discharged to the condenser. The cause of the event was a failure of the Steam Generator 3 Main Feed Regulator Valve control system.<br /><br /> The safety significance of the event is very low. Unit 1 was not affected and there were no adverse effects on the health and safety of the public.
425 | 4252014003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252014003R00.pdf | 2014-10-12 | QR6 | Manual Reactor Trip | [45 empty] | Vogtle 2 | P | WE | SU | 1 | On October 12, 2014 at approximately 0944 EST, while performing Unit 2 reactor startup, control rods were being inserted to stabilize Rx power for Low Power Physics Testing. With the rod bank selector switch in Manual, operators observed control bank A inserting instead of the expected D bank inserting. Operators took action to trip the reactor and stabilize the plant. The cause of this event was incorrect setup of the Rod Bank Overlap unit.<br /><br /> Upon tripping the reactor, plant systems responded per design and Unit 2 was stabilized in Mode 3. Unit 1 was not affected and there were no adverse effects on the health and safety to the public. Therefore, the safety significance of this event is very low.
425 | 4252015001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252015001R00.pdf | 2015-03-14 | QL5 | Partial Closure of MSIVs | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On March 14, 2015 at approximately 04:29 AM Eastern Daylight Time (EDT), Vogtle Unit 2 was operating in Mode 1 at 100 percent power when the Loop 3 outboard Main Steam Isolation Valve (MSIV) spuriously closed. The sudden closure of the steam isolation valve caused a rapid pressure reduction in the remaining three Steam Generators (SGs) due to increased steam flow resulting in a Reactor Protection System (RPS) actuation due to rate compensated Low Main Steam Line Pressure Safety Injection and Steam Line Isolation. All control rods fully inserted and all equipment actuated as designed.<br /><br /> The unit was stabilized in Mode 3 with decay heat being removed through the atmospheric relief valves (ARVs) to the environment. The Loop 3 MSIV closure was due to failure of the hydraulic dump solenoid valve which resulted in a loss of hydraulic pressure to the MSIV.<br /><br /> This event had no adverse effect on the health and safety of the public, and is of very low safety significance. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of a system listed in 10CFR 50.73(a)(2)(iv)(B). Unit 1 was unaffected.
425 | 4252016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4252016002R00.pdf | 2016-05-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Vogtle 2 | P | WE | PO | 100 | On May 25, 2016 at approximately 0206 Eastern Daylight Time, the Unit 2 was operating in Mode 1 and 100 percent power when the reactor tripped due to low-low level in Steam Generator 1. All control rods fully inserted into the core and all safety systems actuated as designed.<br /><br /> The unit was stabilized in Mode 3 with decay heat being removed through the main steam lines to the steam dumps and to the condenser. The low-low level in Steam Generator 1 was due to a human performance error by technicians performing a loop calibration on the Steam Generator 1 level instrumentation. This error resulted in a perceived high level into the Steam Generator Water Level Control system. In response, the Feedwater regulating valve closed which lowered actual level in Steam Generator 1. <br /><br /> Because all control rods fully inserted into the core and all the safety systems actuated as designed, this event had no adverse effect on the health and safety of the public, and is of very low safety significance. This event is reportable per 10 CFR 73(a)(2)(iv)(A), due to the actuation of a system listed in 10CFR 50.73(a)(2)(iv)(B).
440 | 4401987007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987007R00.pdf | 1987-02-13 | QR8 | Spurious Reactor Trip | [45 empty] | Perry | B | GE | PO | 6 | POWER LEVEL - 006%. ON 2/13/87 AT 2238, A PRESSURE TRANSIENT WITHIN A REACTOR VESSEL (RPV) LEVEL INSTRUMENT RACK RESULTED IN A DIVISION 2 REDUNDANT REACTIVITY CONTROL SYSTEM (RRCS) ALTERNATE ROD INSERTION (ARI). THE CAUSE OF THIS EVENT IS ATTRIBUTED TO THE DESIGN CONFIGURATION OF THE RRCS LEVEL INSTRUMENTS. BOTH CHANNELS OF THE RRCS LEVEL INSTRUMENTS FOR EACH DIVISION OF RRCS ARE LOCATED ON A COMMON REFERENCE LEG. EITHER DIVISION IS CAPABLE OF INITIATING THE RRCS PROTECTIVE ACTIONS. THE OPENING OF THE LOW SIDE INSTRUMENT ISOLATION VALVE CAUSED A PRESSURE TRANSIENT RESULTING IN AN INDICATED LEVEL DECREASE BELOW LEVEL 2. THE INDICATED DECREASE BELOW LEVEL 2 CAUSED AN ACTUATION OF BOTH CHANNELS OF DIVISION 2 OF RRCS RESULTING IN A RRCS ARI AND TRIP OF THE REACTOR RECIRCULATION PUMPS. AS A RESULT OF A PREVIOUS EVENT, AN ENGINEERING DESIGN CHANGE WAS INITIATED TO RELOCATE THE DIVISIONAL RRCS LEVEL TRANSMITTERS TO SEPARATE INSTRUMENT REFERENCE LEGS. THIS CHANGE IS CURRENTLY UNDER EVALUATION AND DEVELOPMENT. AS A RESULT OF THIS EVENT, THE INSTRUMENT AND CONTROL SECTION WILL ADMINISTRATIVELY CONTROL CONDITIONS UNDER WHICH THE CALIBRATION OF INSTRUMENTS ON THE AFFECTED INSTRUMENT RACKS MAY BE PERFORMED. INTERIM CONTROLS WILL ENSURE THAT ROUTINE CALIBRATIONS WILL NOT BE PERFORMED WHILE THE REACTOR IS IN OPERATION.
440 | 4401987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987012R00.pdf | 1987-03-02 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Perry | B | GE | PO | 28 | POWER LEVEL - 028%. ON MARCH 2, 1987 AT 0319, A REACTOR SCRAM OCCURRED DUE TO A REACTOR VESSEL WATER LEVEL OF LESS THAN LEVEL 3 (+177.7 INCHES ABOVE TOP OF ACTIVE FUEL). IN ADDITION, A NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM BALANCE OF PLANT ISOLATION AND A REACTOR WATER CLEANUP ISOLATION OCCURRED DUE TO A REACTOR VESSEL WATER LEVEL OF LESS THAN LEVEL 2. THE CAUSE OF THIS EVENT WAS PERSONNEL ERROR. WHILE ATTEMPTING TO FREE STUCK LEVEL SWITCH 1N21-N337, OPERATIONS PERSONNEL INADVERTENTLY ACTUATED THE HOT SURGE TANK LO LO LEVEL SWITCH 1N21-N335, RESULTING IN A LOSS OF FEEDWATER TO THE REACTOR VESSEL. CORRECTIVE ACTIONS TO PREVENT RECURRENCE INCLUDE DISCIPLINARY ACTION FOR THE PERSONNEL INVOLVED IN THIS EVENT AND A REVISION TO THE STANDING INSTRUCTION ON OPERATIONS SECTION COMMUNICATION. IN ADDITION, AN ENGINEERING DESIGN CHANGE WILL BE IMPLEMENTED TO REVISE THE REACTOR FEEDWATER BOOSTER PUMP TRIP LOGIC. SUBMITTAL OF THIS REPORT ALSO MEETS THE REQUIREMENTS FOR TECHNICAL SPECIFICATION 3.5.1, ACTION G, SPECIAL REPORT FOR EMERGENCY CORE COOLING SYSTEM ACTUATION AND INJECTION INTO THE REACTOR COOLANT SYSTEM.
440 | 4401987027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987027R01.pdf | 1987-04-13 | K1 | Steam Line Break Outside Containment | [9 empty] | X | X | [25 empty] | X |  |  |  | X |  |  |  |  | Perry | B | GE | SU | 3 | POWER LEVEL - 003%. ON APRIL 13, 1987 AT 1817, A MANUAL FAST REACTOR SHUTDOWN WAS CONDUCTED DUE TO A LOSS OF CONDENSER VACUUM AND REPORT OF A STEAM LEAK IN THE TURBINE BUILDING. CONTROL ROOM OPERATORS ALSO NOTED CONDENSER OFF-GAS FLOWRATE WAS OFFSCALE HIGH. OPERATORS WERE DISPATCHED TO THE TURBINE BUILDING TO INVESTIGATE THE CAUSE OF THE CONDENSER VACUUM LOSS. THE LOSS OF CONDENSER VACUUM WAS DUE TO A HOLE IN A 24 INCH MAIN STEAM DRAIN MANIFOLD WHICH FEEDS THE HIGH PRESSURE CONDENSER. THE MANIFOLD FRACTURED AT THE TOE OF THE WELD AT THE JUNCTION OF A 3 INCH MAIN TURBINE STOP VALVE DRAIN LINE HEADER. THE STEAM LEAK WAS FROM THE DRAIN LINE HEADER WHICH HAD DISLODGED FROM THE MANIFOLD. THE CAUSE OF THE BREAK IS BELIEVED TO BE HIGH FREQUENCY VIBRATION DUE TO EXTENSIVE STEAM FLASHING AND WATER PARTICLE IMPINGEMENT IN THE DRAIN LINE HEADER. TO PREVENT RECURRENCE THE HIGH PRESSURE DRAIN MANIFOLD HAS BEEN REPLACED AND ADDITIONAL PIPE RESTRAINTS ADDED TO THE MANIFOLD AND DRAIN LINES. THE 3 INCH MAIN TURBINE STOP VALVE BEFORE SEAT DRAIN HEADER WAS REPLACED WITH A 6 INCH LINE DOWNSTREAM OF A THROTTLE VALVE TO ASSURE LOW VELOCITY STEAM FLOW INTO THE MANIFOLD. ADDITIONALLY, AN EXISTING 6 INCH DRAIN LINE WAS RECONFIGURED 180 DEGREES ON THE MANIFOLD TO MORE EVENLY DISTRIBUTE DRAIN LINE FLOW FORCES.
440 | 4401987030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987030R00.pdf | 1987-05-01 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 50 | POWER LEVEL - 050%. ON MAY 1, 1987 AT 1737, A REACTOR PROTECTION SYSTEM MANUAL REACTOR SCRAM WAS INITIATED BY CONTROL ROOM OPERATORS DUE TO A LOSS OF REACTOR FEEDWATER (FW). THE CAUSE OF THIS EVENT WAS A FAILURE OF THE AIR LINES FOR CONDENSATE FLOW CONTROL VALVE 1N21-F230. VIBRATION OF THE CONDENSATE PIPING AND VALVE CAUSED THE AIR LINES TO FAIL. LOSS OF CONTROL FOR VALVE 1N21-F230 RESULTED IN A DECREASE OF HOT SURGE TANK (HST) LEVEL AND SUBSEQUENT TRIP OF THE OPERATING REACTOR FEEDWATER BOOSTER PUMPS (RFBP) AND BOTH TURBINE DRIVEN REACTOR FEEDWATER PUMPS. IN ADDITION, A FEEDWATER WATER HAMMER OCCURRED WHEN THE RFBPS AUTOSTARTED WHEN HST LEVEL RECOVERED AFTER THE REACTOR SCRAM. ENGINEERING DESIGN CHANGES WILL BE IMPLEMENTED TO; INSTALL FLEXIBLE METAL AIR LINES ON 1N21-F230, ADD A SECOND CONDENSATE CONTROL VALVE IN PARALLEL WITH 1N21-F230, INSTALL ADDITIONAL PIPE SUPPORTS/GUIDES TO REDUCE VIBRATION, PROVIDE A SEAL-IN FOR THE RFBP TRIP ON L0 L0 HST LEVEL, AND REVISE THE TRIP LOGIC FOR THE MOTOR DRIVEN FEEDWATER PUMP TO PROVIDE A PUMP TRIP ON LOW NPSH.
440 | 4401987035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987035R00.pdf | 1987-05-24 | QL6 | Condenser Leakage | [45 empty] | Perry | B | GE | PO | 55 | POWER LEVEL - 055%. ON MAY 24, 1987 AT 0304, A REACTOR PROTECTION SYSTEM (RPS) MANUAL REACTOR SCRAM WAS INITIATED BY CONTROL ROOM OPERATORS IN RESPONSE TO A LEAK IN THE CONDENSATE SYSTEM. SINCE THE CONDENSATE LEAK COULD NOT BE ISOLATED WITH THE CONDENSATE SYSTEM IN SERVICE, THE OPERATIONS SECTION SHIFT SUPERVISOR ORDERED A REACTOR SHUTDOWN. INVESTIGATION FOLLOWING THE SCRAM REVEALED THAT THE CONDENSATE LEAK WAS ORIGINATING FROM THE 1N21-F701B VALVE (1N21-F230 UPSTREAM PIPING DRAIN). THE 1N21-F701B VALVE AND DRAIN LINE HAD SEVERED FROM THE CONDENSATE PIPING. THE CAUSE OF THIS EVENT WAS EXCESSIVE VIBRATION OF THE CONDENSATE SYSTEM RESULTING IN THE FAILURE OF THE PIPING FOR THE 1N21-F701B DRAIN VALVE. AN ENGINEERING DESIGN CHANGE HAD BEEN INITIATED DUE TO A PREVIOUS EVENT (SEE LER 87-030) TO ADD A SECOND CONDENSATE CONTROL VALVE IN PARALLEL WITH 1N21-F230 AND ADD ADDITIONAL PIPE SUPPORTS/GUIDES TO REDUCE THE VIBRATION EXPERIENCED IN THE VICINITY OF THE 1N21-F230 VALVE. THIS DESIGN CHANGE IS UNDER DEVELOPMENT TO BE IMPLEMENTED IN AN UPCOMING OUTAGE. AN EVALUATION OF VIBRATION EFFECTS ON CONDENSATE AND FEEDWATER SYSTEM VENT AND DRAIN VALVES WILL ALSO BE PERFORMED TO DETERMINE FURTHER CORRECTIVE ACTIONS. IN ADDITION, AN ENGINEERING DESIGN CHANGE IS BEING STUDIED TO REDUCE THE PRESSURE IN THE SYSTEM PIPING.
440 | 4401987037 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987037R00.pdf | 1987-05-27 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 58 | POWER LEVEL - 058%. ON MAY 27, 1987, AT 0547, A REACTOR SCRAM OCCURRED DUE TO A REACTOR VESSEL WATER LEVEL OF LESS THAN LEVEL 3 (+177.7 INCHES ABOVE TOP OF ACTIVE FUEL (TAF)). IN RESPONSE TO THE REACTOR SCRAM, PLANT OPERATORS ENTERED OFF-NORMAL INSTRUCTION (ONI-C71), 'REACTOR SCRAM (UNIT 1),' PLACED THE MODE SWITCH IN SHUTDOWN, AND TRIPPED THE MAIN TURBINE. REACTOR WATER LEVEL WAS RESTORED USING THE B TURBINE DRIVEN FEEDWATER PUMP (TDFP) IN MANUAL. THE MINIMUM REACTOR VESSEL WATER LEVEL REACHED DURING THIS EVENT WAS +157 INCHES ABOVE TAF. TROUBLESHOOTING SUBSEQUENT TO THE SCRAM LOCATED A FAILED RESISTOR INTERNAL TO THE CONTROL CIRCUIT OF THE MOTOR DRIVEN FEEDWATER PUMP (MFP) WHICH RESULTED IN ITS FLOW CONTROL VALVES GOING CLOSED, AT 0546:58. WITH THESE VALVES SHUT, THE MFP STOPPED SUPPLYING WATER TO THE REACTOR VESSEL. WITH ONLY THE B TDFP SUPPLYING WATER TO THE REACTOR VESSEL, A STEAM FLOW/FEEDWATER FLOW MISMATCH DEVELOPED THAT RESULTED IN WATER LEVEL DECREASING AND CAUSING THE REACTOR SCRAM. THE CARD CONTAINING THIS RESISTOR WAS REPLACED, THE CONTROL CIRCUIT WAS CALIBRATED WITH THE NEW CARD IN PLACE AND THE MFP CONTROLLER WAS RETURNED TO SERVICE. ONCE THIS REPAIR WAS PERFORMED, THE TRANSIENT ANALYSIS WAS COMPLETED AND APPROVAL TO RESTART WAS GRANTED BY THE PLANT MANAGER. THE PLANT WAS RESTARTED AT 1454.
440 | 4401987042 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987042R00.pdf | 1987-06-17 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Perry | B | GE | PO | 23 | POWER LEVEL - 023%. ON JUNE 17, 1987 AT 1139, A REACTOR PROTECTION SYSTEM (RPS) ELECTRICAL PROTECTION ASSEMBLY (EPA) BREAKER TRIPPED, RESULTING IN DEENERGIZATION OF RPS BUS A AND CLOSURE OF THE OUTBOARD MAIN STEAM ISOLATION VALVES (MSIV). CLOSURE OF THE MSIVS RESULTED IN A REACTOR SCRAM. LOSS OF THE RPS BUS ALSO RESULTED IN A NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM (NSSSS) ISOLATION SIGNAL AND CLOSURE OF THE ASSOCIATED CONTAINMENT ISOLATION VALVES. THE ROOT CAUSE OF THE CONTAINMENT ISOLATION WAS A FAILED COMPONENT OF AN EPA LOGIC CARD WHICH PRODUCED SPURIOUS OUTPUT VOLTAGE PULSES AND RESULTANT TRIPPING OF THE EPA BREAKER. THE CAUSE OF THE MSIV CLOSURE AND RESULTANT SCRAM WAS THE DESIGN OF THE POWER SUPPLIES TO THE MSIV PILOT VALVE SOLENOIDS. BOTH OF THE THE SOLENOIDS FOR EACH OUTBOARD MSIV WERE POWERED FROM THE SAME RPS BUS, THEREFORE, MSIV CLOSURE RESULTED WHEN NORMAL RPS POWER WAS LOST TO BOTH SOLENOIDS. THE LOGIC CARDS FOR THE RPS BUS A EPAS WERE REPLACED, CHANGES WERE MADE TO THE APPROPRIATE PLANT OPERATING INSTRUCTIONS, AND SURVEILLANCE TESTING OF THE NORMAL RPS POWER SUPPLY OUTPUT BREAKERS WAS COMPLETED ON JUNE 20. THE EPA CARDS FOR THE NORMAL RPS B POWER SUPPLY WERE REPLACED AND THE POWER SUPPLY CONFIGURATION TO THE INBOARD AND OUTBOARD MSIV SOLENOIDS WAS MODIFIED DURING THE CURRENT PLANT OUTAGE.
440 | 4401987045 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987045R00.pdf | 1987-06-30 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 28 | POWER LEVEL - 028%. ON JUNE 30, 1987 AT 1030, A MANUAL REACTOR SCRAM WAS CONDUCTED DUE TO A GENERATOR BUSHING FAILURE AND RESULTANT INCREASED HYDROGEN CONCENTRATION IN THE GENERATOR NEUTRAL BUSHING COMPARTMENT. INVESTIGATION DETERMINED THAT THE B PHASE EAST END GENERATOR NEUTRAL BUSHING HAD OVERHEATED DUE TO OIL PARTIALLY FILLING THE COOLING GAS DUCT AND PREVENTING THE PROPER COOLING. THE B PHASE WEST END NEUTRAL BUSHING WAS ALSO FOUND TO HAVE OIL INSIDE OF THE COOLING DUCT. THE OIL IS BELIEVED TO HAVE BEEN LEFT FROM A JUNE, 1986 EVENT WHERE A VENT VALVE ON THE GENERATOR SEAL OIL DRAIN FLOAT TRAP WAS IMPROPERLY POSITIONED. THE BUSHING COOLING DUCTS WERE NOT ADEQUATELY INSPECTED FOR OIL BLOCKAGE DURING THE CLEANUP ACTIVITIES FOLLOWING THIS EVENT. ALL 12 OF THE GENERATOR BUSHINGS HAVE BEEN INSPECTED FOR OIL BLOCKAGE. BOTH THE B PHASE EAST AND WEST END NEUTRAL BUSHINGS HAVE BEEN COMPLETELY REPLACED. THE INDIVIDUALS INVOLVED WITH THE INSPECTION ACTIVITIES HAVE BEEN MADE AWARE OF THE CONSEQUENCES OF THIS EVENT AND ARE NOW WELL AWARE OF THE PROPER METHODS TO INSPECT THE GENERATOR BUSHINGS. ADDITIONALLY, A REPETITIVE TASK HAS BEEN DEVELOPED TO PERIODICALLY INSPECT THE BUSHINGS FOR COOLANT PATH BLOCKAGE AND TO PROVIDE THE NECESSARY METHODOLOGY TO PERFORM A THOROUGH INSPECTION DURING FUTURE RETEST OR CLEANUP ACTIVITIES.
440 | 4401987064 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987064R00.pdf | 1987-09-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Perry | B | GE | PO | 63 | POWER LEVEL - 063%. ON SEPTEMBER 9, 1987 AT 2033 A REACTOR SCRAM OCCURRED DUE TO HIGH REACTOR WATER LEVEL (LEVEL 8, + 219.5 INCHES ABOVE TOP OF ACTIVE FUEL) CAUSED BY A SUDDEN CHANGE IN THE FEEDWATER FLOW CONTROL SIGNAL AND THE TURBINE DRIVEN FEEDWATER PUMPS (TDFP) RAMPING TO FULL SPEED. THE HIGH REACTOR WATER LEVEL ALSO CAUSED THE MAIN TURBINE AND THE FEEDWATER PUMPS TO TRIP. REACTOR WATER LEVEL THEN DROPPED TO LEVEL 2 (+ 129.8 INCHES ABOVE TOP OF ACTIVE FUEL) CAUSING THE HIGH PRESSURE CORE SPRAY (HPCS) AND REACTOR CORE ISOLATION COOLING SYSTEMS TO START AND INJECT TO THE REACTOR VESSEL. AN UNUSUAL EVENT WAS DECLARED DUE TO THE AUTOMATIC ACTUATION OF HPCS. THE CAUSE OF THE EVENT WAS A PROCEDURAL DEFICIENCY. A PERIODIC TEST INSTRUCTION (PTI), WHICH STROKES THE LOW PRESSURE STOP VALVES FOR THE TDFP, DID NOT ISOLATE A TURBINE TRIP SIGNAL FROM THE FEEDWATER CONTROL SYSTEM. ADDITIONALLY, THE LIMIT SWITCH USED FOR THE TRIP SIGNAL PROVIDED A FALSE TURBINE TRIP SIGNAL. THE PTI HAS BEEN REVISED TO ENSURE A TURBINE TRIP SIGNAL WILL NOT CAUSE A FLOW CONTROL SIGNAL CHANGE DURING THE TEST. A DESIGN CHANGE IS BEING DEVELOPED TO PREVENT A FALSE TURBINE TRIP SIGNAL. ADDITIONALLY, ALL PTI'S WHICH HAVE NOT BEEN PREVIOUSLY PERFORMED WILL BE REVIEWED PRIOR TO PERFORMANCE.
440 | 4401987072 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987072R00.pdf | 1987-10-27 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Perry | B | GE | PO | 51 | POWER LEVEL - 051%. ON OCTOBER 27, 1987 AT 0637, FOLLOWING AN IMPROPER TRANSFER OF STATION LOADS, A REACTOR SCRAM OCCURRED DUE TO A REACTOR WATER LEVEL OF LESS THAN LEVEL 3 (+177.7 INCHES ABOVE TOP OF ACTIVE FUEL (TAF)). IN ADDITION, NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM ISOLATIONS, AS WELL AS HIGH PRESSURE CORE SPRAY AND REACTOR CORE ISOLATION COOLING SYSTEM INITIATIONS OCCURRED DUE TO A REACTOR VESSEL LEVEL OF LESS THAN LEVEL 2 (+129.8 INCHES ABOVE TAF). THE CAUSE OF THE EVENT WAS PERSONNEL ERROR. WHEN TRANSFERRING STATION LOADS FROM THE STARTUP TRANSFORMER TO THE AUXILIARY TRANSFORMER, A CONTROL ROOM OPERATOR INADVERTENTLY DE-ENERGIZED THE HOT SURGE TANK LOW LEVEL TRIP LOGIC, RESULTING IN A LOSS OF FEEDWATER TO THE REACTOR VESSEL. CORRECTIVE ACTIONS TO PREVENT RECURRENCE INCLUDE DISCIPLINARY ACTION FOR THE OPERATOR INVOLVED IN THIS EVENT AND IMPLEMENTATION OF AN ENGINEERING DESIGN CHANGE TO INCREASE THE RELIABILITY OF HOT SURGE TANK LOW LEVEL TRIP LOGIC. SUBMITTAL OF THIS REPORT ALSO MEETS THE REQUIREMENTS FOR TECH SPEC 3.5.1, ACTION G, SPECIAL REPORT FOR EMERGENCY CORE COOLING SYSTEM ACTUATION AND INJECTION INTO THE REACTOR COOLANT SYSTEM.
440 | 4401987073 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401987073R01.pdf | 1987-10-29 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 80 | POWER LEVEL - 080%. ON OCTOBER 29, 1987 AT 1837, 2155 AND 2216 THREE MAIN STEAM ISOLATION VALVES (MSIV) FAILED TO FAST CLOSE IN THE TIME REQUIRED BY TECHNICAL SPECIFICATIONS 3.4.7 AND 3.6.4. SUBSEQUENTLY, THE THREE MSIVS WERE STROKED WITH SATISFACTORY CLOSURE TIMES. ON NOVEMBER 3 AT 1157 AND 1208 TWO OF THE SAME MSIVS FAILED TO CLOSE WITHIN THE REQUIRED TIME. BASED ON REPEAT FAILURES A PLANT SHUTDOWN WAS COMMENCED AT 1330. THE REACTOR WAS MANUALLY SCRAMMED AT 1819. THE CAUSE OF THE MSIVS DELAYED CLOSURES HAS BEEN ATTRIBUTED TO THE ASSOCIATED FAST CLOSURE DUAL SOLENOID AIR PILOT VALVES STICKING IN THE NORMAL ENERGIZED POSITION WHEN DEENERGIZED. THE DUAL SOLENOID VALVES WERE STICKING DUE TO DEGRADATION OF THE ELASTOMER DISC AND CORE ASSEMBLY SEALS CAUSED BY EXPOSURE TO EXCESSIVE HEAT FROM PREVIOUSLY EXISTING STEAM LEAKS. THE ELASTOMER DISCS AND SEALS FOR ALL MSIV DUAL SOLENOID PILOT VALVES HAVE BEEN REPLACED. OTHER EQUIPMENT HAS BEEN EVALUATED FOR ANY ADVERSE AFFECTS FROM KNOWN STEAM LEAKS. ADDITIONAL TEMPERATURE MONITORING EQUIPMENT HAS BEEN INSTALLED AND SPECIAL INSTRUCTIONS ESTABLISHED SPECIFYING ACTIONS TO BE TAKEN UPON EXCEEDING BASELINE TEMPERATURE VALUES. SUBSEQUENT PHYSICAL, CHEMICAL AND THERMAL ENDURANCE TESTING CONFIRMED THE FAILURE MECHANISM OF THE ELASTOMER.
440 | 4401988012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988012R00.pdf | 1988-04-27 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 100 | POWER LEVEL - 100%. ON APRIL 27, 1988, AT 2209, AN AUTOMATIC REACTOR SCRAM OCCURRED DUE TO A REACTOR WATER LEVEL OF LESS THAN LEVEL 3 (+177.7 INCHES ABOVE THE TOP OF ACTIVE FUEL). THE LOW WATER LEVEL OCCURRED AFTER AN IMPROPER TRANSFER OF DC POWER SUPPLIES RESULTING IN A TEMPORARY LOSS OF AC CONTROL POWER FOR THE HOT SURGE TANK LEVEL CONTROL VALVES AND A SUBSEQUENT TRIP OF ALL OPERATING FEEDWATER PUMPS. THE CAUSES OF THE EVENT ARE PERSONNEL ERROR AND PROCEDURAL INADEQUACY. A MISINTERPRETATION OF THE INSTRUCTION DESCRIBING DC POWER SUPPLY TRANSFERS PLACED THE DC ELECTRICAL SYSTEM IN A NON-RECOMMENDED LINEUP LEADING TO THE LOSS OF VITAL 120 VAC POWER FED FROM THE DC BUS VIA AN INVERTER. THE INSTRUCTION WAS CONFUSING AND DIFFICULT TO IMPLEMENT. CORRECTIVE ACTIONS TO PREVENT RECURRENCE INCLUDE; COUNSELING OF THE OPERATORS INVOLVED REGARDING THEIR RESPONSIBILITIES TOWARDS FAIMILARITY WITH INSTRUCTIONS AND PROCEDURAL COMPLIANCE, TRAINING FOR ALL OPERATORS REGARDING THE SEQUENCE OF EVENTS, AND REVISING THE APPROPRIATE SYSTEM OPERATING INSTRUCTIONS TO PROVIDE GREATER EASE OF USE BY THE OPERATOR.
440 | 4401988015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988015R00.pdf | 1988-04-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Perry | B | GE | SU | 1 | POWER LEVEL - 001%. ON APRIL 30, 1988 AT 1754, DURING PLANT STARTUP A REACTOR SCRAM OCCURRED DUE TO A REACTOR WATER LEVEL OF LESS THAN LEVEL 3 (+177.7 INCHES ABOVE TOP OF ACTIVE FUEL). THIS EVENT OCCURRED DURING A PLANT STARTUP WHEN THE STEAM BYPASS VALVES OPENED UNEXPECTEDLY UPON OPENING OF THE B MAIN STEAM ISOLATION VALVE (MSIV) RESULTING IN THE LEVEL TRANSIENT. THE ROOT CAUSE OF THIS EVENT WAS A PROCEDURAL DEFICIENCY. THE OPERATING PROCEDURES DID NOT ADEQUATELY ADDRESS THE INTERACTION OR PROVIDE ADEQUATE SETPOINT MARGIN FOR THE STEAM BYPASS AND PRESSURE REGULATING SYSTEM WHEN OPENING MSIVS. AN ADDITIONAL CONCERN ASSOCIATED WITH THIS EVENT WAS THAT THE STEAM BYPASS VALVE OPEN ALARM AND ANNUNCIATOR WERE NOT NOTICED BY THE CONTROL ROOM OPERATORS. CORRECTIVE ACTIONS TO PREVENT RECURRENCE INCLUDE; A REVISION TO THE OPERATING PROCEDURES TO ENSURE THAT THE BYPASS SYSTEM DOES NOT UNNECESSARILY OPERATE WHEN OPENING THE MSIVS AT PRESSURE, COUNSELING OF THE OPERATORS INVOLVED REGARDING THEIR RESPONSIBILITIES TOWARD ALARM RESPONSE AND KNOWLEDGE OF PLANT CONDITIONS, AND TRAINING FOR ALL OPERATORS REGARDING THE SEQUENCE OF EVENTS. ADDITIONALLY, A HUMAN FACTORS REVIEW HAS RESULTED IN A DESIGN CHANGE WHICH WILL UPGRADE THE PRIORITY COLOR CODING OF THE BYPASS VALVE OPEN ANNUNCIATOR FROM WHITE TO AMBER.
440 | 4401988017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988017R01.pdf | 1988-05-06 | QR8 | Spurious Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | POWER LEVEL - 100%. ON 5/6/88 AT 1436, DURING THE PERFORMANCE OF A MONTHLY REACTOR PROTECTION SYSTEM (RPS) CHANNEL FUNCTIONAL TEST, AN UNEXPECTED SCRAM OF GROUP 3 CONTROL RODS (APPROXIMATELY 1/4 OF TOTAL) CAUSED REACTOR VESSEL LEVEL TO DECREASE TO LOW LEVEL 3 (+177.7 INCHES ABOVE TOP OF ACTIVE FUEL) RESULTING IN A FULL REACTOR SCRAM. THE SURVEILLANCE TRIPS ONE (A) OF TWO RPS TRIP SYSTEMS CAUSING A HALF RPS TRIP. COINCIDENT WITH THE HALF RPS TRIP A BLOWN FUSE TO THE RPS TRIP SYSTEM B GROUP 3B CONTROL RODS CAUSED A COMPLETE DEENERGIZATION OF ALL GROUP 3 CONTROL ROD SCRAM SOLENOIDS. THE ENSUING GROUP 3 CONTROL ROD SCRAM CAUSED A RAPID POWER DECREASE AND VOID COLLAPSE RESULTING IN A REACTOR VESSEL LOW LEVEL 3 AND FULL RPS SCRAM. OPERATORS RESPONDED IN ACCORDANCE WITH PLANT PROCEDURES AND ALL SYSTEMS OPERATED AS DESIGNED. THE CAUSE OF THE BLOWN FUSE COULD NOT BE READILY IDENTIFIED. THE FUSE WAS REPLACED, AND CURRENT AND VOLTAGE MONITORED WHILE PERFORMING PERTINENT STEPS OF THE MONTHLY RPS SURVEILLANCE TEST. NO ABNORMALITIES WERE IDENTIFIED. ADDITIONAL TEMPERATURE AND CURRENT MONITORING DETERMINED THAT THE CIRCUIT CONFIGURATION UPSTREAM OF THIS FUSE CAUSES SLIGHTLY ELEVATED TEMPERATURES ADJACENT TO THE FUSE. THE FUSE WAS SENT TO THE VENDOR TO PERFORM A FAILURE ANALYSIS.
440 | 4401988020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988020R00.pdf | 1988-06-05 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Perry | B | GE | PO | 81 | POWER LEVEL - 081%. ON JUNE 5, 1988, AT 0326, A REACTOR SCRAM OCCURRED DUE TO HIGH AVERAGE POWER RANGE MONITOR NEUTRON FLUX LEVELS. DURING MANUAL ADJUSTMENT OF REACTOR RECIRCULATION FLOW, THE CONTROL ROOM OPERATOR INADVERTENTLY CAUSED THE RECIRCULATION FLOW CONTROL SYSTEM TO SHIFT TO AUTOMATIC, CAUSING AN INCREASE IN RECIRCULATION FLOW, AND THE SUBSEQUENT REACTOR SCRAM. THE CAUSE OF THIS EVENT WAS PERSONNEL ERROR. AT THE TIME OF THE EVENT, THE FLUX CONTROLLER WAS NOT PROPERLY ADJUSTED FOR AUTOMATIC OPERATION, REQUIRING OPERATION IN THE MANUAL MODE. THE OPERATOR DID NOT EXERCISE PROPER CAUTION WHEN MAKING THE FLOW ADJUSTMENT, AND INADVERTENTLY DEPRESSED THE AUTO PUSHBUTTON ON THE CONTROLLER. TO PREVENT RECURRENCE, THE AUTOMATIC MODE OF FLUX CONTROL HAS BEEN DISABLED UNTIL PROPER ADJUSTMENTS ARE COMPLETED, TO PREVENT ANY UNINTENTIONAL TRANSFERS TO AUTOMATIC. ADDITIONALLY, THE OPERATOR INVOLVED IN THIS EVENT HAS BEEN DISCIPLINED, AND ALL LICENSED OPERATORS WILL BE TRAINED TO THIS LICENSEE EVENT REPORT.
440 | 4401988023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988023R00.pdf | 1988-06-08 | QR8 | Spurious Reactor Trip | [45 empty] | Perry | B | GE | PO | 23 | POWER LEVEL - 023%. ON JUNE 8, 1988 AT 0923, A REACTOR SCRAM AND NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM BALANCE OF PLANT (BOP) CONTAINMENT ISOLATION OCCURRED DUE TO LOSS OF POWER TO BOTH REACTOR PROTECTION SYSTEM (RPS) POWER DISTRIBUTION BUSSES. AT 0922 THE MAIN TURBINE TRIPPED DUE TO HIGH LEVEL IN A MOISTURE SEPARATOR REHEATER DRAIN TANK. DURING RECOVERY FROM THE MAIN TURBINE TRIP, AN OPERATOR INADVERTENTLY TRIPPED THE TWO MAINLINE BREAKERS FEEDING THE BOP ELECTRICAL DISTRIBUTION BUSSES. CONSEQUENTLY, BOTH RPS BUSSES WERE DEENERGIZED, RESULTING IN A REACTOR SCRAM, A FULL CONTAINMENT ISOLATION, BOTH REACTOR RECIRCULATION PUMPS TRIPPING AND LOSS OF FEEDWATER. THE CONTROL ROOM OPERATORS VERIFIED ALL AUTOMATIC ACTUATIONS OCCURRED. THE REACTOR CORE ISOLATION COOLING SYSTEM WAS STARTED AT 0926 AND UTILIZED TO CONTROL REACTOR VESSEL LEVEL AND PRESSURE. THE CAUSE OF THE EVENT WAS PERSONNEL ERROR. THE SUPERVISING OPERATOR TURNED THE CONTROL SWITCHES IN THE WRONG DIRECTION WHEN ATTEMPTING TO RESET THE BREAKER POSITION INDICATION FLAGS RESULTING IN THE BOP SUPPLY BREAKERS OPENING. THE OPERATOR HAS BEEN COUNSELED BY PLANT MANAGEMENT AND DISCIPLINARY ACTION HAS BEEN TAKEN. IN ACCORDANCE WITH THE LICENSED OPERATOR REQUALIFICATION TRAINING PROGRAM, OPERATORS WILL RECEIVE TRAINING ON THE SEQUENCE OF EVENTS WHICH LED TO THIS REPORT.
440 | 4401988024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988024R00.pdf | 1988-06-16 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Perry | B | GE | PO | 100 | POWER LEVEL - 100%. ON JUNE 16, 1988 AT 1432 DURING TROUBLESHOOTING TO A RECIRCULATION SYSTEM AUTOMATIC FLUX CONTROLLER CIRCUIT CARD, A SPURIOUS SPIKE IN RECIRCULATION FLOW DEMAND CAUSED INCREASED CORE FLOW RESULTING IN AN UPSCALE NEUTRON FLUX TRIP AND SUBSEQUENT REACTOR SCRAM. PRIOR TO THE EVENT, THE FLUX CONTROLLER WAS IN MANUAL AND THE INDIVIDUAL LOOP FLOW CONTROLLERS WERE IN AUTOMATIC. THE CAUSE OF THE EVENT WAS THE REINSERTION OF THE AUTOMATIC FLUX CONTROL CARD INTO THE RECIRCULATION FLOW CONTROL CIRCUITRY. THIS ACTION INDUCED A NOISE SPIKE INTO THE CONTROL LOOP CIRCUITRY. THE PERTURBATION RESULTED IN AN APPROXIMATELY 8% INCREASE IN FLOW CONTROL VALVE POSITION DEMAND FROM THE INITIAL 41%. SUBSEQUENT TROUBLESHOOTING OF THE CIRCUIT ON JUNE 17 CONFIRMED THIS HYPOTHESIS AS DATA SHOWED THAT FLOW DEMAND SIGNAL SPIKES OF VARYING MAGNITUDE AND DIRECTION WILL OCCUR UPON INSERTION OF THE FLUX CONTROL CARD INTO THE LOOP CIRCUITRY. TO PREVENT FUTURE OCCURRENCES, THE HYDRAULIC POWER UNITS (HPUS) TO THE RECIRCULATION SYSTEM FLOW CONTROL VALVES WILL BE LOCKED UP TO PREVENT UNEXPECTED TRANSIENTS TO THE PLANT PRIOR TO SUBSEQUENT REMOVAL AND REINSTALLATION OF ELECTRIC CIRCUIT BOARDS IN THE FLOW CONTROL SYSTEM DURING POWER OPERATION. ADDITIONALLY, THE RECIRCULATION SYSTEM WILL NOT BE OPERATED IN AUTOMATIC FLOW CONTROL UNTIL OPTIMUM TUNING OF THE SYSTEM IS ACHIEVED.
440 | 4401988026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401988026R00.pdf | 1988-06-23 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 80 | POWER LEVEL - 080%. ON JUNE 23, 1988, AT 0944, A REACTOR SCRAM OCCURRED DUE TO AN UNEXPECTED TURBINE TRIP WITH REACTOR POWER GREATER THAN THE SCRAM BYPASS SETPOINT. AT THE TIME OF THE EVENT, CONTROL ROOM OPERATORS WERE PERFORMING WEEKLY TURBINE TESTING REQUIREMENTS. ALL PLANT SYSTEMS FUNCTIONED AS DESIGNED, AND THE PLANT WAS STABILIZED IN A NORMAL HOT SHUTDOWN CONDITION. THE CAUSE OF THE TURBINE TRIP WAS A MECHANICAL FAILURE OF THE TRIP LATCH ASSEMBLY ATTRIBUTED TO IMPROPER CLEARANCES WITHIN THE MECHANISM ESTABLISHED DURING MANUFACTURING AND INITIAL INSTALLATION. THE COMPONENT SUPPLIER, GENERAL ELECTRIC, HAS BEEN NOTIFIED OF THE DEFICIENCY FOR POTENTIAL GENERIC APPLICATION. IN ORDER TO PREVENT RECURRENCE, THE DEFECTIVE PARTS WERE REPLACED AND PROPER CLEARANCES WITHIN THE MECHANISM WERE ESTABLISHED BY MACHINING OF VARIOUS TRIP LATCH ASSEMBLY SURFACES. SYSTEM RETESTS WERE PERFORMED TO ENSURE PROPER OPERATION OF THE TRIP ASSEMBLY, AND THE PLANT WAS RETURNED TO FULL POWER ON JUNE 27, 1988.
440 | 4401990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401990001R00.pdf | 1990-01-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 100 | On January 7, 1990, at 1132, a reactor scram occurred due to a reactor water level of less than Level 3 (+177.7 inches above the top of active fuel). The low water level occurred after an improper transfer of 480 volt AC power supplies resulted in a momentary power interruption to the feedwater control circuitry and a total loss of feedwater flow. <br /><br /> The cause of this event was Personnel Error, inattention to detail. An operator inadvertently pulled the wrong fuses, which resulted in the 480 volt bus being deenergized when the bus transfer was made. <br /><br /> To prevent recurrence, the operator has been counseled on the importance of paying close attention to detail when operating plant equipment. The system operating instruction was revised and supplemental training on live-bus transfers was developed. Investigation is being performed into possible design changes to increase Feedwater Control System availability in the event of loss of non-essential busses. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event. <br /><br /> Submittal of this report also meets the requirements for Technical Specification 3.5.1 Action g. which requires a Special Report following any Emergency Core Cooling System actuation and injection into the Reactor Coolant System.
440 | 4401991027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401991027R00.pdf | 1991-12-22 | J1 | Flood | [8 empty] | X |  | X | [24 empty] | X |  |  |  |  | X |  |  |  |  | Perry | B | GE | PO | 100 | On December 22, 1991, at 0205 hours, a manual reactor scram was inserted per Integrated Operating Instruction (IOI) - 8 due to a non-isolable break in the Circulating Water System (N71) piping. The break occurred on a section of 36 inch fiberglass reinforced plastic pipe which supplies cooling water to the auxiliary condensers. At 0259, the shift supervisor declared an Alert based on reports of rising water level received and indications available in the Control Room. All required notifications were made regarding the Alert declaration. <br /><br /> Equipment anomalies and malfunctions which occurred after the manual scram was inserted are summarized in the text of this LER. The cause of the pipe rupture was attributed to a combination of factors which included a pre-existing flaw in the fiberglass, functional degradation of a pipe support and improper installation of an O-ring gasket at the fiberglass to steel transition flange. The plant was restarted on January 3, 1992 after repairs were made to the affected piping and associated supports. Additionally, the equipment anomalies and malfunctions which occurred after plant shutdown were investigated and corrective actions taken where appropriate.
440 | 4401992017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401992017R00.pdf | 1992-09-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Perry | B | GE | PO | 100 | At 2107 hours on September 10, 1992 a full Reactor Protection System (RPS) scram occurred due to reactor water level reaching the level 3 setpoint of 178 inches. The low reactor water level condition resulted from closure of the 'B' Reactor Feed Pump Turbine (RFPT) control valves following a loss of hydraulic oil pressure from the RFPT lube oil system. <br /><br /> The loss of hydraulic pressure was due to oil leaking by the gasket for RFPT B servo valve filter. It was determined that the oil pressure did not drop low enough to indicate a RFPT trip, which would have initiated a Motor Feed Pump (MFP) auto-start and a Reactor Recirculation System Flow Control Valve runback, but was low enough to allow closure of the RFPT control valves. The leaking gasket was believed to be the result of improper reassembly during periodic filter replacement during a recent refueling outage. <br /><br /> The filter gasket was inspected and showed no evidence of a material defect. The gasket was subsequently replaced and proper reassembly of the filter assembly verified. Appropriate torque on the filter assembly retaining bolts was also verified for both RFPT trains. <br /><br /> Submittal of this report also meets the requirements for Technical Specification 3.5.1, Action g. which requires a Special Report following any Emergency Core Cooling System actuation and injection into the Reactor Coolant System.
440 | 4401993010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401993010R00.pdf | 1993-03-26 | QL4 | Loss of Non-safety-Related Cooling Water | [8 empty] | X |  | X | [24 empty] | X |  |  |  |  | X |  |  |  |  | Perry | B | GE | PO | 100 | On March 26, 1993, at 1525 hours, a manual reactor scram was inserted due a rupture in a 30 inch section of underground Service Water piping. Prior to the event, leak isolation was in progress to determine the source of water which was earlier reported coming from the ground near the Water Treatment Building. An Alert was conservatively declared at approximately 1535 hours due to flooding in plant areas which potentially posed a threat to safe shutdown equipment. <br /><br /> All plant equipment functioned as designed during the plant shutdown with the exception of several minor equipment anomalies. No safety related equipment was affected as a result of the flooding. <br /><br /> The cause for the piping failure was attributed to induced axial piping stress caused by pipe bending as a result of a localized loss of soil support. Appropriate corrective action to effect repairs to the Service Water piping will be completed prior to plant startup. Additional corrective measures will also be taken to minimize water entry into plant buildings.
440 | 4401993015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401993015R00.pdf | 1993-07-09 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | On July 9, 1993, at 0537, with the reactor at 100 percent power, and both Reactor Recirculation Pumps in fast speed, both pumps unexpectedly downshifted automatically to slow speed. At 0544, Control Room operators manually scrammed the reactor from 52 percent power in accordance with plant operating procedures after the reactor entered the region of potential instability of the power to flow map.<br /><br /> It was concluded that the most probable cause of the Reactor Recirculation Pump speed downshift was the failure of both Reactor Recirculation Pump Suction Temperature Resistance Temperature Detectors (RTDs). Both RTDs were replaced and subsequently returned to the manufacturer for failure analysis. Any further corrective actions will be determined pending the results of this analysis. Additionally, a modification was made to provide a control room alarm should a RTD failure recur. A time events analyzer has been installed to monitor the Reactor Recirculation Pump fast to slow speed downshift logic circuitry during the current Reactor startup.
440 | 4401994002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401994002R00.pdf | 1994-01-28 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | On January 28, 1994 at 1944, both Reactor Recirculation system pumps automatically downshifted from fast speed to slow speed. Due to the decrease in core flow, reactor parameters entered the region of potential instability on the power to flow map. In accordance with plant procedures, the control room operator initiated a manual scram at 1945 with reactor power level at 47 percent. No power oscillations indicating core power instability were observed while within the instability region of the power to flow map. <br /><br /> The cause of this event was an equipment failure. A relay on alarm card 1C34-K618B failed open causing the low feedwater flow relays to initiate a recirculation pump downshift. The cause of the relay failure could not be determined. A review of the failure history for this model card did not identify any generic concerns or adverse failure trends. As a result of this event, the alarm card with the failed relay and the alarm card in the redundant trip system were replaced. Two other alarm cards of the same model that could cause a recirculation pump downshift were also replaced.
440 | 4401995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401995005R00.pdf | 1995-08-31 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 100 | On August 31, 1995, at 1142 hours, the Perry Nuclear Power Plant was at 100 percent rated thermal power, when the reactor automatically scrammed due to a trip of the main turbine and subsequent closure of the Turbine Control and Stop valves. <br /><br /> The root cause of the scram was equipment failure. A resistor in a 125 VDC to 120 VAC Topaz inverter failed resulting in the loss of a 24 VDC instrument power supply to Reactor Pressure Vessel level instrumentation. Upon loss of the 24 VDC power supply, reactor low water level initiation logic was satisfied and a Reactor Core Isolation Cooling (RCIC) system initiation signal was generated. The RCIC initiation in turn caused an immediate main turbine trip and subsequent reactor scram. Plant systems and components functioned as designed during this transient with the exception that one outboard containment isolation valve, which failed to close. This event has minimal safety significance as the scenario is bounded by accident analyses. <br /><br /> Corrective actions for this event include: replacement of the Topaz inverter unit and restoration of the instrument power supply; evaluation of inverter upgrades; and evaluation of plant modifications to preclude an immediate reactor scram upon loss of an inverter. This event is being reported in accordance with the requirements of 10CFR50.73 (a) (2) (iv), 10CFR50.73(a) (2) (i) (B). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
440 | 4401995007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401995007R00.pdf | 1995-09-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Perry | B | GE | PO | 15 | On September 2, 1995, at 1735 hours, the Perry Nuclear Power Plant was at 15 percent rated thermal power when the reactor automatically scrammed due to low reactor pressure vessel (RPV) water level. The reactor scram occurred as operators were preparing to transfer feedwater flow from the motor driven feedwater pump (MFP) to the 'A' turbine driven feedwater pump (i.e., reactor feedwater pump turbine (RFPT)). Feedwater control was lost, resulting in a reactor pressure vessel water level decrease and ultimately, a low RPV level 3 scram. Level was restored by manually initiating the High Pressure Core Spray (HPCS) system and by using the 'A' RFPT. The plant was stabilized in Operational Condition 3 (Hot Shutdown). This event had minimal safety significance; the scenario was bounded by accident analyses, and plant systems and components functioned as designed. <br /><br /> The cause of this event was operator error. The 'A' RFPT had been started with its flow controller in AUTO rather than in the procedurally required MANUAL position, resulting in a loss of feedwater control to the operating MFP. Corrective actions include training, personnel counseling, and a reemphasis of management's expectations with respect to self-checking. This report is submitted in accordance with 10 CFR 50.73 (a) (2) (iv), for an event which resulted in an automatic Reactor Protection system actuation and a manual Engineered Safety Feature actuation (i.e., HPCS initiation). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
440 | 4401995008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401995008R00.pdf | 1995-09-11 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Perry | B | GE | PO | 100 | On September 11, 1995, at 1351 hours, the Perry Nuclear Power Plant was at 100 percent rated thermal power when the reactor automatically scrammed due to a trip of the main turbine and subsequent closure of the turbine control and stop valves. <br /><br /> The root cause of the reactor scram was equipment failure. A capacitor in a 125 VDC to 120 VAC Topaz inverter failed, resulting in degradation of a 24 VDC instrument power supply to Reactor Pressure Vessel level instrumentation. Upon degradation of the 24 VDC power supply, reactor low water level initiation logic was satisfied, resulting in the generation of a Reactor Core Isolation Cooling (RCIC) system initiation signal. The RCIC initiation in turn caused an immediate main turbine trip and subsequent reactor scram. Plant systems and components functioned as designed during this transient. This event had minimal safety significance; the scenario is bounded by accident analyses, and plant systems and components functioned as designed. <br /><br /> Corrective actions for this event include: replacement of the Topaz inverter and restoration of the instrument power supply; evaluation of inverter refurbishment schedules and upgrades; and evaluation of plant modifications to preclude an immediate reactor scram upon loss of an inverter. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv). This report is also being submitted to fulfill the requirements of Technical Specification 3.5.1, Action h.
440 | 4401996005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401996005R00.pdf | 1996-05-30 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 100 | On May 30, 1996, at 0616 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 100 percent rated thermal power, when an automatic reactor scram occurred due to an auxiliary transformer sudden pressure signal and subsequent main generator lockout, main generator trip, and turbine control valve fast closure. The event was initiated when 13.8 kV circuit breaker L1108 was re-closed following replacement and post maintenance testing. The circuit breaker tripped open in response to a failure of the associated nonsafety load center transformer, LF-1-C. As a result of this transient, the 22 kV/13.8 kV auxiliary transformer, 110-PY-B, developed a sudden pressure signal due to internal winding damage which was caused by the through-fault current generated when the LF-1-C transformer failed. This damage rendered the auxiliary transformer inoperable, resulting in the reactor scram. The nonsafety electrical loads automatically transferred to the inservice start-up transformer, 200-PY-B, during the event; safety-related loads were being supplied by the start-up transformer at the time of the event. Plant systems and components functioned as designed with the exception of the auxiliary transformer, which should have been able to accept the through-fault current received. This event had minimal safety significance since safety-related electrical loads were not affected, and the plant was stabilized within the bounds of normal operating procedures. <br /><br /> The corrective actions for this event include: replacement of the failed transformers; evaluation on the necessity of load center transformer upgrades; and, evaluation and/or validation of the susceptibility of other critical transformers to the mechanisms which caused the respective failures. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv) as an automatic actuation of the Reactor Protection System.
440 | 4401997001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401997001R00.pdf | 1997-01-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Perry | B | GE | PO | 100 | POWER LEVEL - 100%. On January 7, 1997, at 0533 hours, the Perry Nuclear Power Plant, Unit 1, automatically scrammed from 100 percent rated thermal power, due to a loss of electrical power to the Feedwater Control system which resulted in a Reactor Protection system actuation on low reactor water level. The High Pressure Core Spray system, the Division 3 Diesel Generator, and associated support systems including Division 3 Emergency Service Water (ESW), the Reactor Core Isolation Cooling system, the Division 1 ESW system, and the Nuclear Steam Supply Shutoff system also actuated during the event. The cause of this event is personnel error; a Nonlicensed Operator failed to utilize self-checking and performed an inappropriate procedural step which resulted in the loss of electrical power to the vital loads. The pre-job briefing conducted for the switching activity did not contain sufficient detail to ensure successful completion of the switching activity. A Standing Instruction was issued to inform the operating crews of the event, to communicate expectations concerning in-field supervision and pre-job briefings, and to detail missed opportunities for preventing the event through self-checking and checking of others. Procedural enhancements are being evaluated and programmatic improvements are being developed. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv). This report is also being submitted to fulfill the requirements of Operational Requirements Manual, Special Reports, Emergency Core Cooling System Injection, Section 7.6.2.1.
440 | 4401997005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401997005R00.pdf | 1997-06-05 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Perry | B | GE | PO | 100 | On June 5, 1997 at 1050 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 100 percent rated thermal power, when an automatic reactor scram occurred due to a 13.8 kV cable termination bus bar support fault at the auxiliary transformer, and subsequent auxiliary transformer phase differential relaying, generator lockout, turbine trip, and turbine control valve fast closure. The event was initiated when a three phase ground fault occurred on the 13.8 kV supply side termination compartment of the auxiliary transformer. It was determined the fault developed when electrical tracking established a conduction path across the 13.8 kV bus bar support/insulator to ground, apparently as a result of an accumulation of moisture and dust which entered the termination compartment housing at the location where a piece of gasket material was missing from the compartment housing sealing surface. Safety-related electrical loads were being supplied by the inservice start-up transformer. The nonsafety electrical loads automatically transferred to the start-up transformer, 200-PY-B, with the exception that the nonsafety bus that was locked out. This event had minimal safety significance since the safety-related loads were not affected, and the plant was stabilized within the bounds of plant operating procedures.The corrective actions for this event include: rework the 13.8 kV terminations and auxiliary transformer testing; periodic inspections of transformer termination compartments; additional training of transformer maintenance personnel; and, inspection/testing of protective relays for Unit 1 and Unit 2 startup transformers. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an automatic actuation of the Reactor Protection System.
440 | 4401997016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401997016R00.pdf | 1997-12-19 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 100 | On December 19, 1997, at 0939 hours, the Perry Nuclear Power Plant, Unit 1, automatically scrammed from 100 percent of rated thermal power, due to a Turbine Electro-Hydraulic Control (EHC) system tubing fluid leak which resulted in a turbine trip, Reactor Protection system (RPS) actuation, and subsequent Residual Heat Removal isolation logic actuation. Operators responded to the event in accordance with the appropriate procedures and the plant was safely shut down.The cause of this event is a vibration-induced fatigue failure of a section of turbine control valve (TCV) EHC system tubing. The vibration is the normal result of the pressure transients within the system during operation. Contributing causes to the tubing failure were the design application of the tubing fitting used to connect the EHC tubing to the TCV, and the support scheme of the tubing.The EHC tubing compression fittings for the applicable hydraulic lines at the four TCVs were replaced with welded flare fittings. Additional EHC tubing hangers were added to two of the four TCVs to provide additional tubing support closer to the fittings. A design modification to install an accumulator in the applicable TCV ,hydraulic lines to dampen the vibration is being evaluated. The applicable tubing and fittings at the TCVs are being monitored, as plant conditions permit, until an appropriate design modification is implemented.
440 | 4401998002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4401998002R00.pdf | 1998-07-01 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Perry | B | GE | PO | 100 | On July 1, 1998, at 0805 hours, Perry Nuclear Power Plant (PNPP) experienced a Reactor Core Isolation Cooling (RCIC) system initiation causing the main turbine and both feedwater pump turbines to trip, as designed. The plant automatically scrammed from 100 percent rated thermal power, due to closure of the main turbine stop and control valves. During the associated reactor level transient, the High Pressure Core Spray system initiated and injected into the Reactor Pressure Vessel.The cause of the RCIC initiation was due to design application of the optical isolator. A capacitor shorted in a division 1 trip unit. The short circuit caused a decrease in the supply voltage. The decrease in voltage allowed the division 1 RCIC initiation logic to be satisfied. It is suspected that transient noise spikes, due to inductive relay kickback, triggered an optical isolator output. The output satisfied the division 2 initiation logic, resulting in a RCIC initiation. (Note: The division 2 logic is physically located in division1.) The failed and damaged components have been replaced. The initiation relay contacts were verified to be in the proper position. The optical isolator and the division 2 initiation logic relays were bench tested satisfactorily and returned to service. Wiring checks were completed to ensure the installed configuration was as designed.This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv) and also satisfies PNPP's Operational Requirements Manual section 7.6.2.1.
440 | 4402001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402001001R00.pdf | 2001-04-29 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Perry | B | GE | PO | 16 | On 4/28/01 at 2101 hours, a main generator field ground annunciator was received due to a Stator Water System leak and actions were taken to remove the main generator from service at 2323 hours. Following generator removal/turbine trip, the main condenser vacuum degraded and was determined non-recoverable. A manual reactor scram was inserted by procedure at 0050 hours, on 4/29/01. Following insertion of the reactor scram, as a result of one turbine steam bypass valve, which stuck one half open for four minutes, invalid Division 2 Emergency Closed Cooling System (ECCS) actuation signals were received on a combination of low sensed level and high pressure signals. Then shortly after MSIV closure at 0249 hours, during the first of a series of manual SRV operations for controlling pressure, an invalid Division 3 ECCS actuation signal was received. Though the signals were invalid, all systems responded as designed to their logic actuation. Also in response to the Division 3 actuation signal, the High Pressure Core Spray System pump was over-ridden off in accordance with plant procedures. Subsequently, the A and B loops of Residual Heat Removal were required by procedure to be placed in suppression pool cooling mode of operation as a result of SRV operations. This resulted in entry into Technical Specification 3.0.3, "Limiting Condition for Operation Applicability."The cause of the loss of vacuum was a process error that resulted in two moisture separator drain tank manways being improperly torqued during the recent refueling outage and becoming unseated when the pressure was reduced in the tank following the turbine removal from service. The cause of the reactor level/pressure actuations was determined to be localized flashing and pressurization of the sensing lines in the affected instrument reference legs.The stator water cooling lines were repaired. The affected manways were re-worked, gaskets repaired and the remaining manways were properly retorqued; RPV level instrument reference legs were filled and vented, and operators were provided with awareness briefings and lessons learned from the event.This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), as a condition that resulted in multiple specified system actuations, and 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications.
440 | 4402001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402001003R00.pdf | 2001-07-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 100 | On 7/11/01, at 2223 hours, the plant was operating at 100 percent reactor power when a loss of feedwater occurred resulting in an automatic reactor scram, an automatic trip of the Reactor Recirculation Pumps, an automatic initiation and injection of the High Pressure Core Spray System (HPCS) and the Reactor Core Isolation Cooling System (RCIC) and a Balance of Plant Isolation due to a valid Reactor Pressure Vessel (RPV) water low level signal. Subsequently, at 0400 on 7/12/01, an invalid low RPV water level signal occurred resulting in an invalid automatic initiation of the HPCS pump, HPCS diesel and associated support systems, however no injection occurred. All systems responses were as expected to the valid and to the invalid signals.The cause of the loss of feedwater event was determined to be a blown fuse that supplies 24-Volt DC electrical power to the Loop B Analog Instrument Panel, which contains instrumentation for the feedwater control system. The cause of the invalid RPV low level actuation was determined to be due to a thermal hydraulic perturbation coincident with decreasing reactor pressure.The power supply fuse was replaced and a thermographic examination was performed of all fuses located in the Control Room. A thermographic examination of the Control Room fuses was again performed following plant restoration at approximately 60 percent power. Although no additional failures were identified, fuses indicating above normal temperatures were replaced. To address the invalid HPCS initiation, the signal dampening for the HPCS RPV level instruments was increased in order to reduce the instrument vulnerability to short duration pulses.This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), an event or condition that resulted in specified system actuations.
440 | 4402001005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402001005R01.pdf | 2001-12-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Perry | B | GE | PO | 100 | On December 15, 2001, at 2228 hours, with the plant operating at 100 percent reactor power, an excessive feedwater demand transient occurred resulting in a high Reactor Pressure Vessel (RPV) water level scram. Following the feedwater pump trip on high RPV level, RPV level decreased causing actuation of High Pressure Core Spray System (HPCS), Reactor Core Isolation Cooling System and containment isolation as designed.A Reactor Protection System (RPS) actuation occurred on low RPV water level at 2304 hours when level inadvertently drifted low. Additionally, the HPCS diesel governor was misadjusted during diesel shutdown resulting in inoperability that was later identified during the review of normal surveillance testing results on December 21, 2001.The cause of the feedwater transient was determined to be a failed logic card that has since been replaced. The cause of the RPS actuation and the failure to meet Technical Specifications was determined to be operator performance deficiencies. Lessons learned from the event were presented to operators and the HPCS diesel procedure was revised.This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), an event or condition that resulted in specified system actuations, 10CFR50.73(a)(2)(i)(B), a condition prohibited by Technical Specifications, and also satisfies Perry Plant's Operational Requirements Manual (ORM) section 7.6.2.1, special report for an Emergency Closed Cooling System (ECCS) injection into the RPV. This was the fourteenth HPCS injection to date. The injection nozzle usage factor is less than 0.70, therefore no further data is required by the ORM.
440 | 4402002001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402002001R01.pdf | 2002-09-22 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 90 | On September 22, 2002, at 0146 hours, when the Perry Nuclear Power Plant was operating in Mode 1 at 90 percent reactor power, a turbine trip occurred which resulted in a turbine control valve fast closure reactor scram Investigation determined that the turbine trip occurred due to the failure of the turbine trip latch assembly to properly reset following weekly testing. While attempting to reset the scram following the event, it was identified that a Scram Discharge Volume (SDV) drain valve stem coupling had failed. The valve repositioned to its required closed position during the scram, however, it would not reopen when the scram was reset. Additionally, increased seal leakage from Reactor Recirculation Pump A was noted. The turbine trip was caused by a malfunction of the turbine trip latch assembly which failed to reset following testing of the mechanical trip device. The failure to relatch was determined to be caused by latch travel limitations as a result of two missing setscrews. The missing set screws were replaced, the linkage was adjusted and the assembly was retested. The SDV drain valve failure to open was due to failure of the stem coupling. All four SDV vent and drain valve stem couplings were replaced with a coupling of an improved design The reactor recirculation pump seal leakage was due to a dislodged guide bushing in the seal assembly. The seal was replaced with a rebuilt spare seal. This event was reviewed and determined to be within design evaluation limits, and therefore was determined to be not safety significant. This event was reported via the Emergency Notification System in accordance with 10CFR50 72(b)(2)(iv)(B), as an event that resulted in an actuation of the Reactor Protection System when the reactor is critical. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of the system specified in 10CFR50.73(a)(2)(iv)(B)(1), which is the Reactor Protection System.
440 | 4402003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402003002R01.pdf | 2003-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Perry | B | GE | PO | 100 | On August 14, 2003, at 1610 hours, with the Perry Nuclear Power Plant operating in Mode 1, at approximately 100 percent reactor power, a generator trip due to under-frequency occurred resulting in a turbine control valve fast closure scram. The under-frequency was the result of a loss of off-site power. The cause of the grid disturbance that resulted in the loss of off-site power is still under investigation by First Energy. The loss of off-site power required entry into the emergency plan for an Unusual Event. Entry into the emergency plan is reportable per 10CFR50.72(a)(1)(i). Additional reporting requirements are documented in the event report. Loss of off-site power to the safety-related emergency power supply busses for greater than 15 minutes resulted in the declaration of an Unusual Event, which was reported to the NRC via the Emergency Notification System (ENS) at 1635hours. Subsequently, it was recognized that power was not available at the Emergency Operations Facility and the Backup Emergency Operations Facility. This condition was reported to the NRC via the ENS at 2225 hours. The Unusual Event was terminated at 1952 hours on August 15, 2003, following restoration of off-site power. Following restoration of power to the emergency busses with the emergency diesel generators, low pressure alarms were received on low pressure core spray (LPCS) and on residual heat removal (RHR) A loop. Following initial investigation, both LPCS and RHR A were declared inoperable at 1847 hours. The associated water-leg pump was determined to be air bound and was vented. Both LPCS and RHR A were vented prior to returning to service.This report also satisfies Operational Requirements Manual section 7.6.2.1, which requires a special report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
440 | 4402004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402004002R00.pdf | 2004-12-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Perry | B | GE | PO | 55 | On December 23, 2004, at 2345 hours, both reactor recirculation system (RRC) pumps at the Perry Nuclear Power Plant (PNPP) unexpectedly downshifted from fast to slow speed. At the time of RRC pump speed downshift, the plant was stable in Operational Condition 1 at 100 percent rated thermal power. Reactor power decreased to about 44 percent and then gradually increased to 55 percent rated thermal power. The power and flow reduction placed the plant in the immediate exit region of the power-flow map . At 2354 hours a reactor scram occurred due to core oscillations being detected by the oscillation power range monitor (OPRM). All control rods fully inserted.The cause of the scram was determined to be a reactor protection system scram signal initiated from the OPRM per design and appropriate for the plant conditions. Troubleshooting of the RRC system pump speed downshift initially identified the probable cause to be a faulty card in the RRC pump control circuit. However, following a subsequent similar RRC pump downshift on January 6, 2005, the cause was determined to be an optical isolator intermittent failure as a result of an inadequate surge suppression network in the control circuit for the RRC pumps (See PNPP LER 2005-001) .This event is being reported under requirements of 10 CFR 50 .73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any of the specified systems.
440 | 4402005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402005001R00.pdf | 2005-01-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Perry | B | GE | PO | 44 | On January 6, 2005, at 0106 hours, while operating at approximately 100 percent rated thermal power, the Perry Nuclear Power Plant (PNPP) reactor recirculation system (RRC) pumps A and B unexpectedly downshifted from fast to slow speed. Reactor power decreased to approximately 44 percent power. This power and flow reduction placed the plant in the immediate exit region of the power-flow map. While operators were inserting control rods in accordance with the applicable off normal operating instructions, RRC pump A unexpectedly tripped from slow speed to off at 0110 hours. At 0112 hours, a manual reactor scram was initiated by the control room crew. All control rods fully inserted. At 0119 hours, following reactor level reduction below level 8 (219 inches above top of active fuel), the motor feedwater pump could not be manually started. At 0122 hours, a reactor core isolation cooling (RCIC) pump was started for injection to the reactor vessel and continued to provide reactor level control. It was determined that the RRC pumps downshift originated from a degraded optical isolator in the RRC logic circuitry. The installed resistor/capacitor surge suppression network on the optical isolator was insufficient to protect the output transistors from the inductive kick experienced during normal operation, allowing intermittent malfunctioning output. To minimize this kick, diodes were installed across applicable optical isolators, downstream trip logic relays to limit the inductive loads on the optical isolator card transistors. This event is being reported under requirements of 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the specified systems.
440 | 4402006005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402006005R00.pdf | 2006-12-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Perry | B | GE | PO | 100 | On December 13, 2006, at approximately 0435 hours, operators manually initiated a Reactor Protection System actuation in response to decreasing Reactor Pressure Vessel (RPV) coolant level. At the time of the event, the plant was in Mode 1 (i.e., Power Operation) with the reactor operating at 100 percent of rated thermal power. All control rods fully inserted into the core and RPV coolant level was maintained such that no emergency core cooling systems were needed to maintain level.The cause of the event is attributed to decreasing Instrument Air System pressure caused by the separation of a header tubing elbow joint, which resulted in a transient in the Reactor Feedwater System. Less than adequate workmanship during plant construction, in the assembly of the air header joint, was determined to be the cause of the air header joint separation. The header tubing joint was replaced. Inspections of a sample of the accessible portions of the Instrument Air System were performed, prior to plant startup. Additional inspections of 2" and 3" soldered joints will be completed by the end of re-fuel outage 12 in 2009. The safety significance of this event is considered to be minimal.This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
440 | 4402007001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402007001R00.pdf | 2007-05-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Perry | B | GE | PO | 31 | On May 15, 2007, at approximately 0058 hours, the Reactor Protection System (RPS) automatically actuated in response to decreasing reactor pressure vessel (RPV) coolant level. At the time of the event, Reactor Feedwater System test/tuning activities were in progress with the reactor operating at approximately 31 percent of rated thermal power. All control rods fully inserted into the core and RPV coolant level was restored with no actuation of emergency core cooling systems.The cause of the event was attributed to a decrease in RPV coolant level resulting from a design logic error not detected during modification pre-operational review or test activities. A contributing cause included a weak conduct of testing process.The design logic error was corrected. The testing instruction was revised. Existing procedures are being revised, and enhanced procedural guidance will be implemented to improve temporary instruction control, conduct of testing, implementation of engineering changes, and infrequently performed tests and evolutions. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the RPS.
440 | 4402007004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402007004R01.pdf | 2007-11-28 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 100 | On November 28, 2007, at 0732 hours, the Reactor Protection System (RPS) automatically actuated due to receipt of a turbine control valve fast closure signal. At the time of the event, the plant was operating at 100 percent rated thermal power. All control rods fully inserted. The High Pressure Core Spray (HPCS) system automatically started and was used to maintain reactor water level. The Reactor Core Isolation Cooling (RCIC) system started but tripped 13 seconds later.The RPS actuation signal was caused by a failure of the power supplies in the Digital Feedwater Control System. The power supplies were replaced with a different model.Failure of the RCIC system to continue operating was due to improper tuning of the flow controller in January 2006. The RCIC flow controller settings were restored to known acceptable values. Further investigation revealed that the RCIC system was inoperable since that time and, as a result, Technical Specifications for RCIC and HPCS were not met.The safety significance of this event is considered to be very low. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(a), 10CFR50.73(a)(2)(i)(B), and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
440 | 4402009001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402009001R00.pdf | 2009-06-21 | QR5 | Turbine Trip | [45 empty] | Perry | B | GE | PO | 100 | On June 21, 2009, at 1750 hours, the reactor protection system (RPS) automatically actuated due to receipt of a turbine control valve fast closure signal. All control rods fully inserted and there were no complications during the shutdown. Reactor coolant pressure and level were maintained within expected parameters. The event was caused by receipt of an invalid high water level signal from moisture separator reheater (MSR) 1B instrumentation, which resulted in a main turbine trip, fast closure of the turbine control valves, and activation of the RPS. Incorrect adjustment of the MSR level switches following maintenance in the recent refueling outage was the direct cause for their actuation. Failure to evaluate industry operating experience, not documenting as-found deficiencies in the corrective action program, not considering non-safety equipment as important, and improper work package/procedure use and adherence contributed to this event. The MSR level switches were subsequently adjusted and calibrated satisfactorily to assure proper operation. Maintenance procedures and templates will be revised to prevent recurrence of incorrect level switch adjustment. The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system including reactor scram or reactor trip.
440 | 4402009004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402009004R00.pdf | 2009-10-16 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | On October 15, 2009, at approximately 1225 hours, a planned shutdown was commenced due to Emergency Service Water System pump B inoperability. At 2241 hours, reactor recirculation pump A failed to transfer to slow speed during pump downshift and subsequently tripped. On October 16, 2009, at 0048 hours, with the reactor operating at approximately 30 percent rated thermal power, shutdown of the plant was completed by manual actuation of the Reactor Protection System (RPS) when the Mode switch was placed in Shutdown in accordance with plant procedures. The reactor recirculation pump A failed to transfer to slow speed because the low-frequency motor-generator output breaker did not close. This resulted from an intermittent connection of an improperly seated contactor retaining clip on the contactor, caused by a skill-based human performance error during a preventive maintenance task. Recently related corrective actions have been focused on addressing the inconsistent use of human performance tools by individual workers and the lack of reinforcement of tool usage by supervisors and management. The failed contactor has been replaced and tested. Proper assembly of the contactor was verified. The safety significance of this event is considered to be low. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event resulting in manual actuation of the RPS.
440 | 4402010003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402010003R00.pdf | 2010-05-11 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | On May 11, 2010, at 2318 hours, a manual Reactor Protection System actuation was inserted in accordance with Technical Specification (TS) 3.1.5, "Control Rod Scram Accumulators." Control Rod Drive (CRD) system charging water header pressure was less than 1520 pounds per square inch gauge and multiple accumulator fault alarms were received on withdrawn control rods. A failed master trip unit caused an invalid Division 2 loss of coolant accident initiation signal and loss of electrical control power to the operating CRD pump and standby CRD pump. Control logic for the operating CRD pump was in an alternate electrical line-up at the time and could not be transferred to its normal source for a timely restart.A replacement trip unit was installed and tested satisfactorily. Future replacement trip units will be required to have 100 hours burn-in prior to installation to reduce the potential for early failures. Plant procedures will be revised to improve recognition and evaluation of long-term alternate plant configurations and degraded conditions.The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.73(a)(2)(i)(A),completion of any nuclear power plant shutdown required by the plant's TS, and 10 CFR 50.73 (a)(2)(iv)(A), an event or condition that resulted in a manual or automatic actuation of plant systems listed in paragraph (a)(2)(iv)(B).
440 | 4402012001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402012001R00.pdf | 2012-03-01 | QR6 | Manual Reactor Trip | [45 empty] | Perry | B | GE | PO | 100 | On March 1, 2012, at 0224 hours, operators manually initiated a reactor protection system actuation in response to a turbine generator runback. At the time of the event, the plant was in Mode 1 with the reactor operating at 100 percent of rated thermal power. All control rods fully inserted into the core and no Emergency Core Cooling systems were required to maintain level.The turbine generator runback resulted from restoration of a generator stator water cooling system pressure gauge after calibration. A low pressure condition was created in a sensing line common to the gauge and associated pressure switch when a technician opened the gauge isolation valve. The low pressure condition resulted in pressure switch actuation on low pressure and was the direct cause of the turbine generator runback. Corrective actions include coding the pressure gauge calibration as an outage task, revising plant procedures, and training of plant personnel to the lessons learned from this event. The safety significance of this event is considered to be small.This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of the reactor protection system.
440 | 4402013001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402013001R00.pdf | 2013-01-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 99 | On January 22, 2013, at 0332 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The High Pressure Core Spray (HPCS) and the Reactor Core Isolation Cooling (RCIC) systems actuated based on a valid reactor water level initiation and injected to restore RPV water level.The cause of the event was failure of a balance-of-plant inverter/static transfer switch, which provides electrical power to the digital feedwater control system. A circuit card in the static transfer switch degraded, which affected operation of the inverter. The electrical loads serviced by the inverter/static transfer switch were placed on an alternate power source. This alignment will continue until permanent repairs are made which are currently scheduled for the next refueling outage.The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
440 | 4402014004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402014004R00.pdf | 2014-10-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 99 | On October 20, 2014, at 0217 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The High Pressure Core Spray (HPCS) and the Reactor Core Isolation Cooling (RCIC) systems actuated based on a valid low reactor water level initiation and injected to restore RPV water level. <br /><br /> The cause of the event was failure of a balance-of-plant static transfer switch, which provides electrical power to the digital feedwater control system. A circuit card in the static transfer switch degraded, which caused a loss of power during manual transfer operations. The electrical loads serviced by the inverter were placed on an alternate power source using the bypass test switch. A design change was completed to provide diverse power sources for the digital feedwater control system availability logic to prevent similar occurrences. <br /><br /> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
440 | 4402014005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402014005R00.pdf | 2014-11-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Perry | B | GE | PO | 98 | On November 7, 2014, at 0847 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The high pressure core spray (HPCS) and the reactor core isolation cooling (RCIC) systems actuated based on a valid low reactor water level initiation and injected to restore RPV water level.<br /><br /> The cause of the event was determined to be the injection of an invalid runback signal from the redundant reactivity control system (RRCS) into the digital feedwater control system (DFWCS). The design change which implemented DFWCS was identified to have a latent design flaw and a design change will be implemented to eliminate these single point vulnerabilities.<br /><br /> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and also Operational Requirements Manual (ORM) section 7.6.2.1, which requires a special report submittal following an emergency core cooling system actuation and injection into the reactor coolant system.
440 | 4402016001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402016001R01.pdf | 2016-01-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Perry | B | GE | PO | 100 | At 2100 hours, on January 23, 2016, the Perry Nuclear Power Plant (PNPP) commenced a reactor shutdown to investigate unidentified leakage in the drywell. At 2122 hours, drywell unidentified leakage exceeded Technical Specification (TS) limits necessitating a plant shutdown as required by TSs. At 0357 hours, on January 24, 2016, while performing the shutdown required by plant TSs, the average power range monitors (APRM) became inoperable due to a calibration setpoint being out of tolerance in the nonconservative direction following a transfer of the reactor recirculation pumps to slow speed. This resulted in a loss of safety function for the APRMs. At 1007 hours, on January 24, 2016, with the plant at 8 percent power, during a feedwater shift to place the motor feed pump in service, reactor water level rose to the level 8 setpoint and the reactor protection system (RPS) automatically initiated, shutting down the reactor. Following the shutdown, a small leak was identified on the reactor recirculation loop "A" pump discharge valve vent line. The recirculation loop is part of the reactor coolant system; this resulted in a degraded condition and a condition prohibited by TS due to pressure boundary leakage. <br /><br /> The cause of the recirculation loop vent line leak was that the weld connecting the root appendage was not performed per the design drawing. The APRM calibration issue was caused by a change to the feedwater flow input to the heat balance. The cause of the reactor level rise and subsequent high water level scram was due to operator error in monitoring and manipulating feedwater system indications and controls.<br /><br /> The safety significance of this event is considered to be small. These events are being reported under; 50.73(a)(2)(i)(A), for completion of any plant shutdown required by the plant's TS; 50.73(a)(2)(ii)(A) for a condition resulting in the plant's principle safety barrier being seriously degraded; 50.73(a)(2)(i)(B) for a violation of Technical Specifications; 50.73(a)(2)(iv)(A) for actuation of the RPS while critical; and 50.73(a)(2)(v)(A) for a loss of safety function.
440 | 4402016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4402016002R00.pdf | 2016-02-08 | QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | [45 empty] | Perry | B | GE | PO | 100 | On February 8, 2016, at 1503 hours, control room operators initiated a manual reactor protection system (RPS) actuation in response to rising temperature in the suppression pool. All control rods full inserted. Prior to the RPS actuation the plant was in mode 1 at approximately 96 percent rated thermal power. At 1500 hours, multiple safety relief valves (SRVs) partially opened due to an invalid reactor pressure vessel (RPV) pressure signal. Control room indications showed two SRVs remained open resulting in a suppression pool temperature rise. Suppression pool cooling was initiated and a plant cooldown to Mode 4 was initiated. <br /><br /> The direct cause of the event was a momentary pressure perturbation limited to the RPV B reference leg that caused the connected transmitters to sense RPV pressure and level changes that resulted in SRV actuation. Corrective actions include revision to plant procedures for operation of the RPV reference legs and associated purge panels, and changes to the time constants for the affected RPV transmitters. <br /><br /> The safety significance of this event is considered to be very small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual actuation of the RPS.
443 | 4431989008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431989008R00.pdf | 1989-06-22 | QR6 | Manual Reactor Trip | [45 empty] | Seabrook | P | WE | SU | 3 | POWER LEVEL - 003%. ON 6/22/89, A MANUAL REACTOR TRIP WAS INITIATED WHILE CONDUCTING A NATURAL CIRCULATION TEST. SHORTLY AFTER TRIPPING THE REACTOR COOLANT PUMPS, AS PER THE NATURAL CIRCULATION TEST PROCEDURE. ONE OF THE CONDENSER STEAM DUMP VALVES BEING USED TO CONTROL TEMPERATURE FAILED TO THE FULL OPEN POSITION. THIS OPEN VALVE CAUSED AN INCREASED STEAM DEMAND WHICH INITIATED AN UNPLANNED PLANT COOLDOWN. THIS COOLDOWN CAUSED THE PRESSURIZER LEVEL TO DECREASE BELOW THE 17% MANUAL TRIP CRITERIA SPECIFIED IN THE STARTUP TEST PROCEDURE. DUE TO THE UNIT SHIFT SUPERVISOR'S MISINTERPRETATION OF THE TEST PROCEDURE TRIP CRITERIA. THE PLANT WAS NOT MANUALLY TRIPPED AT THAT TIME. WHEN THE STEAM DUMP VALVE, MS-PV-3011. WAS CLOSED, THE PREVIOUSLY DECREASING PRESSURIZER PRESSURE AND PRESSURIZER LEVEL BEGAN INCREASING. BOTH PRESSURIZER PRESSURE AND LEVEL CONTINUED TO INCREASE UNTIL THE PRESSURIZER PRESSURE, AT 2310 PSIG, APPROACHED THE TEST PROCEDURE MANUAL TRIP CRITERION OF 2340 PSIG AND A MANUAL REACTOR TRIP WAS INITIATED AT 12:36PM. THE CAUSE OF M8-PV-3011 FAILING TO THE FULL OPEN POSITION HAS BEEN DETERMINED TO BE THE POSITIONER FEEDBACK LINKAGE WHICH BECAME DISCONNECTED DURING THE TEST. CORRECTIVE ACTION FOR THIS VALVE AND SIMILAR VALVES IS BEING SCHEDULED. THE STARTUP TEST PROGRAM WILL BE REVISED TO REQUIRE THAT A MORE COMPREHENSIVE PRE-TEST BRIEFING BE PROVIDED AND A DETERMINATION BE MADE OF WHICH TESTS REQUIRE SPECIAL CLASSROOM AND REVIEWED.
443 | 4431990015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431990015R01.pdf | 1990-06-20 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 30 | On June 20, 1990, at 4:39 p.m., while in MODE 1 at 30% reactor power and increasing, a turbine-generator trip with reactor trip occurred. The trip was initiated by the actuation of a main generator ground fault relay designed to protect the last 5% of generator windings from a ground fault. An Emergency Feedwater (EFW) actuation also occurred due to low-low steam generator narrow range level. Steam generator "A" EFW isolated due to high EFW flow one minute into the event. <br /><br /> The turbine-generator tripped due to the ground fault relay actuating. All the applicable trips and interlocks associated with a turbine generator, reactor trip and feedwater isolation functioned as designed. Parameters associated with the reactor were reviewed by the on-shift reactor engineer and determined to be normal. The EFW isolation occurred when the turbine driven pump came up to full speed, thus creating a situation where both EFW pumps were supplying feedwater simultaneously. <br /><br /> The root cause for the actuation of the ground fault relay has been determined to be incorrect relay settings provided by the vendor. A Minor Modification (MMOD) will be issued to revise the relay settings and bypass the trip function of the relay. Additional corrective actions include revising the EFW isolation setpoint as well as reviewing and updating emergency operating procedures.
443 | 4431990018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431990018R00.pdf | 1990-07-05 | QR8 | Spurious Reactor Trip | [45 empty] | Seabrook | P | WE | PO | 75 | On July 5, 1990, at 4:29 P.M., while in MODE 1 at 75% reactor power, a reactor trip with turbine trip occurred. The trip was initiated by a main steam low Electrohydraulic Control (EHC) oil pressure signal. A Main Feedwater Isolation also occurred due to the sensitivity of the steam generator level trip signals to pressure pulses. <br /><br /> The reactor tripped due to contact closure of the EHC oil pressure switches satisfying the two out of three logic for reactor trip on low EHC oil pressure. All applicable trips and interlocks associated with the reactor trip and feedwater isolation functioned as designed. All operator actions were determined to be appropriate. <br /><br /> The root cause has been determined to be excessive vibration of the EHC pressure switches due to their mounting location. This vibration caused the switches to close even though adequate EHC oil pressure existed. Corrective actions include relocation of the pressure switches to an area with less vibration as well as monitoring the pressure switches in their new locations upon the plant's return to power operations. Additionally, a design change to eliminate the effects of the pressure pulses on the steam generator level trip signals will be evaluated. <br /><br /> This is the first event of this type at Seabrook Station.
443 | 4431990022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431990022R00.pdf | 1990-08-22 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On August 22, 1990 at 9:19 a.m., EDT, while in MODE 1 at 100% reactor power, a turbine- generator trip with reactor trip occurred. The trip was initiated by an apparent loss of voltage on the Electrohydraulic Control (EHC) 24 volt DC bus during troubleshooting activities. A Main Feedwater Isolation also occurred subsequent to the reactor trip. <br /><br /> A work request was initiated to perform circuit checks in the Early Valve Actuation (EVA) circuitry due to inconsistent operation of the EVA's TEST INTERLOCK light located on the Main Control Board (MCB). Subsequent to initial testing at the MCB, it was decided to continue the testing locally at the EHC cabinet. Two test leads were used to simulate the test signal and to supply 24 volt DC power to the EVA circuit. After the second application of the test leads, a voltage drop occurred on the 24 volt DC trip bus resulting in a turbine-generator trip with reactor trip. <br /><br /> The root cause for the loss of voltage on the EHC 24 volt DC bus could not be conclusively determined, although a contributing factor was the troubleshooting activity associated with the EVA circuit. Personnel error in applying the test leads has not been ruled out but is considered unlikely. New Hampshire Yankee will carefully evaluate all future EHC maintenance activities performed during power operation in order to minimize challenges to plant systems. Additionally, as part of our Trip Avoidance Program, each EHC maintenance activity during power operation will be reviewed on a case-by-case basis, prior to the initiation of work in the field. <br /><br /> With respect to feedwater isolation, a design change has been initiated to install an electronic circuit which will eliminate the effects of the pressure pulses on the steam generator level trip signals.
443 | 4431990025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431990025R00.pdf | 1990-11-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Seabrook | P | WE | PO | 100 | On November 9, 1990, at 2:31 p.m. EST, while in Mode 1 at 100% power, a reactor trip with turbine-generator trip occurred. The trip was initiated by a steam generator low-low narrow range level signal. <br /><br /> The initiating event was caused by fatigue failure of a control air pipe nipple. This nipple connects the air booster relay to the valve actuator for feedwater flow control valve, 1-FW-FCV-520. Following the failure of the nipple, valve 1-FW-FCV-520, failed closed as designed, due to a loss of control air. The valve closure resulted in a loss of feedwater to the "B" steam generator. A reactor trip occurred as designed, when the steam generator water level dropped below the low-low narrow range level setpoint. Subsequent to the reactor trip, a Main Feedwater Isolation occurred due to high-high steam generator water level signal spikes. In addition, an Emergency Feedwater Actuation occurred as designed, due to the loss of feedwater to a steam generator. <br /><br /> The root cause of the event has been determined to be vibration induced fatigue failure of the pipe fitting due to a less than optimal design location. Corrective actions include relocation of the air booster relays for all four feedwater flow control and bypass valves. In addition, a walkdown of the secondary side will be performed during 100% power operation to identify similar control air arrangements that may be affected by excessive vibration. <br /><br /> This is the first event of this type at Seabrook Station.
443 | 4431991001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431991001R00.pdf | 1991-02-12 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Seabrook | P | WE | PO | 100 | On February 12, 1991, at 8:22 a.m. EST, a turbine-generator trip with a reactor trip occurred while the plant was at 100% power. The trip was initiated by a loss of Electrohydraulic Control (EHC) system pressure. A Main Feedwater Isolation and an Emergency Feedwater Actuation also occurred subsequent to the trip. <br /><br /> Prior to the event, 480 volt AC unit substation ED-US-14 was cross connected to unit substation ED-US-21 in preparation for various electrical maintenance tasks on the primary breaker, secondary breaker and transformer for ED-US-14. Approximately twenty-five minutes following the cross connection, the secondary breaker for ED-US-21 tripped due to the energization of two large cyclic loads, the turbine building crane and the guardhouse megatherm tank heaters. Consequently, power was lost to both EHC pumps causing a loss of EHC system pressure that resulted in a turbine-generator trip with a reactor trip as designed. <br /><br /> The root cause has been determined to be an inadequate procedure. A contributing cause was inadequate training. To prevent recurrence, operating procedures, maintenance Repetitive Task Sheets and planning and scheduling procedures will be revised to provide additional controls to ensure that the overall connected load is formally evaluated and controlled prior to cross connecting unit substations. The lessons learned from this event will be discussed with all operating crews. Additionally, a Training Development Recommendation (TDR) will be written to address failure mode and consequence thought processes during abnormal system alignments. <br /><br /> This is the first event of this type at Seabrook Station.
443 | 4431991002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431991002R00.pdf | 1991-03-30 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X | [30 empty] | X |  |  |  | Seabrook | P | WE | PO | 100 | POWER LEVEL - 100%. On March 30, 1991 at 11:48 a.m., a manual reactor trip was initiated while the plant was at approximately 50% power. The reactor trip was initiated due to a turbine runback coincident with a loss of the condenser steam dump valves. <br /><br /> While the plant was at 100% power, an electrical fault occurred in the transformer section of 480 volt AC unit substation EDE-US-52 resulting in a loss of all loads powered from this bus. Consequently, a turbine runback was initiated by a loss of Generator Stator Cooling (GSC) system control power. Additionally, control power to the condenser steam dump valves was lost. In response to the loss of the condenser steam dump valves, all four atmospheric steam dump valves and several steam generator safety valves automatically actuated. <br /><br /> Following the reactor trip and turbine trip, a Main Feedwater Isolation and an Emergency Feedwater actuation occurred as designed. Additionally, upon restoration of power, the Control Room Emergency Air Cleanup and Filtration Subsystem actuated as designed. <br /><br /> The root cause for the electrical fault has been determined to be a turn-to-turn fault on one phase of the 4160/480 volt AC transformer's primary winding. The transformer for the bus was replaced. Additionally, this event will be discussed with operations personnel during requalification training. An emphasis will be placed on the reportability requirements pursuant to 10 CFR 50.72 regarding ESF actuations. <br /><br /> This is the first event of this type at Seabrook Station.
443 | 4431991006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431991006R00.pdf | 1991-06-02 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On June 2, 1991, at 6:47 a.m., a turbine generator trip with a subsequent reactor trip occurred while the plant was at 100% power. The trip was initiated by an inadvertent actuation of the turbine mechanical overspeed protection system. A Main Feedwater Isolation also occurred subsequent to the trip. <br /><br /> During a weekly turbine mechanical overspeed trip test, the oil trip solenoid valve (OTSV) did not return to its original position. Maintenance personnel removed one of the solenoid valve housing covers to conduct a visual verification of the actual position of the OTSV and its limit switch. While the housing cover was removed the limit switch assembly base plate and bracket dropped away from the housing. Consequently, the limit switch changed state causing the mechanical lockout solenoid valve to reset. A turbine trip immediately resulted since the OTSV was still supplying bearing oil to actuate the mechanical overspeed trip lever assembly. <br /><br /> In response to the turbine trip and reactor trip, the condenser steam dump valves actuated as designed. However, two steam dump valves remained open longer than expected. <br /><br /> The cause of the oil trip solenoid valve to remain in the test position was the presence of corrosion products inside the valve body.<br /><br /> The oil trip solenoid valve was replaced and subsequently exercised to ensure free movement. Additional corrective actions include the following: 1) Similar solenoid oil valves will be labeled to warn technicians of the trip potential if the cover is removed; 2) The weekly mechanical overspeed trip test procedures were revised to provide additional guidance for unsuccessful tests and to exercise these valves on a weekly basis to prevent corrosion product buildup; 3). The oil resets, oil trip and mechanical trip solenoid valves in the Emergency Trip System will be replaced; 4) An evaluation of previous problems with the condenser steam dump valves was performed and no generic problems were identified.
443 | 4431991008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431991008R00.pdf | 1991-06-27 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Seabrook | P | WE | PO | 100 | On June 27, 1991, at 1:34 p.m., a turbine generator trip with a subsequent reactor trip occurred while the plant was at 100% power. The turbine trip was initiated when two switchyard 345kV circuit breakers tripped open disconnecting the generator from the offsite distribution system. <br /><br /> The event occurred during the performance of a preventive maintenance activity on a breaker failure relay 50BF-2/11(H)! for 345kV circuit breaker 11. As the relay was being returned to service (closure of two knife blade switches), momentary arcing occurred across the contacts. The arcing caused a high speed tripping auxiliary relay to pick up without picking up an associated lock out relay. This partial relay actuation resulted in 345kV circuit breakers 11 and 163 opening without generating a signal to open the Unit Auxiliary Transformer (UAT) supply breakers to unit busses 1 through 6. Because of this, the automatic transfer to the Reserve Auxiliary Transformers (RAT) was prevented, resulting in the automatic starting of both emergency diesel generators. Offsite power remained available to the RATs at all times. A turbine trip occurred within one second of the opening of the 345kV circuit breakers. The turbine trip initiated a reactor trip. Following the reactor trip, natural circulation was established. A Main Feedwater Isolation and subsequent Emergency Feedwater Actuation also occurred. Additionally, a Containment Ventilation Isolation and an actuation of the Control Room Emergency Air Cleanup and Filtration System occurred due to the momentary deenergization of the Emergency Busses. <br /><br /> The root cause has been determined to be a manufacturing error in the relay housing contact block assembly for the breaker failure relay. This breaker failure relay was caution tagged to preclude any further maintenance until it is replaced during the first refueling outage. Other relays similar in design will be inspected to ensure that the correct switch assemblies are installed. In addition, the automatic transfer scheme from the UATs to the RATs and the tripping scheme for the out of step relay will be reevaluated.
443 | 4431991009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431991009R00.pdf | 1991-07-04 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Seabrook | P | WE | PO | 100 | On July 4, 1991, at 8:25 a.m. a reactor trip with a turbine generator trip occurred while the plant was at 100% power. The reactor trip was initiated due to low flow in Reactor Coolant System (RCS), loop 3. <br /><br /> The initiating event was caused by an electrical fault in a bus bar. This bus bar is located in the electrical terminal connector box for Reactor Coolant Pump (RCP) "C". As a result of the electrical fault, RCP "C" tripped due to protective relaying action. A reactor trip with a turbine generator trip occurred as designed, due to low flow in Reactor Coolant System loop 3. Subsequent to the reactor trip, a Main Feedwater Isolation occurred due to high-high steam generator water level spikes. In addition, an Emergency Feedwater Actuation occurred due to the feedwater isolation.<br /><br /> The root cause for the electrical fault was determined to be a quarter-inch bolt that was missing from the top access cover plate of the electrical terminal connector box. Additionally, the gasket for this cover plate had pulled away from the connector box, The missing bolt and loose gasket created a direct path for dirt and moisture to enter the electrical terminal connector box which caused the electrical fault, The top access cover plate is not ordinarily used for maintenance. There is no history of this cover plate ever being unbolted since it was originally installed, therefore, it is believed that the bolt was never installed.<br /><br /> The subject gasket and bolt were replaced and an inspection of the cover plates for the three remaining RCPs was conducted to ensure that all the required bolts were installed and that the gaskets were intact. Additionally, the electrical terminal connector boxes for the three remaining RCPs will be inspected during the first refueling outage for signs of moisture and dirt intrusion.
443 | 4431992017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431992017R00.pdf | 1992-09-07 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Seabrook | P | WE | PO | 12 | On September 7, 1992, at approximately 0030 EDT, during a routine shutdown to begin a refueling outage, at approximately 12 percent power, Steam Generator (SG) level oscillations occurred in one SG. Subsequent level oscillations increased resulting in one SG being overfed, and causing a high SG level alarm. This caused the feedwater to isolate to all four SG's, and it initiated Emergency Feedwater Flow and caused a turbine trip. The loss of feedwater resulted in decreasing levels in all of the SG's. Approximately 2 minutes later, at 0032 EDT, levels decreased until the low-low level setpoint (narrow range) was reached in one of the SG's, which initiated a reactor trip.<br /><br /> There were no adverse safety consequences as a result of this event. All equipment functioned as designed and all operator actions were determined to be appropriate to ensure the safety of the plant and the public. <br /><br /> The root cause for this event was determined to be incomplete communication, in that the operations crew did not effectively communicate and coordinate actions that were taking place on rod control, feedwater control, and turbine control. <br /><br /> Operations personnel will critique this event in order to better understand the factors that led to its occurrence. Additionally, it will be determined whether any recommendations and/or lessons learned should be incorporated into the training process. It is anticipated that these actions will be completed by November 30, 1992. North Atlantic will also review the operator requalification training program to ensure that the trip reduction low power feedwater control methodology training is adequate. It is anticipated that this review will be completed on November 30, 1992.
443 | 4431992024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431992024R00.pdf | 1992-11-27 | QR8 | Spurious Reactor Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On November 27, 1992 at 1519 a reactor trip occurred from 100% power. The reactor trip was due to a spurious signal in the Reactor Coolant System (RC) Overpower Delta T (OPDT) protection circuit. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System and Engineered Safety Feature (ESF) System.<br /><br /> The OPDT protection circuit is designed to provide assurance of fuel integrity under all possible overpower conditions and receives inputs from Delta T and T sub AVG. A two of four coincidence is required to initiate a reactor trip. At the time of the event the RC Loop 1 OPDT channel was in test to perform a setpoint adjustment. With this channel in test actuation of only one of the three remaining channels is required to initiate a reactor trip. At 1519 a spike on the RC Loop 4 OPDT channel made up the required coincidence and initiated a OPDT reactor trip. <br /><br /> The plant response to the trip was normal and no unexpected transients were observed. The cause of the event is attributed to an erratic setpoint voltage being generated by RC Loop 4 OPDT circuit card. This caused the RC Loop 4 OPDT trip setpoint to spike below actual Delta T. As a result of having the Loop 1 OPDT channel in test, when the Loop 4 setpoint signal went below the actual Delta T value the required OPDT reactor trip coincidence was made up and a reactor trip occurred. <br /><br /> Corrective action was to replace the faulty circuit card. There were no adverse safety consequences as a result of this event. At the time of the event the plant was in Mode 1 at 100% power. This is the first event at Seabrook Station where a spurious OPDT signal caused a reactor trip.
443 | 4431992025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431992025R00.pdf | 1992-12-13 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Seabrook | P | WE | PO | 100 | On December 13, 1992, at 0646, a manual reactor trip was initiated from full-power due to the trip of two out of the three Circulating Water System (CW) pumps. The CW pumps, which provide cooling water flow from the Atlantic Ocean to the condensers, tripped due to a higher than normal differential water level across the traveling screens located upstream of the pumps' suction. The high differential water level was caused by debris (primarily seaweed) brought into the CW intake during a storm which began on December 11, 1992. Debris that enters the CW System is removed by traveling screens, During this event the traveling screens tripped on thermal overload allowing debris to increase the differential water level and to trip the CW pumps. <br /><br /> There were no adverse safety consequences as a result of this event. All plant systems functioned as designed in response to the trip and Control Room personnel correctly performed appropriate recovery actions. <br /><br /> The root cause for this event was determined to be tripping of the traveling screens on thermal overload as a result of the traveling screens rapidly cycling between fast and slow speeds.<br /><br /> Corrective actions included installing a Temporary Modification to allow for continuous manual operation of the screens at either slow or fast speed. This eliminated the potential for the aforementioned cycling between fast and slow speed, and hence, the potential for tripping on thermal overload. Additionally, procedure ON1017.02, "Circulating Water Screen Wash Operation," was also reviewed and revised to reflect the Temporary Modification.
443 | 4431993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431993001R00.pdf | 1993-01-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Seabrook | P | WE | PO | 100 | On January 3, 1993 at 0350 a manual reactor trip was initiated from 100% power. The reactor was manually tripped after both main feedwater pumps (MFP) SJ! shutdown due to low suction pressure. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System and Engineered Safety Feature (ESF) System. <br /><br /> On January 2, 1993 a failure of the tube side relief valve SN! for the 25A condensate (CO) heater SJ! required isolation of the heater. Subsequent condensate (CO) and feedwater (FW) level oscillations caused the 21/22 CO heater strings to isolate and the heater bypass valve to open. An incorrect restoration of the 21/22 CO heater strings isolated CO flow to the MFPs which caused both pumps to shutdown due to low suction pressure. With no main feedwater flow to the steam generators, the reactor was manually tripped.<br /><br /> The plant response to the trip was normal and no unexpected transients were observed. The primary root cause of the event was incomplete communications and a secondary root cause was lack of procedural guidance.<br /><br /> Immediate corrective action was to walkdown the CO and FW systems and to review the event with the oncoming operating crews. The 25A tube side relief valve was repaired during the power ascension. To prevent recurrence, Operations Management will continue to emphasize the importance of clear, explicit communications and will develop a procedure to respond to heater drain system transients.
443 | 4431993003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431993003R00.pdf | 1993-01-14 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On January 14, 1993, at 2019, an automatic reactor trip from 100 percent power occurred. This reactor trip followed a turbine trip caused by a phase to ground fault on the 25 kV main generator isolated phase bus (EL). This event was reported to the NRC at 2135 as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), automatic actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System. <br /><br /> The 25 kV main generator isolated phase bus connects the output of the main generator to the three phase transformer used to step up the 25 kV generator output to the 345 kV grid voltage. Each air-insulated phase of the bus is surrounded by a duct assembly that isolates it from the other phases and the surrounding area. The bus conductors are cooled by a bus cooling unit that includes redundant fans and associated backdraft dampers downstream of the fans. A phase to ground fault occurred when a blade from the damper for the running fan became detached from the damper frame and was carried in the air stream, eventually making contact with the bus and a section of air duct. <br /><br /> There were no adverse safety consequences as a result of this event. The plant response to the trip was normal, and all operator actions were determined to be correct. <br /><br /> The damper blade failure was attributed to an inadequate damper blade pivot pin design by the vendor who supplied the bus duct cooling fan units. Corrective action was to redesign the damper assemblies to reduce the possibility of blade failure and to add a heavy debris screen downstream of the damper to prevent migration of loose parts if a future damper failure should occur.
443 | 4431993009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431993009R01.pdf | 1993-05-20 | QL5 | Partial Closure of MSIVs | [45 empty] | Seabrook | P | WE | PO | 100 | On May 20, 1993, at 0437 EDT, a manual reactor trip from 100 percent power was initiated when a main steam [SB] isolation valve (MSIV) closed during MSIV quarterly testing. The trip was followed by a Feedwater Isolation and two Emergency Feedwater actuations. This event was reported to the NRC at 0553 EDT as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System. <br /><br /> During MSIV quarterly testing, the MSIVs are alternately stroked to ten percent closed and then reopened. However, one MSIV failed to return to the open position when the ten percent limit was reached, and instead continued to close. The reactor was manually tripped when the narrow range level in the affected steam generator was twenty-two percent and decreasing. There were no adverse safety consequences as a result of this event. <br /><br /> The cause of the MSIV malfunction was determined to be debris lodged in a hydraulic solenoid valve that allowed the hydraulic pressure keeping the MSIV open to bleed off, resulting in the MSIV drifting closed.
443 | 4431993012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431993012R00.pdf | 1993-07-27 | QR8 | Spurious Reactor Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On July 27, 1993, at 0814 an automatic reactor trip from 100 percent power occurred. This reactor trip was initiated when an electrical fault in the Train 'A' Solid State Protection System (SSPS)[JG] cabinet resulted in a loss of power to the undervoltage (UV) coil for the Train 'A' reactor trip breaker. The deenerigization of the UV coil caused Reactor Trip Breaker (RTB) 'A' to open resulting in a reactor trip. Primary plant response was normal with expected Engineered Safety Feature (ESF) actuations (Emergency Feedwater System [BA] actuation on Steam Generator LO-LO level and Feedwater System [SJ] Isolation in response to the reactor trip). At 0939 EDT on July 27, 1993 North Atlantic made a four-hour notification to the NRC pursuant to 10CFR50.72(b)(2)(ii) since these events resulted in a Reactor Protection System (RPS) actuation and ESF actuations. <br /><br /> There were no adverse safety consequences as a result of this event. Plant equipment functioned as designed in response to the reactor trip and operator actions were determined to be correct in response to the reactor trip. At no time during the event was there any adverse impact on the health and safety of plant employees or the public.<br /><br /> The root cause for this event was determined to be a faulty lamp test assembly in the logic test panel of the Train A SSPS cabinet. The lamp test assembly introduced a short from the SSPS auctioneered 48 VDC bus to logic ground when performing a lamp test. <br /><br /> Short term corrective actions completed prior to reactor startup included replacing the lamp test socket and test circuit driver card. Also a visual inspection of the remaining Train A and B SSPS lamp test sockets was performed to verify pin separation. Long term corrective actions include performing a failure analysis on the lamp test socket and to evaluate the SSPS test circuit to determine whether the potential for the failure of a single lamp test socket resulting in a reactor trip can be eliminated.
443 | 4431993018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431993018R00.pdf | 1993-09-22 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Seabrook | P | WE | PO | 100 | On September 22, 1993, at 0521 EDT, an automatic reactor trip from 100 percent power occurred. This trip was initiated by a reactor coolant pump (RCP) undervoltage reactor trip signal, which was caused by degradation of the main generator [TL] rotor field. Primary plant response was normal with expected Engineered Safety Feature (ESF) actuations. This event was reported to the NRC at 0638 EDT on September 22, 1993 as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System.<br /><br /> The voltage and current used to develop the magnetic field on the main generator rotor are supplied by a synchronous alternating current exciter directly coupled to the main rotor shaft. The magnitude of the exciter output voltage controlled by varying the exciter field strength. This is accomplished by applying a direct current voltage to two collector rings located on one end of the exciter rotor through six graphite brushes. <br /><br /> The cause of the loss of main generator rotor field was the degradation of the exciter output voltage due to arcing at the exciter brush/collector ring interface. This arcing eventually caused a degradation of electrical contact between the brushes and the collector ring, which led to a degrading exciter field. The degrading exciter field in turn resulted in a degrading main generator field and the Station undervoltage conditions that generated the RCP undervoltage reactor trip signal. <br /><br /> There were no adverse safety consequences as a result of this event.
443 | 4431994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431994001R01.pdf | 1994-01-25 | QL5 | Partial Closure of MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Seabrook | P | WE | PO | 100 | On January 25, 1994, at 0934 an automatic reactor trip from 100 percent power occurred when a main steam [SB] isolation valve (MSIV) closed during MSIV quarterly surveillance testing. The reactor trip, which was due to low-low narrow range steam generator level, was followed by a Safety Injection and Main Steam Isolation. This event was reported to the NRC at 1000 on January 25, 1994 as a one-hour notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) an Engineered Safety Feature (ESF) System. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The physical cause of the MSIV malfunction was determined to be a combination of contaminated hydraulic fluid, a sticking main dump valve, and other related hardware issues. Collectively, these factors allowed the hydraulic pressure to bleed off and cause the MSIV to continue to close during testing. A root cause analysis was performed at two levels: the first to evaluate MSIV hardware specific issues and a second to evaluate organizational and programmatic performance. The root causes for this event include inadequate failure analysis of previous MSIV events, an inadequate preventative maintenance program for the MSIVs, and inadequate workmanship and quality assurance practices when the MSIV hydraulic subsystems were rebuilt in 1991. <br /><br /> North Atlantic has taken actions to correct the hardware specific MSIV conditions. North Atlantic will implement actions to address the root and contributing causes of this event.
443 | 4431995002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431995002R00.pdf | 1995-06-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Seabrook | P | WE | PO | 100 | On June 18, 1995 at 1827 a manual reactor trip was initiated from 100% power. The reactor AB! was manually tripped after power was lost to both turbine electro-hydraulic control (EHC) TG! pumps. This event was reported to the NRC pursuant to 10 CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) system. There were no adverse safety consequences as a result of this event. <br /><br /> Prior to the reactor trip, Unit Substation US-14 EA! was cross-tied to Unit Substation US-21 to restore power to two motor control centers, after the primary feeder breaker on US-21 tripped open due to a ground caused by a failed surge arrester. The US-14 transformer tripped, while cross-tied to US-21, due to an unrelated end-of-life fault (primary to secondary) on the US-14 13.8 kV non-safety related transformer. This resulted in the loss of power to the EHC pumps. The loss of power to buses US-14 and US-21 complicated the secondary plant trip response. <br /><br /> The root cause of this event was determined to be an inadequate design for the 13.8 kV non-safety related transformer. <br /><br /> North Atlantic has taken actions to correct the transformer and surge arrester conditions. These include replacing trip critical 13.8 kV non-safety related transformers, developing further guidance regarding cross-tying electrical buses and replacing surge arresters.
443 | 4431996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431996001R00.pdf | 1996-01-27 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On January 27, 1 996 at 0945 an automatic reactor trip occurred at 1 00% power. pressure. The turbine combined intercept valves closed in response to the insertion of a fast close signal due to position mismatch. Concurrently, the turbine control valves closed due to the insertion of a slow close signal. The resulting turbine load rejection caused the Reactor Coolant System temperature and pressure to increase. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System and Engineered Safety Feature system. There were no adverse safety consequences as a result of this event. <br /><br /> The turbine combined intercept valve and control valve closure was caused by a failure of a circuit card in the turbine speed control circuit in the Electro-Hydraulic Control system. This resulted in a large speed error signal and valve close signal to the combined intercept valves and control valves.<br /><br /> The root cause of this event was determined to be random failure of an Electro-Hydraulic Control speed control circuit card. <br /><br /> North Atlantic has taken immediate corrective actions including replacing both of the Electro-Hydraulic Control speed control circuit cards. Long term actions include performing several evaluations related to the design and handling of Electro-Hydraulic Control circuit cards.
443 | 4431997008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431997008R00.pdf | 1997-05-10 | QR8 | Spurious Reactor Trip | [45 empty] | Seabrook | P | WE | SU | 8 | On May 10, 1997, at 0211 EDT during a routine shutdown to begin the fifth refueling outage, an automatic reactor trip and subsequent feedwater isolation occurred at approximately 8% Rated Thermal Power (RTP). The reactor trip was initiated by one of two Intermediate Range Neutron Flux Instrumentation (IR NI)[IG] channels. The high flux trip signal (set for 25% RTP) occurred when the IR NI high flux trips were automatically unblocked at 8% reactor power. The IR NI trip bistable for Channel N35 had not reset prior to unblocking the IR NI trips below the P-10 reset setpoint of 8% reactor power and thus initiated a trip signal when unblocked. Both IR NI channels, N35 and N36, had been affected by a significant shift in radial power distribution and channel N35 had experienced power supply degradation problems during the operating cycle. The cumulative effect of these two factors on the IR NI channels caused the trip signals to stay actuated below the power levels at which they should have normally reset. The four power range nuclear instruments indicated approximately 8% reactor power just prior to the trip. The IR NI reactor trip bistables should have reset at 12.5% RTP. This event was reported to the NRC at 0321 May 10, 1997, as a non-emergency event pursuant to 10CFR50.72(b)(2)(ii), automatic actuation of the Reactor Protection System [JC] and Engineered Safety Feature System [JE].The causes of this event are: 1) the inadequate monitoring and trending of the intermediate range channels power supplies, 2) a collective lack of knowledge about the effects that changing IR NI detector currents have on IR NI reactor trip and reset setpoints, and 3) inadequate procedural guidance in the plant shutdown procedure regarding verification that the intermediate range neutron flux trips were reset prior to decreasing power below the P-10 setpoint.Corrective actions include improved monitoring of IR NI channels, enhanced plant shutdown procedures and operator and technical training on this event.
443 | 4431998014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4431998014R00.pdf | 1998-12-22 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On December 22, 1998, at 0827 EST, an automatic reactor trip occurred while at 100 percent power. The reactor trip was initiated due to a turbine trip which occurred upon loss of load when the main generator breaker was opened as a result of a pole disagreement in 345 kV breaker 163. Bus 4 failed to transfer from the Unit Auxiliary Transformer to the Reserve Auxiliary Transformer. Additionally, a voltage transient on Buses 5 and 6 caused some safety related and non-safety related equipment to trip or stop.This event was caused by an auxiliary switch linkage pin in breaker 163 that fell out preventing the linkage from actuating the auxiliary contact thereby causing the pole disagreement when the breaker was opened.The breaker 163 auxiliary switch linkage pin that fell out was reinstalled with new retaining clips. The eleven remaining auxiliary switch link pins and associated clips were verified to be installed on breaker 163. The remaining seven 345 kV breakers were visually inspected and it was verified that the auxiliary switch linkage pins and their associated clips were in place. The 345 kV breakers will be inspected periodically to ensure the auxiliary switch linkage pins and their associated clips are in place.
443 | 4432000004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432000004R00.pdf | 2000-06-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Seabrook | P | WE | PO | 100 | On June 26, 2000 at approximately 1851 with the reactor operating at 100 percent power (mode 1), the "A" Main Feedwater Pump (1FW-P-32A) tripped. The trip of 1FW-P-32A resulted in a setback to 55 percent power. Approximately 1 minute and 25 seconds after the trip of 1FW-P-32A, plant operators received a low level alarm on the "C" steam generator due to the inability of the "B" Main Feedwater Pump (1FW-P-32B) to maintain feed water inventory to the steam generators in proportion to the reactor power level. Shortly thereafter, a manual reactor trip was initiated by plant operators as steam generator levels approached the low-low level trip setpoint. This event (Event Number 37117) was initially reported to the Nuclear Regulatory Commission on June 26, 2000 at 1923 pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is additionally reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(iv). 1FW-P-32A tripped as a result of a momentary steam generator High-High level signal originating from the solid state protection system (SSPS). A number of corrective actions have been completed and identified. There were no adverse safety consequences as a result of this event. Plant equipment functioned as designed and operator actions were determined to be appropriate. This is the first event of this type reported within the past two years.
443 | 4432001002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432001002R00.pdf | 2001-03-05 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Seabrook | P | WE | PO | 100 | On March 5, 2001 at 2324, with the plant at 100% power, Seabrook Station experienced a plant trip during a severe winter storm. Prior to this event, the plant was experiencing difficulty with the off site power supplies to the plant. At 2238 on March 5, 2001, the 345 kV breakers for the Scobie line opened disabling one of the three off-site supplies. At 2248 on March 5, 2001, the 345 kV breakers for the Newington line opened disabling the second of three off-site lines. At 2324 on March 5, 2001, off-site 345 kV electrical supply via the Newington line was restored. However, the breaker alignment prevented this line from powering station buses. Shortly thereafter, the Tewksbury line tripped. Almost immediately after the trip of the Tewksbury line, a reactor trip occurred.An unusual event was declared on March 5, 2001 at 2336 since the supply of off site power was not considered reliable due to the adverse weather conditions. The unusual event was terminated on March 7, 2001 at 1046 when offsite power was restored to emergency Bus 5. The State of New Hampshire, the Commonwealth of Massachusetts and the Nuclear Regulatory Commission were notified of the event.The cause of the event is power arc flashover from the line to ground across the "B" phase 345kV bushings that connect the sulphur hexafluoride (SF6) gas insulated 345 kV bus sections to the 345 kV overhead lines. The power arc flashover was due to the severe weather conditions and subsequent buildup of snow on the "B" phase bushings, which exceeded their capability. The consequences of this event were minimal. However, certain components did not operate as expected. Corrective actions have been identified to prevent recurrence.
443 | 4432001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432001003R00.pdf | 2001-10-15 | QR3 | Reactivity Control Imbalance | [45 empty] | Seabrook | P | WE | PO | 100 | On October 15, 2001 at 1:07 PM, with the plant at 100% power, North Atlantic Energy Service Corporation (North Atlantic) experienced an automatic reactor trip. The reactor trip occurred when rod N11 dropped into the reactor core and a power range high flux rate trip (negative) signal was initiated. At the time of the rod drop event, rod N11 was being moved out from step 229 to step 231 during the performance of a quarterly rod operability check. The plant systems functioned properly during the initial reactor trip and subsequent transition to Mode 3, with two minor system issues that were not the result of the event. Operator response to the automatic trip was appropriate with no human performance issues identified.The rod drop occurred while moving rod N11 out at step 230 when the stationary gripper did not fully engage prior to the movable gripper releasing. The root cause of the N11 Dropped Rod Event is particulate deposits in the rod drive housing and/or on the drive rod. These deposits inhibited the stationary gripper engagement on the drive rod.A four hour and eight hour notification to the Nuclear Regulatory Commission (NRC) was made pursuant to the requirements of 10CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The event notification was 38390.A change to Control Rod Drop Testing procedure will be made to obtain acceptable coil current traces for all control rods during the performance of rod drop testing that is preformed at the end of the refueling outage.This License Event Report is being submitted pursuant to the requirements of 10CFR 50.73(a)(2)(iv)(A).
443 | 4432003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432003002R00.pdf | 2003-10-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Seabrook | P | WE | PO | 100 | At approximately 1948 hours on October 31, 2003, with the plant operating in Mode 1 at 100% power, Seabrook Station experienced an automatic reactor trip following a transfer of the "A" Main Feed Pump (MFP) from the "Manual" to "Automatic" mode of operation. At the time of the reactor trip, plant personnel were troubleshooting the Emergency DC Lube Oil Pump (DC Pump) for the "A" MFP. In order to assist in the performance of troubleshooting activities, the "A" MFP slave controller was placed in the manual mode of operation. When the slave controller was returned to the automatic mode of operation, the "A" MFP control valves closed and the pump coasted down. Due to the reduced feedwater flow, steam generator levels decreased over an approximately forty-eight second period until an automatic reactor trip occurred when the lo-lo level setpoint (25%) was actuated.The cause of the reactor trip was a loss of the "A" MFP when its controller was placed in automatic mode of operation from the manual mode of operation. The loss of the "A" MFP was due to a degraded circuit board/component in the "A" MFP MDT-20 Governor Speed Controller. There were no adverse safety consequences as a result of this event. Plant systems responded normally as a result of the reactor trip.Corrective action was to replace the failed circuit board.
443 | 4432005006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432005006R00.pdf | 2005-05-01 | QR6 | Manual Reactor Trip | [45 empty] | Seabrook | P | WE | PO | 17 | On May 1, 2005 at 1109, Seabrook Station initiated a manual reactor trip from 17% power. During initial start-up of the main turbine following refueling outage 10, the turbine automatically tripped at approximately 1045 rpm when turbine vibration exceeded the trip setpoint of 12 mils. Following the turbine trip, vibration levels continued to increase and the operators manually tripped the reactor in preparation for breaking condenser vacuum to slow the turbine. Condenser vacuum was broken until the high vibration condition cleared and was then subsequently restored to provide a secondary heat sink. The emergency feedwater system actuated on low steam generator levels following the reactor trip. The cause of the turbine high vibration condition was a turbine rub (contact between the rotor and stationary components in the turbine). The rub creates a hot spot on the rotor that causes the shaft to bow, which will change the center of mass of the rotor. Once a rub starts it will typically spread to multiple locations as the rotor bows and vibration levels increase. Corrective action will be taken to add a precaution to operating procedures to minimize thermal distortion and rapid changes in steam flow through the Turbine to reduce the possibility of initiating a rub.
443 | 4432008001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432008001R00.pdf | 2008-01-19 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | At 2302 on January 19, 2008 while operating in mode 1 at 100% power, Seabrook Station experienced aturbine trip and subsequent reactor trip due to a fault on 345kV bus 3. This bus is located between thegenerator step-up transformer and the switchyard circuit beakers. The fault initiated a 345 kV bus lockout, which in turn tripped the main turbine and the circuit breakers associated with the unit auxiliary transformers (UAT), which normally supply the plant's 4,160 volt and 13,800 volt buses. The loss of the UATs initiated an automatic transfer of the plant buses to the alternate 345kV power source via the reserve auxiliary transformers. The transient caused a loss of all four operating reactor coolant pumps (RCP) for approximately one hour. Due to the unavailability of presssurizer spray with all RCPs stopped, the pressurizer power-operated relief valve automatically opened as designed to control reactor coolant system pressure. The operators restored normal pressurizer spray following the restart of one RCP at 0009 on January 20, 2008.The cause of the 345kV bus fault was a failure of the operating shaft in the manually-operated disconnectswitch for 345kV bus 3. On January 22, the plant entered mode 5 to repair 345kV bus 3 and returned to service on January 31, 2008. No adverse safety consequences resulted from this event.
443 | 4432011002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432011002R00.pdf | 2011-10-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Seabrook | P | WE | PO | 100 | At approximately 1226 on October 6, 2011 with the plant operating in Mode 1 at 100% power, Seabrook experienced a plant trip on low steam generator water levels following loss of an operating main feed pump. The main feed pump tripped on low suction pressure while restoring a condensate pump to service following maintenance. During restoration of the pump, air entered the condensate system and caused a drop in condensate pump discharge pressure, which resulted in a low pressure condition at the suction of the main feed pump. The trip of the main feed pump on low suction pressure initiated a turbine setback; however, with reduced feedwater flow, steam generator levels decreased to the low level reactor trip setpoint. The automatic systems functioned as designed. The emergency feedwater system automatically actuated and recovered steam generator levels. No adverse consequences resulted from this event.The cause of this event was the lack of a procedure for restoring a condensate pump to service during operation at power. The corrective action revised the operating procedure to provide instructions for filling and venting a condensate pump following maintenance.
443 | 4432012003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432012003R00.pdf | 2012-09-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Seabrook | P | WE | PO | 85 | On September 14, 2012 at 8:25 pm while operating at approximately 85% power, Seabrook Station experienced an automatic reactor trip on low steam generator (SG) water level. The failure of a printed circuit board in the 7300 process control system caused the feedwater regulating valve for SG-C to close. As a result, the water level in SG-C decreased to the low level trip setpoint and initiated an automatic reactor trip. The emergency feedwater system actuated on low SG level, and plant equipment functioned as expected. No adverse consequences resulted from this event.The root cause of the event was the failure of an internal component on a printed circuit board (manual nuclear tracking driver board) in the 7300 control system. The corrective actions included replacing the failed circuit card and three additional cards in the same instrument loop.
443 | 4432014001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432014001R00.pdf | 2014-04-01 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Seabrook | P | WE | PO | 15 | On April 1, 2014 at 00:26 while operating at approximately 15% power following turbine shutdown and removal of the main generator from service, Seabrook Station experienced an automatic reactor trip on reactor coolant two loop loss of flow. The loss of flow was the result of the unexpected closure of the main generator breaker (MGB) "B" phase resulting in 345KV bus 6 de-energizing to isolate the generator breaker. All buses transferred to the reserve auxiliary transformers as designed; however, a slight delay in the automatic transfer for bus 1 resulted in two reactor coolant pumps (RCP) tripping. The RCPs tripping resulted in an automatic reactor trip due to reactor coolant loop low flow. The emergency feedwater system actuated on low SG level, and plant equipment functioned as expected. No adverse consequences resulted from this event.<br /><br /> The root cause is inadequate procedural guidance as the procedure used for MGB operation lacked appropriate information regarding local/remote selector switch position, mitigating actions, and minimizing time with MGB protection defeated. Corrective action is to revise the procedure to add controls to communicate potential risk while switch is in the local position, ensure the use of guarded equipment controls, and minimize the time spent with the switch in local without breaker lock rods installed.
443 | 4432016001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432016001R00.pdf | 2016-03-02 | QR5 | Turbine Trip | [45 empty] | Seabrook | P | WE | PO | 100 | On March 2, 2016 at 0253 while operating at 100% power, Seabrook Station experienced an automatic reactor trip due to a turbine trip. A failure of inverter ED-I-11 caused a voltage transient in the power supplies for the Turbine Control System (TCS). The TCS is designed with redundant inverters so that the loss of one inverter will not cause a system failure. However, during this event, the inverter failure caused a voltage increase which exceeded the voltage limits of the TCS power supplies causing them to momentarily shut down. Loss of the TCS power supplies initiated an automatic turbine trip signal, which in turn actuated an automatic reactor trip as designed. Other plant equipment functioned as expected and no adverse consequences resulted from this event. <br /><br /> The direct cause of the event was a failure of inverter ED-I-11 which resulted in an overvoltage condition to the turbine control system. At this time, the cause of the failure of the inverter has not been determined. If additional troubleshooting identifies a cause, this LER will be supplemented. Immediate corrective action was implementation of a temporary modification to energize the power panel normally fed by ED-I-11 to eliminate single point vulnerability. Planned corrective actions are to continue troubleshooting and repair of inverter ED-I-11, install overvoltage protection for the TCS cabinets and upgrade the TCS power supplies to higher voltage rated units.
443 | 4432017001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4432017001R00.pdf | 2017-04-29 | QR6 | Manual Reactor Trip | [45 empty] | Seabrook | P | WE | PO | 12 | On April 29, 2017 at 18:44, the Reactor was manually tripped by the operators at approximately 12% power in response to a feedwater isolation caused by High Steam Generator (SG) Level on the 'B' SG. The feedwater isolation signal P-14 was automatically actuated at 18:43 when the 'B' SG level reached the setpoint of 90.8% narrow range level. The plant was being started up following the major work performed for Refueling Outage 18. No adverse consequences resulted from this event. <br /><br /> Post-trip investigation revealed that FW-LT-502-V1L (the Variable leg pressure isolation for FW-LT-502) had not been restored to the required open position during routine instrument line filling and venting. On April 26, 2017, l&C performed backfilling of the reference legs on multiple steam generator level channels, including FW-LT-502, the 'B' SG wide range level instrument. FW-LT-502-V1L not being restored to the open position caused the 'B' SG wide range indication to respond slowly to level changes resulting in overfeeding the 'B' steam generator. The cause of the event was determined to be failure of the l&C technician to properly implement maintenance fundamentals during the performance of restoration of FW-LT-502. Individual performance was corrected. A contributing cause was determined to be improper characterization or SG level backfill activity as skill-of-the-craft. Planned corrective actions include development of a maintenance procedure to provide specific step-by-step instructions.
445 | 4451990009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990009R00.pdf | 1990-04-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Comanche Peak 1 | P | WE | PO | 7 | At approximately 1715 CST on April 21, 1990, while dusting the main control board, the Reactor Operator accidentally bumped switch 1/1-N-33B and reset Source Range Channel N31 which had been previously bypassed for power operation. Re-energizing the Source Range high voltage power supply while operating at 7 percent power exceeded the reactor the setpoint and generated a reactor trip signal. The reactor trip coincident with a low-average Reactor Coolant System (RCS) temperature generated a Feedwater Isolation signal. During reactor trip recovery, the Auxiliary Boiler failed to start due to a faulty igniter assembly and resulted in a slight decrease in RCS Temperature prior to the plant being stabilized in Mode 3. <br /><br /> Corrective actions for this event included the removal of cleaning brushes from the Control Room and the suspension of all control board cleaning until an alternative method is implemented. Additionally, a plexiglass cover has been placed over the involved switch until and evaluation is completed to determine if the switch is overly sensitive and why bumping the switch caused the Source Range Channel to reset.
445 | 4451990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990013R00.pdf | 1990-05-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 48 | At approximately 1504 CDT on May 9, 1990, while using a procedure, written for Mode 5 Cold Shutdown, or Mode 6 Refueling, to calibrate a feedwater pump discharge pressure transmitter, jumpers were installed across the feedwater pump speed controllers while they were being used to maintain feedwater pump speed during Mode 1 Power Operation. Installation of the jumpers caused a coastdown of the feedwater pumps, resulting in a loss of feedwater flow and reduction of steam generator water levels. An automatic reactor trip occurred when the Steam Generator Water Level Low-Low Trip Setpoint was reached. Plant recovery was completed without further incident or unexpected findings. <br /><br /> The root cause of the event has been determined to be an inadequate review and approval process for certain procedure changes. As corrective actions for this event, a procedure revision will ensure technical reviews and operational impact assessments are performed for mode applicability interpretations. Generic corrective actions will increase sensitivity to the impact that non-safety components can have on an operating plant. The Single Point Failure Analysis, which identifies these components, will be utilized programmatically.
445 | 4451990017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990017R00.pdf | 1990-05-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 43 | On May 27, 1990, at 0126 while performing Steam Generator Atmospheric Relief Valve (ARV) capacity testing, a Main Feedwater Flow Control Valve (FCV) failed closed. This resulted in reduced feedwater flow and decreasing Steam Generator (SG) No. 3 water level. The Operator closed the ARV, which was open for test purposes, and started to manually ramp down the main turbine to reduce reactor power. The Operator then opened the bypass flow control valve around the failed closed FCV, but the SG water level continued to decrease. At 0128, when No. 3 SG water level reached approximately 30 percent (automatic reactor trip is at 28 percent SG water level), the operator manually tripped the reactor. All other plant systems operated properly.<br /><br /> The cause of the event was the failure of a solenoid valve coil, associated with No. 3 SG FCV, due to rain water intrusion (FCV's are located outside). A temporarily removed cover allowed water to enter a junction box then drain via conduit to the solenoid coil housing. <br /><br /> Corrective action included the replacement of the failed solenoid coil and inspection of the other solenoids for water/moisture intrusion. An evaluation will determine if additional critical components exist in a similar configuration. Guidance for the conduct of outdoor maintenance activities will be addressed programatically.
445 | 4451990023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990023R00.pdf | 1990-08-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 17 | On August 8,1990, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operations, with reactor power at 17 percent. A loose fuse in the Main Feedwater control power circuit caused closure of a valve in the feedwater flow path to Steam Generator number 4. Water level in Steam Generator number 4 decreased to the Lo-Lo level setpoint, initiating a reactor trip signal. Corrective actions included inspection of similar components in other applications, maintenance on the malfunctioning component, and personnel training.
445 | 4451990025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990025R00.pdf | 1990-08-25 | QP5 | Excessive Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 97 | At approximately 0037 on August 25, 1990, Steam Generator (SG) Number 2 Feedwater Flow Control Valve (FCV) failed full open. A Reactor Operator attempted to close the valve from the Main Control Board by reducing the demand signal; however, at 0038, a turbine trip signal and feedwater isolation signal was generated due to Protection System Interlock P-14, Hi-Hi Level in SG Number 2. The reactor tripped at 0038 due to the turbine trip since reactor power was above the P-9 setpoint of 50 percent.<br /><br /> The cause of the Feedwater FCV failure is attributed to the feedback linkage arm from the valve stem to the valve positioner separating due to flow induced oscillations. Corrective actions include the installation of a lock washer on the feedback linkage arm and a design modification to modify the valve internals to reduce flow induced oscillations.
445 | 4451990027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990027R00.pdf | 1990-09-07 | QP5 | Excessive Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On September 7, 1990, at 0033, Comanche Peak Steam Electric Station (CPSES) Unit 1 Steam Generator (SG) Number (No.) 2 Feedwater Flow Control Valve (FCV) failed full open due to shearing of the positioner feedback linkage arm. The failed valve overfed SG No. 2 and the reactor was manually tripped at 0034 with SG No. 2 level at approximately 80 percent narrow range indicated level. <br /><br /> The plant was stabilized at 0043 in Mode 3. At 0130, a Balance of Plant Reactor Operator (RO) decreased auxiliary feedwater flow to SG No. 4 since the level was increasing faster than the other three. At 0232, a Relief RO noted that SG No. 4 level was approaching the Lo-Lo Level setpoint and increased auxiliary feedwater flow. The low level combined with the increased flow which caused a "shrink and swell" effect in SG No. 4 resulted in a Lo-Lo Level signal which generated an automatic start signal for the Auxiliary Feedwater System.<br /><br /> The cause of the linkage arm failure is attributed to fatigue resulting from flow induced oscillations. Corrective actions include repair of SG No. 2 FCV and a design modification to modify the valve internals to reduce flow induced oscillations.
445 | 4451990028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990028R00.pdf | 1990-09-08 | QR3 | Reactivity Control Imbalance | [45 empty] | Comanche Peak 1 | P | WE | PO | 38 | At 1428 on September 8, 1990, Comanche Peak Steam Electric Station Unit 1 was automatically tripped from 38 percent power. A lightning strike is believed to have caused a surge in the input power resulting in the de-energization of power supplies in the rod drive system, causing the rods controlled by one rod control cabinet to drop into the core. This resulted in the reactor trip from high negative flux rate. <br /><br /> No specific component or system failures were identified as the cause of this event. The installation of surge suppressors in the input supply to rod drive power supplies will provide additional assurance that power supplies remain available during lightning strikes.
445 | 4451990029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990029R00.pdf | 1990-09-10 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 92 | On September 10, 1990, at 0917 CDT, Comanche Peak Steam Electric Station Unit 1 experienced a reactor trip from Mode 1, Power Operations. The reactor trip was caused by a turbine trip which resulted from a high level condition in the B Moisture Separator Reheater (MSR). The high level in the MSR occurred when an operator attempted to restore a separator drain tank drain valve to service while the drain valve was still isolated. The event was caused by the failure of operators to adequately verify component status prior to returning the component to service. Corrective actions taken include review of the lessons learned package by operators and individual counseling.
445 | 4451990030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451990030R00.pdf | 1990-09-15 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 54 | On September 15, 1990, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with reactor power at 54 percent. Operations personnel were preparing to raise reactor power to support secondary system performance evaluation and tuning. When a second Condensate pump was started, the operating Heater Drain Pump and Main Feedwater Pump tripped. As a result of decreasing Steam Generator levels, a manual reactor trip was initiated. The cause of the event was an improperly routed Heater Drain Pump shield ground lead which caused a false ground overcurrent signal. Corrective action included rework of the affected component and review of similar components for the same problem.
445 | 4451991002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451991002R00.pdf | 1991-01-23 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 95 | On January 23, 1991, Comanche Peak Steam Electric Station was in Mode 1, Power Operation, with the reactor at 95 percent of rated thermal power. Operations personnel were in the process of draining the turbine-generator primary water system ion exchanger vessel in preparation for resin changeout. Due to an improperly established vessel isolation, level in the primary water head tank decreased to a point which allowed the introduction of the head tank cover gas into the system flow. The resultant loss of flow indication caused actuation of the generator protection circuit, which lead to a reactor trip. The cause of the event was incorrect head tank low alarm setpoint and an inadequate review of a procedure change. Corrective actions will include setpoint changes and correction to the operating procedure.
445 | 4451991004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451991004R00.pdf | 1991-02-10 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Comanche Peak 1 | P | WE | PO | 80 | On February 10, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, at 80 percent reactor power. While conducting on-the-job training, an Auxiliary Operator opened the 6.9 KV switchgear bus "1A3" auxiliary cabinet potential transformer drawer resulting in a load shed signal for the bus loads, which included Reactor Coolant Pump 1-03, followed by a reactor trip due to a loss of flow in reactor coolant loop 3. The root causes were determined to be inadequate labeling on the potential transformer drawer and poor judgement in opening a drawer without knowing the effect it would have on the plant. Corrective actions include labeling the potential transformer drawers, identifying equipment or panels that have interlocks or special sensitivity for equipment actuation, and issuing guidance to personnel on opening switchgear doors.
445 | 4451991008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451991008R00.pdf | 1991-03-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Comanche Peak 1 | P | WE | PO | 97 | On March 17, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with reactor power at 97 percent. An Auxiliary Operator and trainee were performing a Solid State Protection System, Train A, actuation logic test. During the test, the trainee depressed the shunt the button for the Train B reactor the breaker, instead of the intended Train A the button, causing a reactor trip. Root causes were identified as failure to verify the correct equipment and the Auxiliary Operator allowing his job as a trainer to interfere with his testing duties. Corrective actions include self verification training, enhanced breaker cabinet labels, monitoring operators to ensure self verification techniques are utilized, and additional guidance for trainers on handling trainees.
445 | 4451991020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451991020R00.pdf | 1991-07-13 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 80 | On July 13, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at 80 percent of rated thermal power. In preparation for troubleshooting a seal problem on one of the main turbine electrohydraulic controller fluid pumps, the idle pump was started and one of the operating pumps was secured. Following the pump start, air entrained in the fluid flow caused rapid and erratic operation of the main turbine steam control valves. This created a pressure pulse which propagated up the main steam line to the steam generator causing a spike of sufficient magnitude on the steam generator narrow range level transmitter to exceed the Hi-Hi level setpoint. The resulting turbine trip initiated a reactor trip. The root cause of the event will be verified by testing to be performed during a forthcoming outage. Corrective actions include testing and design modification.
445 | 4451991023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451991023R00.pdf | 1991-10-03 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 30 | On October 3, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at approximately 30 percent of rated thermal power. In order to collect data for evaluation of a problem with the main turbine electrohydraulic control (EHC) system, the idle hydraulic fluid pump was started and one of the two operating pumps was secured. Following the pump switchover, erratic operation of the main turbine steam control valves created a pressure pulse which propagated up the main steam line to the steam generator, causing a spike of sufficient magnitude on the steam generator narrow range level transmitter to exceed the Hi-Hi level setpoint. The main feedwater pumps tripped automatically, and the reactor was manually tripped due to decreasing steam generator levels. Causes include erratic operation of the EHC system and sensitivity of the steam generator narrow range level instrumentation. Corrective actions for EHC system performance anomalies will be determined based on the results of evaluation of test data.
445 | 4451992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451992001R00.pdf | 1992-01-08 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On January 8, 1992, the Reactor Operator was attempting to reestablish the required differential temperature between the main generator primary water system and the hydrogen gas system by taking manual control of primary water flow. While in manual control, primary water temperature started to rise and could not be checked, which resulted in a turbine trip followed by a reactor trip occurred due to high primary water temperature. <br /><br /> Root causes were determined to be failure to understand the potential consequences of controlling primary water flow in manual and failure of the Shift Supervisor to adequately monitor the evolution. Contributing factors were failure to use available procedures, lack of specific information in procedures regarding this risk, and the malfunction of the primary water high temperature alarm. Corrective actions include counselling the specific individuals, intensive training for the crew involved, enhancing requalification training, revising procedures, repairing the alarm, and establishing a task team to evaluate the technical information available to operate and maintain the main generator.
445 | 4451992009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451992009R00.pdf | 1992-05-08 | QR8 | Spurious Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 93 | At 2304 on May 8, 1992, instrumentation and Control (I&C) Technicians began channel calibration of the Loop IV N-16 Power Monitor Module (PMM) by placing the bistables in test. At 2308, the I&C Technicians opened the power supply breaker to the Loop II N-16 PMM instead of the Loop IV N-16 PMM. At 2309, the Loop II N-16 PMM power supply was restored, causing a spike that, along with the Loop IV N-16 bistables in test, met the logic coincidence requirements for a reactor trip. <br /><br /> Root cause of the event was personnel error. Contributing factors involved common key access to the N-16 cabinets and first time performance of this calibration by the individuals involved. Corrective actions included implementation of the appropriate level of the Positive Discipline Program for the individuals involved, a modification to the cabinet locking scheme, and observation of individuals performing sensitive tasks for the first time.
445 | 4451992014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451992014R00.pdf | 1992-06-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 100 | At 0528, on June 11, 1992, a loss of main feedwater resulted in a manual reactor trip due to rapidly lowering steam generator levels. Initially, the cause of the trip was unknown; however, troubleshooting determined that train A Solid State Protection System (SSPS) had produced a spurious signal which simulated a 2 out of 3 low pressure signal for Steam Generator 4. This resulted in a trip of both main feedwater pumps, closure of all feed regulating valves, and closure of the feedwater isolation valve for Steam Generator 4. Troubleshooting did not reveal the source of the problem. After discussions with the SSPS vendor it was concluded that the root cause could not be positively determined because the actuation was caused by an intermittent problem. It was determined, however, that the spurious signal could only have come from one of three possible circuit cards. These three cards were replaced. In addition, a detailed inspection of the termi-points on the circuit cards and a test switch associated with the cards eliminated the possibility that a short to ground had caused the actuation. The three circuit cards were sent to the vendor,and no discrepancies with cards were found. After the cards were replaced, no further spurious signals have been received.
445 | 4451992019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451992019R00.pdf | 1992-07-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 100 | At 1601, on July 20, 1992, a loss of main feedwater resulted in a manual reactor trip due to rapidly lowering Steam Generator (SG) levels. The cause of the loss of main feedwater was the same as a previous trip that had occurred on June 11, 1992, where a fault in Train A Solid State Protection System (SSPS) had produced a spurious signal which simulated a 2 out of 3 low steamline pressure signal for SG 4. The result was a trip of both main feedwater pumps, closure of all feed regulating valves, and closure of the feedwater isolation valve for Steam Generator 4. Troubleshooting concluded that the fault was caused by induced noise in the wiring of the Train A SG Loop 4 low steamline pressure anti-water hammer interlock circuit. This circuit is non-safety related and a safety evaluation has been performed by the vendor for deletion of this circuit from SSPS. A temporary modification was installed to bypass the SG low steamline pressure anti-water hammer interlock circuit. An investigation is ongoing to determine the nature of the malfunction, and further troubleshooting plans are being proposed for an upcoming refueling outage.
445 | 4451992022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451992022R00.pdf | 1992-10-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 1210 on October 12, 1992, Steam Generator (SG) Number (No.) 4 Steam and Feedwater Flow Mismatch Alarm annunciated. The Reactor Operator (RO) immediately took manual control of the SG No. 4 Feedwater Flow Control Valve (FCV). The SG No. 4 FCV had failed in the closed direction, causing loss of feedwater flow to SG No. 4, and would not respond to manual control. At 1214, with SG No. 4 level at 28 percent and dropping, the RO manually tripped the reactor. Plant systems responded as expected. The plant was stabilized in Mode 3, Hot Standby, at approximately 1220 on October 12, 1992. <br /><br /> The root cause of this event was the failure of a spring in the SG No. 4 FCV pressure regulator due to the wrong pressure regulator being installed. Corrective actions include repair of SG No. 4 FCV, and a revision to the Master Parts List. Generic corrective actions include verification of the correct regulators in the other FCVs and other non-safety critical valves and a separate review of the Master Parts List.
445 | 4451993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451993001R01.pdf | 1993-01-18 | QR8 | Spurious Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 1144 on January 18, 1993, while restoring the Solid State Protection System (SSPS) from a test lineup, the Reactor Operator used an incorrect instruction. As a result, trip blocks were not in place for switch manipulation and a reactor trip occurred while restoring SSPS to a normal lineup. <br /><br /> Root cause of the event was personnel error. Contributing factors were that a test procedure reference was not specific which led the RO to an incorrect instruction and that senior supervision monitoring during the restoration was less than adequate. Corrective actions included event review, training and procedure revision.
445 | 4451993002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451993002R00.pdf | 1993-01-24 | QR8 | Spurious Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 1112 a.m. on January 24, 1993, Comanche Peak Steam Electric Station Unit 1 was operating at 100 percent of rated thermal power. During routine performance of the surveillance test on nuclear instrumentation power range channel 3, a spurious signal from pressurizer pressure channel 2 made up the logic for the Over Temperature Nitrogen 16 reactor trip. All systems responded as designed. The root cause of the event was instrument failure during surveillance testing. Corrective action was the replacement of the failed component .
445 | 4451993007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451993007R00.pdf | 1993-06-26 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On June 26, 1993, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at approximately at 100 percent of rated thermal power. A Control Room alarm indicated excessive temperature on the 1-04 Reactor Coolant Pump (RCP) motor stator. Component Cooling Water flow was increased to increase cooling to the RCP. Personnel were dispatched to the Containment Building to troubleshoot. These efforts were not successful in restoring the indicated temperature to normal. As a result, the Shift Supervisor directed a manual reactor trip. Subsequently, it was discovered that a faulty Resistance Temperature Detector (RTD) caused the excessive temperature indication. Another available RTD was connected to the plant computer and the circuit was functionally tested.
445 | 4451993011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451993011R00.pdf | 1993-12-24 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 11:46 a.m. on December 24, 1993, during trouble shooting on the main Turbine Electro-hydraulic Control System (EHC) Unit 1 received a main turbine low lube oil pressure signal resulting in a turbine electrical trip which in turn caused a reactor trip. Turning gear valve 1-HV-6554A received an open signal due to an erroneous signal (less than 230 RPM) coming from the turbine speed control circuitry. <br /><br /> Contributing factors were lack of specific training on the complexity of the EHC system and use of non-grounded test equipment. Corrective actions included event review, lessons learned and training content review.
445 | 4451994001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451994001R00.pdf | 1994-02-01 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 9:38 p.m. February 1, 1994, an indicated low flow condition on primary water to the Main Generator Stator caused a Turbine/Reactor trip. There was no actual loss of stator flow. TU Electric believes that the trip was caused by a spurious signal. Corrective actions included monitoring key points for power supply and instrument signal stability, and evaluation by the vendor.
445 | 4451994006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451994006R00.pdf | 1994-11-29 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 9:21 p.m., CST November 29, 1994, an indicated low flow condition on cooling water to the Main Generator Stator caused a Turbine/Reactor trip. There was no actual loss of stator flow. TU Electric believes that the trip was caused by a sensing line hydraulic anomaly, most likely gas bubbles. Immediate actions were to change the negative slope of the sensing lines to a positive slope to prevent gas accumulation. Corrective actions were to schedule a design modification, which will install separate sensing lines in the primary water flow stator circuit and will install alarms to warn the operators of impending problems with primary water tank level and temperature.
445 | 4451995002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451995002R00.pdf | 1995-05-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On May 5, 1995, at approximately 8:06 p.m., a reactor trip of both CPSES Units 1 and 2 occurred from a lightning strike to the plant. The lightning strike created a voltage surge on the Rod Control System Neutral bus in both units causing a partial rod drop. The reactor trips actuated on the resulting Power Range Negative Rate Reactor Trip. The plant equipment response to the reactor trips was consistent with that expected for the existing plant conditions. <br /><br /> The cause of this event was determined to be: the failure of the lightning protection system to provide effective protection against lightning induced perturbations on sensitive plant electrical equipment.<br /><br /> Corrective actions were to form a Task Team, The Task Teams charter was to evaluate/investigate methods of minimizing the effects of a lighting strike, including any potential design modifications, needed to modify the existing lightning protection system to minimize the effects of a lightning strike, and prevent similar reactor trips.
445 | 4451995003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451995003R01.pdf | 1995-06-11 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 100 | On June 11, 1995, at approximately 12:01 CDT, while performing a slave relay actuation test on Unit 1, a non-safety related inverter transferred from its normal inverter AC power supply to its bypass (alternate) AC power supply, which was deenergized per the slave relay test procedures. This resulted in loss of both condensate pumps. The loss of the condensate pumps resulted in the trip of both Main Feedwater (MFW) pumps. A manual reactor trip of CPSES Unit 1 was initiated due to loss of feedwater to the steam generators. The trip of both MFW pumps initiated an Auxiliary Feedwater actuation signal which started the Motor Driven Auxiliary Feedwater (MDAFW) pumps. Following a LO-LO level signal in Steam Generators 1-01 and 1-02, the Turbine Driven Auxiliary Feedwater (TDAFW) pump started as designed but tripped on overspeed. The details involving the TDAFW pump overspeed will be provided in LER 445/95-004-01.
445 | 4451995007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451995007R00.pdf | 1995-11-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On November 19, 1995, at 5:22 p.m. a Balance of Plant (BOP) analog power supply for controller 1-FK-2289 failed causing 1-FV-2289 (Main Feedwater Pump(MFP) 1A(EIIS:(P)(SJ)) recirc valve) (EIIS:(V)(SJ)) to fail open. The failure of the recirc valve initiated a reduction of flow to the Steam Generators(SG) (EIIS:(SG)(SB)), and a decrease in feedwater suction pressure, resulting in a MFP trip. A restart of the pump and isolation of the recirc valve in combination with the feedwater transient resulted in overfeeding a SG. SG 2 level increased to a Hi Hi level initiating a turbine/reactor trip. Additionally, timer on the pole disagreement for the switch yard (W 3) Breaker 8010 (which is the Unit 1 generator output to the west bus) resulted in the breaker opening and isolation of the 345Kv switchyard west bus. <br /><br /> The failure of analog power supply for 1-FK-2289 was due to a blown fuse in a circuit card, which caused the MFP recirc valve to fail open. The card has been replaced with a new card containing a new fuse. A design modification has been issued to correct the cycle delay for the switch yard Breaker 8010.
445 | 4451996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451996001R00.pdf | 1996-01-17 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On January 17, 1996, at approximately 8:01 a.m.(CST), Unit 1 inverter IV1PC2 output breaker tripped on over current. This resulted in the loss of power to distribution panel 1PC2. At approximately 8:08 a.m., the loss of power to the panel (1PC2), which armed the steam dumps, required the Auxiliary Operator (utility, non-licensed) to transfer power to a separate power source. TU Electric believes that this subsequent transfer action to restore power initiated a spike (high) on the N-16/T sub avg instrumentation creating a temperature error signal to the Steam Dumps. The Steam Dump valves opened resulting in the generation of Main Steam line pressure - low Safety Injection. A reactor trip signal was initiated as a result of the SI signal. ECCS injection was terminated in accordance with the emergency operating procedures. TU Electric believes that the event was caused due to a large T sub avg - T sub ref error signal generated following the restoration of power to the distribution panel. Plant procedures have been revised to prevent repetition of this type of event.
445 | 4451996002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451996002R01.pdf | 1996-01-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 100 | On January 22, 1996, at approximately 8:00 a.m. (CST) during troubleshooting on safety-related inverter IV1EC1, power was lost to panel 1EC1 which caused the four Main Feedwater Isolation Valves (MFIVs) to close. Closure of the MFIVs caused a loss of main feedwater flow which resulted in a manual reactor trip. The event was caused by a less than adequate initial troubleshooting plan following a malfunction on inverter IV1EC1. Operations procedures have been revised to clearly note when the inverter transfer switch is to be placed in the bypass position. During the closure of the MFIVs, it was noted that MFIV 2 was slow to close. Further investigation revealed that this MFIV could have been inoperable for a period of time longer than allowed by Technical Specifications (TS). MFIV 2 was potentially inoperable due to foreign material in the hydraulic solenoid valve. The solenoid valves in the potentially inoperable MFIV were replaced and the MFIV was successfully tested.
445 | 4451996007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451996007R00.pdf | 1996-08-09 | QR8 | Spurious Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On August 09, 1996, at approximately 12:03 p.m., TU Electric was performing a normal surveillance test procedure on Power Range Neutron Flux Channel N-43. This testing required that the Overtemperature (OT) N-16 trip function, which uses the N-43 as an input, to be placed in the TRIP condition. While the Power Range Channel N-43 was in test, a severe lightning storm was occurring outside. A lightning strike caused the Channel IV T sub cold to spike high which resulted in OT N-16 setpoint reduction and a subsequent trip signal. This completed the two-out-of-four logic for a reactor trip on OT N-16. All rods fully inserted into the core. The plant equipment response to the reactor trip was consistent with that expected for the existing plant conditions. <br /><br /> The cause of the reactor trip was deemed to be lighting strike coupled with the Power Range Channel N-43 being in the trip position. Management's expectations will be issued to plant personnel with respect to scheduling and/or suspension of tests/surveillances, which could impact plant operations, during severe weather.
445 | 4451997009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451997009R00.pdf | 1997-10-27 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On October 27, 1997, at approximately 10:44 a.m. Comanche Peak Steam Electric Station Unit 1 experienced a reactor trip initiated due to a main turbine generator trip. Prior to the event, testing of the high voltage switchyard east bus lockout relays was being performed. Slow opening of the Unit 1 generator east bus supply breaker during the testing caused the backup bus protection relay to actuate and tripped the Unit 1 generator west bus supply breaker. This resulted in a Unit 1 loss of load and an automatic turbine and reactor trip. All systems responded normally on the reactor trip and auxiliary feedwater was manually initiated.The cause of the event was the slow operation of the Unit 1 east bus supply breaker. Additionally, it was determined that the work instructions provided insufficient detail to defeat the backup relay protection during the performance of the test.
445 | 4452003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452003002R00.pdf | 2003-03-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 1 | P | WE | PO | 100 | On March 16, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 1, Power Operation, operating at 100 percent power. At 2149 hours, both Main Feedwater pumps tripped on low suction pressure due to an unexpected trip of Condensate pump 1-01. Operators manually tripped the Unit 1 reactor, and all control rods fully inserted. All Auxiliary Feedwater pumps automatically started as expected.TXU Generation Company LP (TXU Energy) believes that the event was caused by a manufacturing defect in the Condensate pump 1-01 motor. Corrective actions include repair of the Condensate pump 1-01 motor and evaluation of the Predictive Analysis Program for large electric motors.All times in this report are approximate and Central Daylight Standard Time unless noted otherwise.
445 | 4452003003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452003003R00.pdf | 2003-05-15 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On May 15, 2003 at 0252 with Units 1 and 2 in Mode 1 (Power Operation) with Unit 1 at 100 percent power and Unit 2 at 99.8 percent power, a disturbance on the Comanche Peak-Parker 345kV transmission line approximately four miles from the CPSES switchyard resulted in a loss of the 345kV switchyard and subsequent reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) on natural circulation in accordance with plant emergency procedures as a result of the loss of non-safety related ac power.The protective relaying system associated with the CPSES Parker Line breaker failed to trip the breaker to isolate the switchyard from the fault and to initiate local breaker failure backup relaying. Because the switchyard breaker failed to isolate the faulted 345kV transmission line, the 345kV switchyard was deenergized and the Reactor Coolant Pumps in both units (4 per unit) tripped due to the loss of non-safety related ac power. CPSES Units 1 and 2 experienced turbine trips and subsequent reactor trips. Both units at CPSES experienced an automatic start of the Auxiliary Feedwater System. Unit 1 Class 1E electrical buses experienced a slow transfer to their alternate source that was fed from the 138kV switchyard. The emergency diesel generators remained available but did not start or load because offsite power was provided to the 1E electrical buses as designed. Systems functioned as designed and the units were stabilized and maintained in MODE 3 on natural circulation.All times in this report are approximate and Central Daylight Time unless noted otherwise.
445 | 4452010001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452010001R00.pdf | 2010-01-09 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On January 9, 2010, Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 1 operating at 100% power. At 1028 hours, the Unit 1 Main Turbine tripped due to a pressure relay actuation on the Unit 1 Main Transformer 01 and the Main Turbine Trip caused an automatic reactor trip. All control rods fully inserted, and all Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the event. Internal inspection of the transformer showed that the relay actuation resulted from an internal failure of the Main Transformer as a result of a phase to ground fault. The exact cause of the fault could not be determined. Immediate corrective actions included isolating the Main Transformer 01 from Unit 1 and the other Main Transformer 02. On January 11, 2010, Unit 1 was synchronized to the grid at 0011 hours and reached a 640 megawatt output by 2100 hours. On January 19, 2010, a planned outage was taken on Unit 1 to install a spare transformer. Unit 1 was synchronized to the grid on January 21, 2010 at 2326 hours and reached 100% power the next day at 1341 hours.All times in this report are approximate and are Central Standard Time unless noted otherwise.
445 | 4452012003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452012003R00.pdf | 2012-11-02 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | On November 2, 2012, Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 1 operating at 100 percent power. At 0142 hours, the Unit 1 reactor was manually tripped due to rising Reactor Coolant Pump (RCP) 1-04 motor lower radial bearing temperature and a bearing oil level alarm. All control rods fully inserted, both Motor Driven Auxiliary Feedwater Pumps were manually started, and the Turbine Driven Auxiliary Feedwater Pump automatically started as a result of the reactor trip. The RCP 1-04 motor experienced a lower radial bearing failure which required a Unit 1 manual reactor trip. The lower radial bearing failure was caused by overheating due to loss of oil in the oil reservoir. The loss of oil was due to slow leakage from a degraded elastomeric coupling within the RCP internal oil supply system. The oil supply coupling connection degraded sufficiently to allow the reservoir level to decrease and prevent adequate lower radial bearing lubrication. The seal degraded because a preventative maintenance (PM) activity had not been created or implemented to periodically change these sub-components. Immediate corrective actions included replacement of the RCP 1-04 lower radial bearing and cooling line coupling, seals, and gaskets, and changing the setpoint on the oil level alarm to account for dynamic oil levels within the lower reservoir which will assure a more timely alarm. As a part of the CPNPP Corrective Action Program, PMs will be developed and implemented to evaluate and replace perishable "soft" subcomponents to ensure that those subcomponents will perform their design function throughout their service life and do not adversely affect equipment operation. All times in this report are approximate and Central Time unless noted otherwise.
445 | 4452014001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452014001R00.pdf | 2014-01-18 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 1 | P | WE | PO | 100 | At 0840 hours, on January 18, 2014, Unit 1 was operating at approximately 100% power when an automatic reactor trip occurred due to a generator lock out relay trip and turbine trip. The plant responded as expected to the transient. The cause of this event was a Unit 1 Generator Current Transformer (CT) cable shorting to ground. Vibration of the cable and contact of the cable with the free end of the conduit resulted in physical wear of the cable jacket and insulation that over the period of more than 12 years (from 2002 to 2014) cut through the jacket and insulation and allowed the conductor to contact the metal of the conduit. The corrective actions included reworking the grounded cable. The Unit 1 and Unit 2 Generator CT cables will be inspected, insulated, retrained, and/or replaced at each unit's next refueling outage. The Unit 1 and Unit 2 Generator CT conduits will have insulated bushings installed at the conduit exits where the conduit is not connected to a device or panel within a hub. No component or system failures occurred. All times in this report are approximate and Central Standard Time unless noted otherwise.
446 | 4461993003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461993003R00.pdf | 1993-05-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 2 | P | WE | PO | 23 | On May 4, 1993, Comanche Peak Steam Electric Station Unit 2 was at approximately 23 percent of rated thermal power after a recent power reduction in preparation for a reactor shutdown from the Remote Shutdown Panel to be performed as part of the initial startup sequence. As a result of a combination of instrument inaccuracies, the feedwater anti- waterhammer permissive was lost, resulting in closure of feedwater isolation valve number 1. With steam generator number 1 at 38 percent level and decreasing, a manual reactor trip was initiated. The cause of the event was instrument error. Corrective action included maintenance on the affected instrumentation channels.
446 | 4461993005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461993005R00.pdf | 1993-05-20 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 72 | At 0701 on May 20, 1993, a low flow condition on primary water to the Main Generator Stator caused a Generator Lockout and Reactor/Turbine trip. The cause of the event was a stem and disk separation on the Generator Stator flow inlet isolation valve. The subject valve was reoriented to reduce the potential for future failures and replaced.
446 | 4461993011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461993011R00.pdf | 1993-11-17 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 2 | P | WE | PO | 100 | On November 17, 1993, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1. Power operation with reactor power at 100 percent. <br /><br /> At 7:59 p.m. on November 17, 1993 Separator Drain Tank, 2A Normal Drain Valve failed open. The failure of the valve was caused due to the jam nut on the Fisher Positioner feedback linkage arm being loose. The jam nut was apparently loosened due to vibration. <br /><br /> The corrective actions were to tighten the jam nut, inspect other similar and identical feedback positioner arms and apply similar corrective actions as applicable.
446 | 4461994003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461994003R00.pdf | 1994-03-05 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 75 | On March 5, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, with reactor power at 75 percent. The Balance of Plant Operator noticed Turbine/Generator (TG) load swings. Abnormal Operating Procedure was entered to stabilize the plant while the problem was being diagnosed. Because possible problems with the Electro-Hydraulic Control (EHC) Converter #1 were indicated, load control was switched to the Mechanical-Hydraulic Controller. The load swings temporarily subsided. The load swings returned and were increasing and the load was shifted to EHC Converter #2. This action did not stabilize the load swings. Without the ability to control the load swings the Unit Supervisor directed a manual reactor trip.After extensive troubleshooting, and correcting Unit 2 was restarted at 3:45 p.m., CDT on March 13, 1994. During the restart with the load at approximately 120 MWe, all four control valves abruptly closed. The BOP Operator immediately tripped the turbine.<br /><br /> It was determined that a feedback (Collins) coil in the EHC system had shorted/failed. Corrective actions involved troubleshooting of the EHC system and replacement of the feedback coil.
446 | 4461994010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461994010R00.pdf | 1994-06-27 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On On June 27, 1994 at approximately 4:54 p.m. Comanche Peak Steam Electric Station (CPSES) Unit 2 experienced an automatic reactor trip from a turbine generator trip. The plant sequence of event recorder logged a generator differential lock-out relay actuation. All required systems functioned as designed. <br /><br /> The event was caused by a short in the lead of the B phase neutral current transformer on the generator. <br /><br /> Corrective actions were to replace the lead in accordance with plant procedures.
446 | 4461994012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461994012R00.pdf | 1994-08-15 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 75 | On August 15, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 with reactor power at 75 percent. The unit was in the process of being shut down due to an oil leak on Main Transformer (EIIS:(XFMR)) (2MT2) High Voltage Phase Bushing. At 10:45 a.m. CST the unit was manually tripped to deenergize the main transformer in order to prevent damage to the bushing and/or the transformer. During the unit trip, Reactor Coolant Pump (EIIS:(P)(AB)) (RCP 2-01) tripped due to an electrical transient caused by the Unit trip. Repeated Auxiliary Feedwater pump (EIIS:(BA)) auto-start Engineered Safety Feature (ESF) initiation signals occurred due to Steam Generator (EIIS:(SG)(SB)) LO-LO level signals. <br /><br /> The oil leak was the result of cracking/failure of the bushing housing on 2MT2. The failed bushing assembly has been sent to the vendor for analysis. The ESF actuation occurred as a normal result of the Steam Generator level shrink from the reactor trip following the closure of the turbine stop valves. Subsequent ESF initiation signals occurred due to a failed control card in the Steam Dump control circuit (EIIS:(SB)(ECBD)). The corrective actions were to replace the failed circuit card.
446 | 4461994014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461994014R00.pdf | 1994-10-07 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | SU | 1 | On October 7, 1994, Comanche Peak Steam Electric Station Unit 2 was in Mode 2 startup and less than 1 percent reactor power. Plant shutdown was in progress for the first refueling outage. Control bank D was at 118 steps. At 5:20 p.m., a manual reactor trip was initiated due to digital rod position indication failure for control bank D control rod H-8. The cause of the event, i.e., Digital Rod Position Indication (DRPI) (EIIS:(ZI)(AA)) for control rod H-8 not responding correctly, was attributed to a loose connector. The loose connection will be corrected during the refueling outage and the DRPI tested prior to reactor startup.
446 | 4451995002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4451995002R00.pdf | 1995-05-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On May 5, 1995, at approximately 8:06 p.m., a reactor trip of both CPSES Units 1 and 2 occurred from a lightning strike to the plant. The lightning strike created a voltage surge on the Rod Control System Neutral bus in both units causing a partial rod drop. The reactor trips actuated on the resulting Power Range Negative Rate Reactor Trip. The plant equipment response to the reactor trips was consistent with that expected for the existing plant conditions. <br /><br /> The cause of this event was determined to be: the failure of the lightning protection system to provide effective protection against lightning induced perturbations on sensitive plant electrical equipment.<br /><br /> Corrective actions were to form a Task Team, The Task Teams charter was to evaluate/investigate methods of minimizing the effects of a lighting strike, including any potential design modifications, needed to modify the existing lightning protection system to minimize the effects of a lightning strike, and prevent similar reactor trips.
446 | 4461995004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461995004R00.pdf | 1995-12-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On December 5, 1995, at approximately 1:11 p.m. Comanche Peak Steam Electric Station Unit 2 experienced a reactor trip initiated due to Lo Lo Steam Generator(SG) reactor trip signal. Prior to the event, troubleshooting on Main Feedwater Pump(MFP) 2A speed control mechanism was being performed. The speed control mechanism was believed to have failed. During the troubleshooting of the speed controller, the MFP 2A turbine control valve began to cycle open and shut repeatedly. In accordance with previously discussed contingency actions, operators manually tripped the MFP 2A. The plant ran back from 100 percent to 60 percent power automatically as expected. Approximately I minute after the runback, erratic steam dump operation resulted in excessive shrink of all SG levels. The unit automatically tripped due to Lo Lo level in SG 3. Additionally, the timer on the pole disagreement for the switch yard breakers resulted in the breakers opening and isolation of the 345Kv switchyard east bus. <br /><br /> The cause of the event was a failure of the MFP 2A controls. The manual trip of the MFP and the rapid closure of the steam dump valves increased the shrinkage in the SGs initiating the actuation of the Lo Lo SG signal which resulted in an automatic reactor trip. The speed control on the MFP 2A and the switchyard breakers have been reworked and modified as required.
446 | 4461996003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461996003R00.pdf | 1996-02-23 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 63 | At approximately 7:27 a.m., on February 23, 1996, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, with reactor power at approximately 63 percent (approximately 742 Megawatts). Reactor power was being decreased by the Reactor Operator (Utility, Licensed) at the rate of 5 percent per hour in preparation for CPSES Unit 2 second refueling outage (2RF02). When the load reduction was performed, turbine output dropped from 742 MWe to 160 MWe, and was oscillating 20 to 30 megawatts on both sides of 160 MWE. The cause of the load decrease was not apparent. In response to the loss of control, the Unit 2 Supervisor made a conservative decision to manually trip the reactor. <br /><br /> The cause event was postulated to be faulty printed circuit cards in the Electro-Hydraulic Control (EHC) runback circuitry.
446 | 4461996006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461996006R00.pdf | 1996-09-18 | QR8 | Spurious Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On September 18, 1996, at approximately 12:45 p.m., during a severe thunderstorm a lightning strike caused Comanche Peak Steam Electric Station (CPSES) Unit 2 T sub cold channels II and IV to spike high which resulted in Overtemperature (OT) N-16 setpoint reduction and a subsequent trip signal. This completed the two-out-of-four logic for a reactor trip on OT N-16. All rods fully inserted into the core. The plant equipment response to the reactor trip was consistent with that expected for the existing plant conditions. <br /><br /> The cause of the reactor trip was deemed to be lighting strike coupled with a ground which existed from the shield to ground on the spare Resistance Temperature Detector (RTD) in channel II and both the spare and active RTDs in channel IV. A Design Change was implemented to eliminate the ground.
446 | 4461996007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461996007R00.pdf | 1996-10-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On October 18, 1996, at approximately 03:06 a.m., an electrical fault on Comanche Peak Steam Electrical Station (CPSES) Unit 2 Service Air Compressor 2-01 motor initiated a lockout on non-safety 6.9 Kv bus 2A3. The loss of the 2A3 bus caused Reactor Coolant Pump 2-03 to de-energize, which resulted in a reactor trip due to Reactor Coolant System loop 3 low flow. <br /><br /> A probable cause for the loss of the 2A3 bus was believed to be slow opening of the service air compressor 2-01 motor breaker during an overcurrent condition, which did not trip in time to prevent lockout on the non-safety 6.9 Kv bus. <br /><br /> Troubleshooting and testing of the breakers did not indicate equipment failures. The affected equipment was tested and declared to be operational.
446 | 4461997002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461997002R00.pdf | 1997-10-25 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | SU | 10 | On October 25, 1997, Comanche Peak Steam Electric Station Unit 2 was in Mode 1 and had commenced a Unit shutdown in preparation for the third refueling outage. At approximately 12:17 a.m., prior to the event, troubleshooting efforts were in progress for a phase failure indication associated with the moveable coils for control rod Bank C. At approximately 4:04 a.m., attempt was made to move Bank C. When the Reactor Operator (Utility, Licensed) placed the In-Hold-Out switch to the "out" position, a Rod Control Urgent Failure alarm was received and an indication of four dropped rods. The Reactor Operator manually tripped the reactor based on the indication of 4 dropped rods. All rods fully inserted when the Reactor Trip Breakers opened. TU Electric concluded that a failure of phase sensing transformer T2 within the rod control cabinet 2AC generated the first fault resulting in an urgent failure alarm. Subsequent troubleshooting resulted in replacement of regulation card. The replaced regulation card had a bent pin which caused the actual dropped rods. The bent pin was possibly caused during insertion of the regulation card. The Phase Sensing Transformer T2 has been replaced. Additional corrective actions including inspection/refurbishment of the rod control system with respect to rod control system are complete.
446 | 4461998002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461998002R00.pdf | 1998-03-08 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On March 8, 1998, Comanche Peak Steam Electric Station Unit 2 was in Mode 1 and had commenced feed and bleed operations on the Turbine Plant Cooling Water (TPCW) system. At approximately 11:01 p.m., both Turbine Plant Cooling Water Pumps (TPCWP) tripped due to lo lo level indication in the TPCW head tank. Shortly thereafter the turbine tripped on high primary water temperature. The reactor automatically tripped on turbine trip as designed. All rods fully inserted when the Reactor Trip Breakers opened. Both the motor driven and the turbine driven auxiliary feedwater pumps (TDAFWP) started due to steam generator shrink following the trip. The turbine driven auxiliary feedwater pump was conservatively shutdown to prevent an excessive cool down of the reactor coolant system (EIIS:(AB)) and a potential safety injection. However, the turbine driven auxiliary feedwater pump restarted. The plant was stabilized in mode 3 and all systems functioned as designed.TU Electric concluded that the event was a result of a low level switch failure in the TPCW makeup valve. The cause of the failure could not be determined. The level switch was tested and the system was determined to be operable, functional, and working. The procedure for performing a feed and bleed of the system was changed to preclude inadvertently draining the tank in the future. All corrective actions are complete.The cause of the second start of the TDAFWP was that inventory had not been sufficiently restored in multiple steam generators to allow the pump to be stopped. The operators checked steam generator level prior to attempting to stop the pump and believed the levels to be sufficient; however, based on pump restart, level was not sufficient in at least two steam generators.
446 | 4461999002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4461999002R00.pdf | 1999-01-03 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | At approximately 11:14 a.m., on January 3, 1999, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, with reactor power at approximately 100 percent, main turbine generator control valves suddenly and unexpectedly closed while at 100 percent rated power. As designed, all steam dumps immediately opened and rods automatically stepped in to control the reactor coolant system temperature transient. The reactor plant, designed to withstand a 50 percent load rejection without a trip, experienced an equivalent 80 percent load rejection event. The cause of the load rejection was not apparent. In response to the loss of turbine load control, the Unit 2 Operations Shift Supervisor (utility, licensed) made a conservative decision to manually trip the reactor.The cause of the event could not be determined. A data acquisition system (minidas) has been connected to the Electro-Hydraulic Control (EHC) control system to monitor and collect data and provide additional diagnostic information, should the failure repeat.
446 | 4462001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462001001R00.pdf | 2001-07-18 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On July 18, 2001, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at 100 percent power. At approximately 7:59 a.m., during performance of a Steam Generator 2-01 Narrow Range Level 519 Channel Operability Test, a test trouble alarm was received on the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) panel. During restoration of AMSAC to clear the trouble alarm, a spurious AMSAC signal was generated causing an automatic turbine trip which resulted in an automatic reactor trip from 100 percent power. All control rods fully inserted. Auxiliary Feedwater (AFW) automatically actuated following the reactor trip and the Main Steam Isolation Valves (MSIV's) were manually closed for temperature control. The plant was stabilized in Mode 3 and all systems functioned as designed.TXU Electric believes that the event was caused by a short circuit in a light bulb socket during replacement of an apparently burned out AC power lamp in the AMSAC panel. Corrective actions include replacement of the defective light socket, inspection of other AMSAC light sockets, and modification of the AMSAC power light circuit.All times in this report are approximate and Central Standard Time unless noted otherwise.
446 | 4462002001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462002001R00.pdf | 2002-06-06 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On June 6, 2002, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, operating at 100 percent power. At 1924 hours, while Maintenance personnel were investigating a "Generator Electronic Protection Failure" alarm, a "Turbine Generator Channel 1 Primary Water Pump Vibration High" signal was received. This resulted in a Main Generator trip which caused a trip of the Unit 2 Main Turbine. The Unit 2 reactor automatically tripped on a "Turbine Trip >50% Power" signal. All control rods fully inserted, and all Auxiliary Feedwater pumps automatically started on Lo-Lo Steam Generator level as expected.TXU Generation Company LP (TXU Energy) believes that the event was caused by a Primary Water Pump Vibration Expansion Measuring cabinet circuit breaker failing open which caused a spurious "Turbine Generator Channel 1 Primary Water Pump Vibration High" signal. Corrective actions include replacement of the failed breaker, failure analysis on the failed breaker, and evaluation of potential circuit design changes or modifications.All times in this report are approximate and Central Daylight Standard Time unless noted otherwise.
446 | 4452003003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4452003003R00.pdf | 2003-05-15 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On May 15, 2003 at 0252 with Units 1 and 2 in Mode 1 (Power Operation) with Unit 1 at 100 percent power and Unit 2 at 99.8 percent power, a disturbance on the Comanche Peak-Parker 345kV transmission line approximately four miles from the CPSES switchyard resulted in a loss of the 345kV switchyard and subsequent reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) on natural circulation in accordance with plant emergency procedures as a result of the loss of non-safety related ac power.The protective relaying system associated with the CPSES Parker Line breaker failed to trip the breaker to isolate the switchyard from the fault and to initiate local breaker failure backup relaying. Because the switchyard breaker failed to isolate the faulted 345kV transmission line, the 345kV switchyard was deenergized and the Reactor Coolant Pumps in both units (4 per unit) tripped due to the loss of non-safety related ac power. CPSES Units 1 and 2 experienced turbine trips and subsequent reactor trips. Both units at CPSES experienced an automatic start of the Auxiliary Feedwater System. Unit 1 Class 1E electrical buses experienced a slow transfer to their alternate source that was fed from the 138kV switchyard. The emergency diesel generators remained available but did not start or load because offsite power was provided to the 1E electrical buses as designed. Systems functioned as designed and the units were stabilized and maintained in MODE 3 on natural circulation.All times in this report are approximate and Central Daylight Time unless noted otherwise.
446 | 4462003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462003001R00.pdf | 2003-07-09 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On July 9, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, operating at 100% power. At 0109 hours, the 2-04 Reactor Coolant Pump (RCP) motor breaker opened which resulted in loss of the 2-04 RCP and an automatic reactor trip. All control rods fully inserted and all Auxiliary Feedwater pumps automatically started as expected.TXU Generation Company LP's (TXU Energy) evaluation of this event has determined that the 2-04 RCP motor breaker opened due to a "B" phase stator to ground short in the 2-04 RCP motor. Corrective actions include repair of the 2-04 RCP motor stator and, as previously discussed in Licensee Event Report 03-002-00 for CPSES Unit 1, an evaluation of the Predictive Analysis Program specifically for large electric motors will be performed to assess the current program scope, monitoring practices, and overall effectiveness.All times in this report are approximate and Central Daylight Tune unless noted otherwise.
446 | 4462003005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462003005R00.pdf | 2003-12-22 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 99 | On December 22, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at 99.5 percent power. At 0827 hours, during collection of voltage and current data readings from the operating 2-01 Main Generator rotor, a stroboscope lamp reflector assembly was inadvertently contacted, became dislodged, and migrated into the rectifier wheel. This caused a phase to phase fault in the Main Generator exciter which resulted in a Main Turbine trip followed by an automatic reactor trip.TXU Generation Company LP (TXU Energy) believes that the cause of the event was improper reassembly of the stroboscope. Corrective actions include enhancing the work instructions for disassembly and reassembly of stroboscopes and issuing a Lessons Learned on this event to personnel that are regularly involved in Main Generator work.All times in this report are approximate and Central Standard Time unless noted otherwise.
446 | 4462006002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462006002R00.pdf | 2006-10-27 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Comanche Peak 2 | P | WE | PO | 28 | On October 27, 2006, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at approximately 28% power following the completion of the ninth refueling outage. During turbine load reject testing, a transient was initiated in the secondary system that resulted in a Steam Generator 2-02 Hi Hi level before manual control could be achieved. This resulted in the generation of a P14 signal causing a turbine trip and a Main Feedwater (MFW) pump trip. A manual reactor trip was initiated due to a loss of MFW. Auxiliary Feedwater automatically started and all systems responded normally during and following the trip.The cause of this event was the initiation of an oscillation in the Main Steam system while implementing a load rejection test which caused indicated steam flow to oscillate between 0 and 1.4Mlb/HR. The MFW, Heater Drain, and Steam Dump control systems were not able to dampen the oscillations. This caused steam flow and feed flow fluctuations that resulted in a turbine trip, MFW pump trip, and subsequently a manual reactor trip. Corrective actions include evaluating changes in the dampening for control inputs in the secondary system and training to ensure lessons learned from this event are shared. All times in this report are approximate and Central Time unless noted otherwise.
446 | 4462006003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462006003R00.pdf | 2006-10-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 2 | P | WE | PO | 80 | On October 29, 2006, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at approximately 80% power following the completion of the ninth refueling outage. While holding for xenon stabilization in preparation for incore/excore calibration, a "Steam Generator 3 Steam and Feedwater Flow Mismatch" was received. Manual control of the Steam Generator (SG) 3 Feedwater regulating valve was taken, but operators were unable to control feed flow. A manual reactor trip was initiated in anticipation of an automatic reactor trip on SG3 Lo Lo level. Auxiliary Feedwater automatically started on low-low level in SG 3. All systems responded normally during and following the trip.The cause of this event was believed to be a loose wire on a Unit 2 Feedwater regulating valve Weidmuller terminal block. Corrective actions included tightening the loose wire and inspecting the connections in other safety related Unit 2 Feedwater regulating valve and bypass valve terminal boxes. Future actions include inspecting the connections for safety related Unit 1 Feedwater regulating valve and bypass valve terminal boxes and checking the tightness of both the instrument and field terminals on all Weidmuller terminal blocks whenever either side of a circuit is being worked on a Weissmuller terminal block. All times in this report are approximate and Central Time unless noted otherwise.
446 | 4462008001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462008001R00.pdf | 2008-03-16 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On March 16, 2008, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1137 hours, the Unit 2 Main Turbine tripped due to a sensed loss of condenser vacuum and the Main Turbine trip caused an automatic reactor trip. All control rods fully inserted, and all three Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the reactor trip.The cause of this event was a sheared common vacuum instrument sensing line to the Main Condenser 2B due to the sensing line being designed and installed without adequate flexibility. The failure was ultimately the result of a combination of residual stress induced by condenser movement and cyclic stress due to vibration. Immediate corrective actions included repair of the sheared vacuum instrument sensing line and modification of the supports on the Unit 1 and 2 sensing lines. The passive single point failure vulnerability was removed on Unit 2 during the tenth refueling outage and it will be removed on Unit 1 during the next refueling outage.All times in this report are approximate and Central Time unless noted otherwise.
446 | 4462011002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462011002R00.pdf | 2011-05-19 | QR6 | Manual Reactor Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On 5/19/2011, at approximately 1407 hours, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was manually tripped due to high sodium concentration in all four steam generators. Unit 2 was operating at 100 percent power at normal operating temperature and pressure when chemistry instrumentation indicated a condenser tube leak. Steam generator sodium concentrations rapidly exceeded the manual trip criteria. All systems responded normally during and following the manual reactor trip.The leak from two condenser tubes was caused by a falling object impacting the tube exteriors. All tubes considered to have been susceptible to damage were examined by eddy current testing and visual exams. Leaking or damaged tubes were plugged and the unit was returned to 100 percent power once chemistry parameters were reestablished within limits.All times in this report are approximate and Central Standard Time unless noted otherwise.
446 | 4462012002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462012002R00.pdf | 2012-11-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On November 17, 2012, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1023 hours, the Unit 2 reactor automatically tripped due to low steam generator water level. All control rods fully inserted and all three Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the event.The cause of this event was the planning process did not provide instructions for mounting the air pressure regulator for the Heater Drain pump discharge valve. The valve was reassembled without properly supporting the pressure regulator which allowed vibration to occur in the tubing. This eventually caused a swage-lok fitting fatigue failure which resulted in the loss of air and closure of the Heater Drain pump discharge valve. This resulted in the loss of one main Feedwater pump and an automatic reactor trip on low steam generator water level.Immediate corrective actions included replacement of the broken fitting and mounting of the air pressure regulator to the actuator of the Heater Drain pump discharge valve. As a part of the CPNPP Corrective Action Program, procedures will be revised to ensure that the planning process contains specific instructions for installation of an alternate part if required.All times in this report are approximate and Central Time unless noted otherwise.
446 | 4462013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462013002R00.pdf | 2013-11-01 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | At 2146 Central Standard Time (CST) on 11/1/2013, Unit 2 was in Mode 1 at 100% power when the reactor tripped during Solid State Protection System (SSPS) slave relay testing. This test utilizes a blocking circuit to verify the operability of the slave relay which trips the main turbine and both main feedwater pump turbines, on a Hi-Hi steam generator level or safety injection (SI). While positioning the slave relay switch in a testing lineup, the relay actuated. The Unit 2 turbine tripped as well as both main feedwater pumps. The trip of both main feedwater pumps started all three Auxiliary Feedwater (AFW) Pumps. All systems responded as expected. The cause of the Unit 2 reactor trip was an original design issue with the main turbine test cabinet. The corrective action is to add a test signal electrical interlock with the blocking relay to prevent slave relay actuation until the block is established for test circuits in Units 1 and 2. All times in this report are approximate and CST unless noted otherwise.
446 | 4462015002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462015002R00.pdf | 2015-10-03 | QP5 | Excessive Feedwater Flow | [45 empty] | Comanche Peak 2 | P | WE | PO | 47 | On October 3, 2015, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at approximately 43% power shutting down for the 15th refueling outage. During the shutdown, a Steam Generator (SG) 2-03 level deviation alarm was received. Manual control of the SG 2-03 Feedwater flow control valve was taken, but Operators were unable to control feed flow. At 0958, a manual reactor trip was initiated in anticipation of an automatic turbine trip at the P-14 setpoint. The Motor Driven Auxiliary Feedwater (AFW) pumps were manually started per Operations procedures to control AFW flow, minimize cool down, and maintain SG levels. All systems responded normally during and following the reactor trip. <br /><br /> The cause of this event was determined to be a manufacturing defect in the SG 2-03 feedwater flow control valve positioner upper O-ring. Corrective actions include replacement of all four Unit 2 feedwater flow control valve positioners and establishment of periodic monitoring of feedwater flow control valve demand as an early detection of a positioner failure. <br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
446 | 4462017002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462017002R00.pdf | 2017-09-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On September 1, 2017 CPNPP Unit 2 was manually tripped by Control Room Operators due to two dropped rods. All safety systems responded as designed including the automatic start of the Auxiliary Feedwater System. The proximate cause of the dropped rods was a high resistance condition on a single phase of a three phase fusible knife switch in a Rod Control System Power cabinet. Subsequent third party cause analysis was unable to determine the root cause of the high resistance condition. The defective switch was replaced. Additional corrective actions to avoid recurrence have been entered into the CPNPP Corrective Action Program. <br /><br /> All times below are in Central Standard Time (CDT). <br /><br /> I. DESCRIPTION OF THE REPORTABLE EVENT<br /><br /> At time 2140 [CDT] on September 1, 2017, CPNPP Unit 2 experienced two (2) dropped rods, one control, one shutdown. The reactor was then manually tripped. The Auxiliary Feedwater system automatically started as expected.
446 | 4462017003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462017003R00.pdf | 2017-11-25 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Comanche Peak 2 | P | WE | PO | 100 | On November 25, 2017 Comanche Peak, Unit 2 received alarms indicating a trip of both main feedwater pumps. After confirming a decreasing water level in all four steam generators, the control room initiated a manual reactor trip. All safety systems responded as designed including the automatic start of the auxiliary feedwater system. The cause of the trip of both main feedwater pumps could not be positively identified. Causal analysis indicates that a prior plant modification maintained power to abandoned relays in the Solid State Protection System that may have caused both main feedwater pumps to trip. Subsequent actions were taken to remove the fuses that provided power to the abandoned relays on both Unit 1 and Unit 2 to eliminate recurrence from this possible source. Additional corrective actions have been entered into the Comanche Peak Corrective Action Program. <br /><br /> All times below are in Central Standard Time (CST).
446 | 4462018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4462018001R01.pdf | 2018-08-13 | QR5 | Turbine Trip | [45 empty] | Comanche Peak 2 | P | WE | PO | 100 | On August 13, 2018, Comanche Peak Nuclear Power Plant, Unit 2 experienced an automatic reactor trip due to an automatic turbine trip Unit 2 was at approximately 100% reactor power when the turbine tripped. Because reactor power was greater than 50% power an automatic reactor trip was initiated. The automatic turbine trip was caused by a loss of generator excitation. The loss of generator excitation also caused a generator lockout One channel of the main generator voltage regulator failed due to a power supply failure and automatically swapped to the backup channel. The primary function of the power supply that failed was to supply power to the firing thyristor in the Thyristor Voltage Regulator (TVR). Upon loss of power, firing was not possible and excitation current fell rapidly The primary channel swapped to manual prior to changing over to the backup channel The backup channel was in manual when it assumed control due to the TVR being in manual (from the primary channel) at the time of fail over. Corrective actions include replacing the failed power supply and evaluating modification of the excitation system. <br /><br /> Analysis did not identify any changes to the original submittal of LER 2-18-001-00. The failure described was the cause of the event and main generator and main turbine protection system performed as designed in response to the failed power supply. <br /><br /> All times are in Central Daylight Time (CDT).
454 | 4541987017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541987017R01.pdf | 1987-07-29 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 1 | P | WE | PO | 98 | POWER LEVEL - 098%. ON 7/29/87 AT 2211, AND AGAIN ON 7/31/87 AT 0153, LIGHTNING STRIKES WERE SUSPECTED THE CAUSE IN THE DE-ENERGIZATION OF POWER SUPPLIES IN THE UNIT ONE ROD DRIVE SYSTEM. THIS RESULTED IN UNIT ONE REACTOR TRIPS FROM HIGH NEGATIVE FLUX RATE ON BOTH DATES. INVESTIGATIVE EFFORTS WERE DIVIDED INTO THREE AREAS. 1) THE ROD DRIVE SYSTEM WAS THOROUGHLY INSPECTED AND TESTED. NO DISCREPANCIES WERE FOUND. A MODIFICATION WAS MADE TO THE GROUND SCHEME ON THE UNIT ONE ROD DRIVE CABINETS TO MATCH THE UNIT TWO CONFIGURATION. IT IS THEORIZED THIS MODIFICATION WILL MINIMIZE SUSCEPTIBILITY OF THE ROD DRIVE SYSTEM TO CIRCULATING CURRENTS INDUCED BY LIGHTNING STRIKES. 2) THE SYSTEM GROUND GRID WAS CHECKED BY THE OPERATIONAL ANALYSIS DEPARTMENT. NO ANOMALIES WERE NOTED. 3) THE LIGHTNING PROTECTION SYSTEMS FOR BOTH UNITS WERE WALKED DOWN AND COMPARED. NO DIFFERENCES WERE NOTED AND THE PRECISE LOCATION OF THE STRIKE COULD NOT BE DETERMINED. ON 7/13/85 A LIGHTNING STRIKE CAUSED A REACTOR TRIP AND THE FAILURE OF SEVERAL OTHER PLANT INSTRUMENTS. MODIFICATIONS TO THE LIGHTNING PROTECTION SYSTEM WERE MADE AS A RESULT OF THAT STRIKE. THIS WAS REPORTED IN LER 454/85-068.
454 | 4541987017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541987017R01.pdf | 1987-07-31 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 1 | P | WE | PO | 30 | POWER LEVEL - 098%. ON 7/29/87 AT 2211, AND AGAIN ON 7/31/87 AT 0153, LIGHTNING STRIKES WERE SUSPECTED THE CAUSE IN THE DE-ENERGIZATION OF POWER SUPPLIES IN THE UNIT ONE ROD DRIVE SYSTEM. THIS RESULTED IN UNIT ONE REACTOR TRIPS FROM HIGH NEGATIVE FLUX RATE ON BOTH DATES. INVESTIGATIVE EFFORTS WERE DIVIDED INTO THREE AREAS. 1) THE ROD DRIVE SYSTEM WAS THOROUGHLY INSPECTED AND TESTED. NO DISCREPANCIES WERE FOUND. A MODIFICATION WAS MADE TO THE GROUND SCHEME ON THE UNIT ONE ROD DRIVE CABINETS TO MATCH THE UNIT TWO CONFIGURATION. IT IS THEORIZED THIS MODIFICATION WILL MINIMIZE SUSCEPTIBILITY OF THE ROD DRIVE SYSTEM TO CIRCULATING CURRENTS INDUCED BY LIGHTNING STRIKES. 2) THE SYSTEM GROUND GRID WAS CHECKED BY THE OPERATIONAL ANALYSIS DEPARTMENT. NO ANOMALIES WERE NOTED. 3) THE LIGHTNING PROTECTION SYSTEMS FOR BOTH UNITS WERE WALKED DOWN AND COMPARED. NO DIFFERENCES WERE NOTED AND THE PRECISE LOCATION OF THE STRIKE COULD NOT BE DETERMINED. ON 7/13/85 A LIGHTNING STRIKE CAUSED A REACTOR TRIP AND THE FAILURE OF SEVERAL OTHER PLANT INSTRUMENTS. MODIFICATIONS TO THE LIGHTNING PROTECTION SYSTEM WERE MADE AS A RESULT OF THAT STRIKE. THIS WAS REPORTED IN LER 454/85-068.
454 | 4541987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541987018R01.pdf | 1987-08-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 1 | P | WE | PO | 97 | POWER LEVEL - 097%. ON AUGUST 11 BYRON UNIT ONE WAS AT 97% POWER WHEN AN ALARM FOR THE 1B FEEDWATER PUMP THRUST BEARING WEAR ANNUNCIATED. A UNIT LOAD REDUCTION WAS INITIATED TO FACILITATE TAKING THE FEEDWATER PUMP OFF LINE. THEN THE PUMP TRIPPED. A LOAD REDUCTION TO 50% POWER WAS INITIATED, BUT NOT IN TIME AS THE REACTOR TRIPPED ON LOW STEAM GENERATOR LEVEL. ALL PLANT SAFETY SYSTEMS RESPONDED AS EXPECTED. A FEEDWATER ISOLATION SIGNAL WAS GENERATED AT 1129 BY A HIGH-2 LEVEL IN THE 1C STEAM GENERATOR LEVEL. THE ACTUATION ALERTED THE OPERATORS TO THE PROBLEM, AND THEY ISOLATED FLOW TO THE AFFECTED STEAM GENERATOR AND RESTORED THE LEVEL TO NORMAL. THE THRUST BEARING WEAR CIRCUITRY WAS CHECKED AND A BROKEN WIRE TO ONE OF THE PROXIMITY PROBES WAS FOUND. THE WIRE WAS REPAIRED AND THE INSTRUMENT CALIBRATED. TO ENSURE THE PUMP WAS OPERABLE, A CHECK OF THE SHAFT PLAY WAS DONE. NO EXCESSIVE WEAR WAS DETECTED. DURING THE STARTUP THE FEEDWATER PUMP WAS MONITORED AND FOUND TO HAVE NO OPERATIONAL PROBLEMS.
454 | 4541987019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541987019R02.pdf | 1987-08-12 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Byron 1 | P | WE | SU | 6 | POWER LEVEL - 006%. ON 8/12/87 BYRON UNIT 1 WAS AT 6.5% POWER RETURNING TO POWER OPERATIONS. DURING THE THROTTLE TO GOVERNOR VALVE TRANSFER ON THE MAIN TURBINE, A THROTTLE VALVE FAILURE INITIATED EVENTS LEADING TO A TURBINE OVERSPEED. MANUAL CONTROL OF THE TURBINE WAS TAKEN IN ORDER TO REDUCE TURBINE SPEED. ONCE THE SPEED WAS REDUCED THE OPERATOR RETURNED THE TURBINE CONTROLLER BACK IN THE AUTO MODE OF OPERATION. WHEN AUTO WAS SELECTED THE GOVERNOR VALVES WENT OPEN RESULTING IN A REACTOR TRIP AND SAFETY INJECTION. THE INTERMEDIATE CAUSE FOR THE THROTTLE VALVE FAILING CLOSED WAS DETERMINED TO BE A FAILED MOOG SERVO VALVE. THE ROOT CAUSE FOR THE VALVE'S FAILURE IS THAT THE NEGATIVE NULL BIAS FOR THE MOOG VALVE WAS GREATER THAN THE MAXIMUM ALLOWABLE VALUE. THE DEFECTIVE MOOG SERVO VALVE WAS REPLACED AND A THROTTLE VALVE TO GOVERNOR VALVE TRANSFER WAS SIMULATED REPEATEDLY TO ENSURE THAT THE CORRECTIVE ACTIONS WERE SUCCESSFUL. PLANT STARTUP PROCEDURES HAVE BEEN REVISED TO INSTRUCT THE OPERATOR TO TRIP THE TURBINE IF MANUAL CONTROL HAS TO BE TAKEN PRIOR TO SYNCHRONIZATION IN ORDER TO REINITIALIZE THE TURBINE CONTROLLER. THERE HAS BEEN NO PREVIOUS REPORTABLE EVENTS.
454 | 4541988002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541988002R00.pdf | 1988-04-18 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 1 | P | WE | PO | 98 | POWER LEVEL - 098%. AT 2120 ON APRIL 18, 1988, A LICENSED REACTOR OPERATOR MANUALLY INSERTED THE CONTROLLING BANK OF CONTROL RODS ONE STEP TO ADJUST AXIAL FLUX DIFFERENCE. THE 'POWER RANGE FLUX RATE HIGH REACTOR TRIP' ANNUNCIATOR ACTUATED AND THE REACTOR TRIP BREAKERS OPENED. CONTROL ROOM OPERATORS ENTERED AND COMPLIED WITH 'REACTOR TRIP OR SAFETY INJECTION UNIT 1 EMERGENCY PROCEDURE.' THE AUXILIARY FEEDWATER PUMPS STARTED DUE TO LOW-LOW STEAM GENERATOR LEVELS THAT RESULTED FROM THE TRIP AT HIGH POWER. STABLE PLANT CONDITIONS WERE ACHIEVED IN HOT STANDBY AT 2230 ON APRIL 18, 1988. THE INTERMEDIATE CAUSE OF THE REACTOR TRIP WAS THE DROPPING ONF ONE OR MORE CONTROL RODS INTO THE REACTOR CORE, WHICH RESULTED IN THE FLUX HIGH NEGATIVE RATE REACTOR TRIP. TROUBLESHOOTING EFFORTS FAILED TO DETERMINE A ROOT CAUSE OF THE DROPPED RODS. IT IS BELIEVED THAT AN INTERMITTENT COMPONENT FAILURE IN THE ROD CONTROL SYSTEM CAUSED THE EVENT, BUT THE COMPONENT DID NOT REMAIN IN THE FAILED MODE FOLLOWING THE REACTOR TRIP. EXTENSIVE TROUBLESHOOTING WAS CONDUCTED TO LOCATE DISCREPANCIES THAT MAY HAVE CAUSED THE ROD DROP. A NUMBER OF LOOSE ELECTRICAL CONNECTIONS WERE IDENTIFIED IN THE ROD CONTROL POWER CABINETS AND ALL WERE REPAIRED.
454 | 4541988004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541988004R00.pdf | 1988-07-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 1 | P | WE | PO | 98 | POWER LEVEL - 098%. UNIT 1 WAS AT 98 PERCENT REACTOR POWER AT 0431 ON JULY 16, 1988, WHEN THE 1B MAIN FEEDWATER PUMP (MFP) TRIPPED. STEAM GENERATOR (S/G) LEVELS DECREASED DUE TO THE FEEDWATER FLOW-STEAM FLOW MISMATCH. IN SPITE OF LICENSED OPERATOR ACTIONS TO REDUCE STEAM FLOW AND INCREASE FEED FLOW, 1D S/G LEVEL DECREASED TO THE LOW-LOW REACTOR TRIP SETPOINT AT 0434. AN AUTOMATIC REACTOR TRIP OCCURRED AND BOTH AUXILIARY FEEDWATER PUMPS AUTOMATICALLY STARTED. THE LICENSED OPERATORS COMPLIED WITH EMERGENCY OPERATING PROCEDURES AND BROUGHT THE PLANT TO A STABLE CONDITION IN HOT STANDBY AT 0530. THIS REPORT IS SUBMITTED IN ACCORDANCE WITH 10CFR50.73(A)(2)(IV) DUE TO THE AUTOMATIC SAFETY SYSTEM ACTUATIONS. THE 1B MFP'S PRECISION TACHOMETER FAILED. THE TACHOMETER TRANSMITTED A CONSTANT INCREASE SPEED OUTPUT SIGNAL TO THE TURBINE'S AUTOMATIC SPEED CONTROL CIRCUITRY. TURBINE SPEED INCREASED UNTIL IT REACHED THE OVERSPEED TURBINE TRIP SETPOINT AND TRIPPED. THE TACHOMETER WAS REPAIRED AND 1B MFP OPERATION WAS MONITORED DURING THE SUBSEQUENT UNIT STARTUP. THE PUMP WAS RETURNED TO SERVICE WITHOUT INCIDENT. A SIMILAR PREVIOUS OCCURRENCE WAS REPORTED IN UNIT 2 LICENSEE EVENT REPORT 87-009.
454 | 4541988005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541988005R01.pdf | 1988-08-04 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 98 | POWER LEVEL - 098%. AT 0047 ON 8/4/88, WITH UNIT 1 AT 98% AND UNIT 2 AT 95% REACTOR POWER, 2 STABILITY TRIP ENABLE ANNUNCIATORS ACTUATED SIMULTANEOUSLY IN THE MAIN CONTROL ROOM AND THE 'UNIT STABILITY GENERATOR TRIP' ANNUNCIATOR ACTUATED. THE UNIT 1 MAIN GENERATOR OUTPUT BREAKERS OPENED AUTOMATICALLY. THE MAIN TURBINE AUTOMATICALLY TRIPPED, AS DID THE REACTOR. FOLLOWING THE REACTOR TRIP ALL STEAM GENERATOR LEVELS RAPIDLY DECREASED AND BOTH AUX. FEEDWATER PUMPS AUTOMATICALLY STARTED. A POST TRIP, EXPECTED FEEDWATER ISOLATION OCCURRED. THE LICENSED OPERATORS IMPLEMENTED THE APPROPRIATE EMERGENCY OPERATING PROCEDURES AND UNIT 1 ACHIEVED STABLE CONDITIONS IN HOT STANDBY AT 0120. THE UNIT TRIP OCCURRED DUE TO A SIGNAL GENERATED BY THE UNIT STABILITY TRIP SYSTEM, WHICH INDICATED THAT THE ELECTRICAL GRID CONFIGURATION COULD NOT DISTRIBUTE THE POWER OUTPUT OF BOTH BYRON UNITS. THE ACTUAL GRID CONFIGURATION WAS CORRECT AND CAPABLE OF DISTRIBUTING THE POWER OUTPUT, HOWEVER, NOISE ON THE MICROWAVE CIRCUIT THAT COMMUNICATES GRID STATUS TO BYRON STATION YIELDED FALSE INDICATIONS. THE FALSE DATA SATISFIED THE TRIP SYSTEM COINCIDENCE AND GENERATED THE AUTOMATIC MAIN GENERATOR TRIP. CORRECTIVE ACTIONS WERE TAKEN TO DISABLE THE UNIT STABILITY GENERATOR TRIPS AND TO RESTRICT POWER OUTPUT FROM BYRON STATION. CE'S OPERATIONAL ANALYSIS DEPT. HAS REPLACED THE SINGLE MICROWAVE CHANNEL WITH 4 SEPARATE CHANNELS.
454 | 4541989002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541989002R00.pdf | 1989-01-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Byron 1 | P | WE | PO | 99 | POWER LEVEL - 099%. UNIT 1 WAS OPERATING AT 99% POWER AT 0956 ON 1/31/89, WHEN THE REACTOR TRIPPED MANUALLY. LEVEL IN STEAM GENERATOR 1C WAS INCREASING BECAUSE ITS FEEDWATER REGULATING VALVE (1FW530) HAD FAILED FULLY OPEN. THE VALVE WOULD NOT RESPOND TO AUTOMATIC OR MANUAL CONTROLS. THE REACTOR TRIP WAS PRUDENT BECAUSE STEAM GENERATOR 1C LEVEL WAS RAPIDLY APPROACHING ITS HIGH-LEVEL AUTOMATIC FEEDWATER ISOLATION SETPOINT (P-14). ALL SAFETY SYSTEMS FUNCTIONED AS DESIGNED. THE UNIT WAS STABILIZED IN HOT STANDBY AT APPROXIMATELY 1114. FEEDWATER REGULATING VALVE 1F2530 WAS FOUND TO HAVE ITS VALVE POSITIONER FEEDBACK ARM DISENGAGED FROM THE VALVE FOLLOWER. NEITHER MANUAL NOR AUTOMATIC CONTROL WAS POSSIBLE WITH THE VALVE IN THIS CONDITION. THE VALVE POSITIONER WAS RECONNECTED USING LOCKTITE AND A STAR WASHER TO PREVENT FUTURE FAILURES. SIMILAR PREVENTATIVE ACTION WAS PERFORMED ON THE REMAINING REGULATING VALVES ON BOTH UNITS.
454 | 4541990006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541990006R00.pdf | 1990-05-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 1 | P | WE | PO | 79 | On 5/03/90, at 0300, with Unit 1 operating at 79% power, the Operating Department began surveillance 1BOS 3.4.2.a-1, "Turbine Throttle, Governor, Reheat, and Intercept Valve Monthly Surveillance." At 0359, the surveillance was held to accommodate troubleshooting on the turbine Digital Electro-Hydraulic Computer (DEHC). Due to the repeated failure of a 2 ampere fuse on 1 of 4 loops on power supply card C1-H35, the turbine runback pushbutton was removed to prevent a runback signal. As the surveillance continued, all indication on the DEHC panel was lost. <br /><br /> The 5 ampere fuse on the same card was blown. As a replacement fuse was inserted, a 100 Megawatt power excursion occurred, followed by a complete load rejection. At 0631, a reactor trip occurred on Low-2 Steam Generator Level. <br /><br /> The 2 ampere fuse failed due to a short circuit in the pushbutton. The button was equipped with a grounded copper screen. When the button was moved inside the socket, the screen came in contact with the pushbutton light's power supply which induced a short and blew the fuse. The root cause for the 5 ampere fuse failure and subsequent reactor trip remain indeterminate. <br /><br /> As corrective action, the screens in all the pushbuttons were removed. The lighting circuit was also rewired to be made separate from the runback circuitry so a loss of indication will not effect a runback signal.<br /><br /> This event is reportable per 10CFR50.73 (a)(2)(iv) for an event that resulted in an automatic actuation of an Engineered Safety Feature, including the Reactor Protection System.
454 | 4541990011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541990011R00.pdf | 1990-08-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 1 | P | WE | PO | 78 | At 0425 on August 19, 1990, with severe lightning activity near Byron Station, a Unit 1 reactor trip occurred from 78% power. A lightning strike induced a voltage surge that activated nine out of ten over-voltage protection devices installed on power supplies in the rod drive (RD) AA! power cabinets. This activation released twelve out of fifteen rod control cluster assembly groups into the core and resulted in a high negative flux rate reactor trip. <br /><br /> Due to several Commonwealth Edison and industry wide lightning induced reactor trips, several modifications have previously been made to both the containment lightning protection system and the rod drive over voltage protectors. <br /><br /> The Rod Drive System will be further modified with a new model of power supply that is less likely to cause a reactor trip after a transient caused by lightning. <br /><br /> This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as a result of the automatic actuation of the Reactor Protection System.
454 | 4541990014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541990014R00.pdf | 1990-12-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Byron 1 | P | WE | PO | 98 | On December 3, 1990, at 1240 while performing scheduled Slave Relay Surveillance 1BOS 3.2.1-980 "Unit One Engineered Safeguard Features Actuation System Instrumentation Slave Relay Surveillance (Train A Feedwater Isolation, Reactor Trip K637)" an actual Feedwater (FW) SJ! Isolation Signal (FWI) was generated causing a loss of feedwater. A Reactor trip on low-2 Steam Generator level in the 1D Steam Generator ensued. All components associated with a FWI/Reactor trip responded as expected with the exception of valve 1FW039A which had dual position indication.<br /><br /> During performance of the surveillance, switch S817 is placed in a "Push to Test" position. After pushing in the switch and verifying indications, the system must be restored by resetting three switches in sequence. S817 is one of the three switches and should be the last to be restored to its normal position. Contrary to the procedure, the S817 switch was restored to its normal position first immediately after the "Push to Test" step was performed. The Feedwater Isolation occurred several steps later when the switch that is normally first to be reset was reset second. The FW Isolation Auxiliary Relays are a latching type and had not been reset with the remaining switch prior to removing the testing block with the other two switches.<br /><br /> Electrical Maintenance Department performed an inspection of S817. No problems were found with the switch. Operating Department Technical Specification surveillance 1BOS 3.2.1-980 was re-performed verifying operability. Required Listening 90-042 for Nuclear Station Operators describing the details of this event was developed and conducted prior to resuming Slave Relay Testing. A note will be added to the appropriate procedures indicating that this is not a spring return to normal switch. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) as any event or condition that resulted in manual or automatic actuation of any Engineered Safeguard Feature.
454 | 4541992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541992001R00.pdf | 1992-01-29 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 93 | On 01/29/92, Unit One Reactor tripped as a result of a Turbine trip from an anti-motoring signal. Maintenance was being performed on a valve labelled 1MS096B, which isolates pressure transmitter 1PT-506. This valve was not properly labelled and in fact was 1MS096C which isolated 1PDS-T0071, the anti-motoring relay. This isolation resulted in low differential pressure signal across the High Pressure Turbine and actuated the anti-motoring Turbine trip and thus the Reactor trip occurred. The incorrect valve tags were removed and replaced with correct tags. The other unit was also found to have incorrect valve tags. <br /><br /> The incorrect tags were replaced except for one located in an inaccessible area. This will be replaced at a later date. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv).
454 | 4541994009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541994009R00.pdf | 1994-09-08 | QR8 | Spurious Reactor Trip | [45 empty] | Byron 1 | P | WE | PO | 10 | Event 1: On September 8, 1994 at 01:25, Byron Unit 1 unexpectedly tripped at approximately 10 percent power. The event occurred during a controlled shutdown for the sixth refueling outage on Byron Unit 1 (B1R06). The unit tripped from high flux on source range (SR) nuclear instrument channel 31 (N31) [IG]. SR N31 re-energized when permissive P10 energized. Both intermediate range (IR) nuclear instrumentation channels (N35, N36) [IG] were above P6. The probable cause of the reactor trip was a faulty logic card in the Solid State Protection System (SSPS) [JG]. This generated a P6 signal for SR N31 before both IR channels were below the setpoint for P6. The Permissive Signal P6 setpoint for re-energizing the SR channels is less than 1.0 E-10 amps on both IR channels. The failure mode of the faulty logic cards was not determined. The failed cards were replaced.<br /><br /> Event 2: On September 8, 1994, at 14:52, a second reactor trip signal occurred. The signal was from high flux on SR N31. Station personnel inadvertently generated the signal during trouble shooting activities. The personnel were investigating the spurious P6 signal that caused the 01:25 reactor trip. Unit 1 was in Mode 3 with all control rods filly inserted. The cause of this event was a personnel error during the trouble shooting activities. Awareness of the cause of this event was heightened with the affected departments. <br /><br /> These events are reportable under 10CFR50.73(a)(2)(iv) as a Reactor Protection System Actuation.
454 | 4541996011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541996011R01.pdf | 1996-07-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 1 | P | WE | SU | 15 | POWER LEVEL - 015%. On 07/02/96 at approximately 0312, the 1B Steam Generator Feedwater Preheater Bypass Isolation Valve failed close due to a broken Instrument Air line. This valve failure resulted in inadequate feedwater to the 1B steam generator. The Unit 1 Reactor was manually tripped prior to reaching the automatic trip on Lo-2 steam generator level. The valve closed due to a broken fitting that supplied air to the actuator. The piping that supplies air to this actuator is copper with soldered joints. One of these soldered joints broke causing the failure. The failed tubing was replaced. The section of tubing that failed was sent to System Materials Analysis Dept. (SMAD) for determination of the specific failure mode. This event is reportable pursuant to the requirements of 10CFR50.73(a)(1) and 50.73(a)(2)(iv).
454 | 4541996017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541996017R00.pdf | 1996-09-11 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 97 | On 09/11/96, with Unit 1 in Mode 1 at 96.5% power, Operators were preparing to perform a monthly surveillance of the Turbine Protection System. Before beginning the surveillance, an Aux Operator erroneously placed a lever actuating tool on the local Turbine Protection System TRIP lever handle instead of the intended TEST lever handle. The Aux Operator realized his error. During attempts to remove the lever actuating tool, the trip lever handle was moved, and a Turbine Trip was generated. Because the Reactor was above 30% power, this also caused an automatic Reactor Trip. The Reactor Trip resulted in an actuation of the Unit 1 Engineered Safety Features equipment. All automatic safety system actuations occurred as designed.<br /><br /> The Root Cause of this event was the Aux Operator's overconfidence concerning his ability to remove the lever actuating tool from the TRIP lever actuating the turbine trip. Coupled with his reflex reaction in attempting to remove the tool, this resulted in the Main Turbine trip and associated Reactor trip. <br /><br /> To prevent recurrence, a barrier was placed over the hub of the Turbine Trip lever to physically prevent the lever actuation tool from being placed over the local trip lever. Also, the Auxiliary Operator has received counseling.<br /><br /> This event resulted in an actuation of the Engineered Safety Features. It is, therefore, a reportable event per 10CFR 50.73(a)(2)(iv).
454 | 4541999003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541999003R00.pdf | 1999-05-13 | QR8 | Spurious Reactor Trip | [45 empty] | Byron 1 | P | WE | PO | 100 | On May 13, 1999, at 0810 hours, with Byron Station Unit 1 at 100% power, an Instrument Maintenance Technician (IM) inadvertently caused a Reactor Trip System (RTS) automatic actuation. This occurred during the performance of the Technical Specification Surveillance Requirement (SR) for the Power Range Neutron Flux Instrumentation channel. The SR being performed was the 92 day frequency Channel Operational Test (COT). The IM mistakenly removed instrument fuses from a channel adjacent to the channel he had placed in test for the surveillance procedure. This action caused the two of four coincidence logic to be satisfied for the generation of an automatic reactor trip. Operators responded using appropriate procedures. The cause of the trip was a human performance error by the IM conducting the surveillance procedure. There were no safety consequences impacting plant or public safety as a result of the event. The FITS functioned as designed. Corrective actions include appropriate Management action with the IM involved and re-enforcement of human performance expectations with all Maintenance Department personnel. There was one previous occurrence involving an RTS actuation due to a human performance cause reported in Byron Station Licensee Event Report 454-96-17. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv).
454 | 4542002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4542002003R00.pdf | 2002-10-15 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 100 | On October 15, 2002, at approximately 1217 hours, the Unit 1 reactor automatically tripped due to a Reactor Coolant (RC) over temperature condition. The immediate cause of the RC over temperature condition was the turbine governor valves closing causing a loss of turbine load. A malfunction in the Digital Electrohydraulic Control (DEHC) System was apparent, however thorough diagnostic testing could not 'identify any problems with the DEHC system. Four circuit cards with a high probability of causing this type of malfunction were replaced and the unit was restarted with additional monitoring equipment. On November 7, 2002 at approximately 1247 hours, the Unit 1 reactor again automatically tripped due to a RC over temperature condition. The investigation revealed a very similar scenario between the previous trip, and this trip. However, immediate indications and subsequent diagnostic testing of the DEHC system this time revealed a failure of the Bit Logic (BL3) circuit board in the DEHC computer. The cause of both reactor trips is attributed to this malfunctioning Bit Logic '(BL3) circuit board in the DEHC computer. The circuit board malfunction was intermittent in nature and could not be diagnosed for the first reactor trip. The failure of the board was due to a single chip, type SN74H60. The cause of the failure of the chip is not determined at this time. The DEHC system computer's BL3 card was replaced. Further analysis will be conducted on the failed chip to determine the cause of the failure. There were no safety consequences impacting plant or public safety as a result of these events. The unit is designed to cope with a loss of turbine load event. In both trips, the reactor trip system functioned as designed and shut down the reactor without incident. These events are reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv).
454 | 4542002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4542002003R00.pdf | 2002-11-07 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 100 | On October 15, 2002, at approximately 1217 hours, the Unit 1 reactor automatically tripped due to a Reactor Coolant (RC) over temperature condition. The immediate cause of the RC over temperature condition was the turbine governor valves closing causing a loss of turbine load. A malfunction in the Digital Electrohydraulic Control (DEHC) System was apparent, however thorough diagnostic testing could not 'identify any problems with the DEHC system. Four circuit cards with a high probability of causing this type of malfunction were replaced and the unit was restarted with additional monitoring equipment. On November 7, 2002 at approximately 1247 hours, the Unit 1 reactor again automatically tripped due to a RC over temperature condition. The investigation revealed a very similar scenario between the previous trip, and this trip. However, immediate indications and subsequent diagnostic testing of the DEHC system this time revealed a failure of the Bit Logic (BL3) circuit board in the DEHC computer. The cause of both reactor trips is attributed to this malfunctioning Bit Logic '(BL3) circuit board in the DEHC computer. The circuit board malfunction was intermittent in nature and could not be diagnosed for the first reactor trip. The failure of the board was due to a single chip, type SN74H60. The cause of the failure of the chip is not determined at this time. The DEHC system computer's BL3 card was replaced. Further analysis will be conducted on the failed chip to determine the cause of the failure. There were no safety consequences impacting plant or public safety as a result of these events. The unit is designed to cope with a loss of turbine load event. In both trips, the reactor trip system functioned as designed and shut down the reactor without incident. These events are reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv).
454 | 4542015002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4542015002R00.pdf | 2015-03-03 | QR5 | Turbine Trip | [45 empty] | Byron 1 | P | WE | PO | 100 | At 1101 hours on March 3, 2015, Byron Station Unit 1 tripped from full power due to a phase to phase fault on the 1E Main Power Transformer (MPT) between electrical Phase A and Phase B. Before this trip, the Byron area had experienced severe weather. At the time of the event, the temperature was approximately 30 degrees F; however, temperatures had been around 23 degrees F hours earlier. An ice formation on the Phase B Bus bar that is located directly above the high voltage bushings dropped and caused a phase to phase fault between Phase A and B.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The cause of this event was due to latent design vulnerability that existed in the configuration of the Bus bar relative to the MPT bushings. The Bus bar location directly above and parallel to the MPT bushings created a condition that resulted in a phase to phase short when ice from the Bus bar fell across the bushings. The Bus bar is six inches in diameter and located approximately twenty-three feet above the top of the bushings. The 1E MPT high voltage and neutral bushings were replaced during the forced outage. Following successful testing of the 1E MPT, Byron Unit 1 was restarted.
455 | 4551987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987002R01.pdf | 1987-02-05 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Byron 2 | P | WE | PO | 6 | POWER LEVEL - 006%. ON FEBRUARY 5, 1987, BYRON UNIT 2 EXPERIENCED A FEEDWATER ISOLATION AND A REACTOR TRIP. ON FEBRUARY 14, 1987, BYRON UNIT 2 EXPERIENCED A REACTOR TRIP. ON FEBRUARY 16, 1987, BYRON UNIT 2 EXPERIENCED A FEEDWATER ISOLATION. ALL SAFEGUARD ACTUATION FEATURES FUNCTIONED AS DESIGNED. ALL THREE EVENTS HAD INTERMEDIATE CAUSES OF LICENSED NUCLEAR STATION OPERATOR'S INABILITY TO CONTROL WESTINGHOUSE MODEL D-5 STEAM GENERATOR LEVELS DURING LOW POWER TRANSIENTS. THE ROOT CAUSE IS THE LACK OF IN-HOUSE AND INDUSTRY EXPERIENCE ON WESTINGHOUSE D-5 STEAM GENERATOR LEVEL BEHAVIOR. CORRECTIVE ACTIONS INVOLVE GAINING ADDITIONAL EXPERIENCE AND DEVELOPING OPERATING STRATEGIES FOR COPING WITH THE D-5 LEVEL CONTROL. AFTER COMPLETION OF U-2'S INITIAL STARTUP TESTING PROGRAM, THE ENTIRE EXPERIENCE ON MODEL D-5 STEAM GENERATORS HAS BEEN EVALUATED FOR ACCEPTABILITY. THE RESULTS OF THIS EVALUATION ARE REPORTED IN THIS SUPPLEMENTAL LICENSEE EVENT REPORT. THERE HAVE BEEN NO PREVIOUS OCCURRENCES.
455 | 4551987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987002R01.pdf | 1987-02-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Byron 2 | P | WE | SU | 1 | POWER LEVEL - 006%. ON FEBRUARY 5, 1987, BYRON UNIT 2 EXPERIENCED A FEEDWATER ISOLATION AND A REACTOR TRIP. ON FEBRUARY 14, 1987, BYRON UNIT 2 EXPERIENCED A REACTOR TRIP. ON FEBRUARY 16, 1987, BYRON UNIT 2 EXPERIENCED A FEEDWATER ISOLATION. ALL SAFEGUARD ACTUATION FEATURES FUNCTIONED AS DESIGNED. ALL THREE EVENTS HAD INTERMEDIATE CAUSES OF LICENSED NUCLEAR STATION OPERATOR'S INABILITY TO CONTROL WESTINGHOUSE MODEL D-5 STEAM GENERATOR LEVELS DURING LOW POWER TRANSIENTS. THE ROOT CAUSE IS THE LACK OF IN-HOUSE AND INDUSTRY EXPERIENCE ON WESTINGHOUSE D-5 STEAM GENERATOR LEVEL BEHAVIOR. CORRECTIVE ACTIONS INVOLVE GAINING ADDITIONAL EXPERIENCE AND DEVELOPING OPERATING STRATEGIES FOR COPING WITH THE D-5 LEVEL CONTROL. AFTER COMPLETION OF U-2'S INITIAL STARTUP TESTING PROGRAM, THE ENTIRE EXPERIENCE ON MODEL D-5 STEAM GENERATORS HAS BEEN EVALUATED FOR ACCEPTABILITY. THE RESULTS OF THIS EVALUATION ARE REPORTED IN THIS SUPPLEMENTAL LICENSEE EVENT REPORT. THERE HAVE BEEN NO PREVIOUS OCCURRENCES.
455 | 4551987005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987005R00.pdf | 1987-03-31 | QR5 | Turbine Trip | [45 empty] | Byron 2 | P | WE | PO | 17 | POWER LEVEL - 017%. THE UNIT 2 REACTOR TRIPPED DUE TO A SPURIOUS ACTUATION OF THE TURBINE MOTORING GENERATOR TRIP CIRCUITRY. THE ROOT CAUSE OF THIS EVENT COULD NOT BE DETERMINED. THE CALIBRATION OF THE DIFFERENTIAL PRESSURE SWITCH WHICH FEEDS THE TURBINE MOTORING GENERATOR TRIP CIRCUITRY WAS CHECKED AND FOUND TO BE OUT OF TOLERANCE, HOWEVER, THE DIRECTION OF THE OUT OF TOLERANCE WOULD HAVE RESULTED IN A TRIP AT A LOWER THAN NORMAL POWER LEVEL RATHER THAN THE HIGHER THAN NORMAL LEVEL AT WHICH THIS TRIP OCCURRED. THE PRESSURE SWITCH WAS REPLACED, NEVERTHELESS. THE PRESSURE SWITCH WAS CHECKED DURING THE UNIT STARTUP AND NO ABNORMAL FUNCTIONING WAS DETECTED. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF THIS TYPE.
455 | 4551987006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987006R01.pdf | 1987-04-27 | QR8 | Spurious Reactor Trip | [45 empty] | Byron 2 | P | WE | PO | 89 | POWER LEVEL - 089%. ON APRIL 27, 1987 AT 1603, A REACTOR TRIP RESULTED WHEN THE PRESSURIZER PRESSURE SPIKED BELOW THE REACTOR TRIP SETPOINT ON CHANNEL 456, COINCIDENT WITH THE PERFORMANCE OF THE DELTA T/T AVERAGE SURVEILLANCE, WHICH PLACED THE PRESSURIZER PRESSURE CHANNEL 455 IN THE LOW TRIPPED CONDITION. THE TWO OF FOUR (2/4) REACTOR PROTECTION LOGIC WAS MET AND THE REACTOR TRIP OCCURRED. AS A RESULT OF THE UNIT'S NORMAL RESPONSE TO THE TRANSIENT, AN AUXILIARY FEEDWATER ACTUATION OCCURRED ON LOW STEAM GENERATOR LEVEL. THE UNIT WAS RESTORED TO STABLE CONDITIONS IN HOT STANDBY AT APPROXIMATELY 1650. THE MOST PROBABLE ROOT CAUSE OF THIS EVENT WAS THE PRESSURIZER PRESSURE TRANSMITTER AND THE NUCLEAR LOOP POWER SUPPLY ON CHANNEL 456 FAILING DURING THE PERFORMANCE OF THE DELTA T/T AVERAGE SURVEILLANCE. THE CORRECTIVE ACTIONS TAKEN WERE TO REPLACE BOTH THE PRESSURE TRANSMITTER AND THE NUCLEAR LOOP POWER SUPPLY. THERE WAS ONE PREVIOUS SIMILAR OCCURRENCE REPORTED IN LER 455/87-001.
455 | 4551987007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987007R01.pdf | 1987-05-04 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Byron 2 | P | WE | PO | 88 | POWER LEVEL - 088%. ON MAY 4, 1987, AT 0644, THE UNIT 2 REACTOR TRIPPED DURING THE PERFORMANCE OF THE QUARTERLY POWER RANGE CALIBRATION SURVEILLANCE ON CHANNEL NI-43. UNIT 2 WAS IN MODE 1 - POWER OPERATIONS AT 88% POWER. AS A REQUIREMENT OF THE SURVEILLANCE, THE POWER RANGE CHANNEL'S BISTABLES WERE TRIPPED. DURING THE CONDUCT OF THE SURVEILLANCE, THE INSTRUMENT BUS 211 BREAKER TRIPPED. THIS DE-ENERGIZED CHANNEL N41 AND TRIPPED ITS BISTABLES. THIS SATISFIED THE 2 OUT OF 4 LOGIC COINCIDENCE FOR HIGH NEUTRON FLUX REACTOR TRIP. AS A NORMAL RESULT, THE STEAM GENERATOR LEVEL REACHED THE LOW LEVEL AUTOMATIC AUXILIARY FEEDWATER (AF) PUMP START SETPOINT. THE 2B DIESEL DRIVEN AF PUMP STARTED, AS EXPECTED. THE 2A AF PUMP DID NOT START AS A RESULT OF THE INSTRUMENT BUS 211 TRIP. THE UNIT WAS RECOVERED CONSISTENT WITH EMERGENCY PROCEDURES WITHOUT INCIDENT. THE CAUSE OF THE INSTRUMENT BUS 211 TRIP IS DUE TO A FAILURE OF A SILICON CONTROLLED RECTIFIER AND A CAPACITOR IN THE INVERTER. THE CAPACITOR FAILURE CAUSED THE RECTIFIER FAILURE. THE FAILURE MECHANISM OF THE CAPACITOR COULD NOT BE DETERMINED AND IS ATTRIBUTABLE TO NORMAL WEAROUT. THE COMPONENTS WERE REPLACED AND THE BUS RE-ENERGIZED. THERE WERE NO ADVERSE SAFETY CONSEQUENCES.
455 | 4551987009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987009R01.pdf | 1987-06-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 98 | POWER LEVEL - 098%. AT 0921 ON JUNE 29, 1987 A MANUAL UNIT 2 REACTOR TRIP WAS INITIATED DUE TO THE 2C (TURBINE DRIVEN) MAIN FEEDWATER PUMP (FW) TRIP. THE LEVEL IN ALL FOUR STEAM GENERATORS WAS BELOW THE LO LEVEL ALARM SETPOINT AND TRENDING TOWARD THE LO-LO REACTOR TRIP SETPOINT. THE SHIFT ENGINEER (LICENSED) ORDERED THE NUCLEAR STATION OPERATOR (LICENSED) TO MANUALLY TRIP THE REACTOR IN ACCORDANCE WITH GOOD OPERATING PRACTICES. AT THE LO-LO STEAM GENERATOR LEVEL SETPOINT THE AUXILIARY FEEDWATER PUMPS (AF) AUTOMATICALLY STARTED AS DESIGNED. THE UNIT WAS STABILIZED IN MODE 3 - HOT STANDBY. THE CAUSE OF THE 2C MAIN FEEDWATER PUMP TRIP WAS A COLD SOLDER JOINT ON A CAPACITOR IN THE SPEED CONTROL FEEDBACK LOOP. THE SOLDER JOINT WAS REPAIRED AND TESTED. IN ADDITION, SELECTED PARAMETERS WILL BE MONITORED DURING SUBSEQUENT OPERATIONS TO ENSURE PROPER FUNCTIONING. THERE HAVE BEEN NO PREVIOUS OCCURRENCES.
455 | 4551987010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987010R00.pdf | 1987-07-01 | QR6 | Manual Reactor Trip | [45 empty] | Byron 2 | P | WE | PO | 32 | POWER LEVEL - 032%. AT 0605, ON JULY 1, 1987, A LOW ELECTRO-HYDRAULIC (EH) (JJ) RESERVOIR LEVEL ALARM WAS RECEIVED. AN INVESTIGATION DETERMINED THAT THERE WAS A FLUID LEAK AT THE EH SKID DUE TO A LINE BREAK. THE LEAK WAS UNISOLATABLE, CONSEQUENTLY A TURBINE POWER RAMP DOWN WAS BEGUN IN AN ATTEMPT TO BRING THE TURBINE BELOW THE REACTOR TRIP SETPOINT. AT 0628 THE EH PUMPS BEGAN TO CAVITAGE DUE TO LOW LEVEL. THE EH PUMPS WERE TRIPPED. THE REACTOR WAS ALSO TRIPPED IN ANTICIPATION OF THE IMMINENT TURBINE TRIP DUE TO LOSS OF EH PRESSURE. THE ROOT CAUSE OF THE LINE BREAK APPEARS TO BE EXCESSIVE VIBRATION. THE PRESSURE SUPPLY LINE TO THE FULLERS EARTH FILTER WHICH BROKE WAS REMOVED AND A VALVE AND NIPPLE INSTALLED FOR ISOLATION UNTIL ADDITIONAL LINE SUPPORTS CAN BE DESIGNED AND INSTALLED. THERE HAVE BEEN NO PREVIOUS EVENTS.
455 | 4551987011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987011R01.pdf | 1987-07-25 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Byron 2 | P | WE | PO | 98 | POWER LEVEL - 098%. AT 1216 ON 7/25/87, UNIT 2 TRIPPED ON AN OVERTEMPERATURE CONDITION FOLLOWING A 30% LOAD REJECTION TEST. THE CAUSE OF THE REACTOR TRIP WAS PARTIALLY DUE TO THE DIGITAL ELECTRO-HYDRAULIC (DEH) CONTROLLER BEING IN THE SEQUENTIAL VALVE MODE PROGRAM WHICH CAUSED THE GOVERNOR CONTROL VALVES TO BE IN THE MOST EFFICIENT POWER OPERATION, BUT DURING THE RUNBACK CAUSED THE VALVES TO BE IN VARYING POSITIONS CAUSING T(REF) TO WIDELY VARY. IN ADDITION, THE STEAM DUMPS DID NOT STROKE FULLY OPEN RESULTING IN DECREASED SECONDARY SIDE HEAT REMOVAL CAPABILITY. TO CORRECT THE CONDITIONS WHICH LED TO THE REACTOR TRIP, THE DEH COMPUTER HAS BEEN EXAMINED BY WESTINGHOUSE AND SOFTWARE CHANGES IMPLEMENTED. THE STEAM DUMPS WERE REPAIRED AND TESTED TO VERIFY PROPER OPERATION, AND THE FEEDWATER SYSTEM WAS FINE TUNED FOR BETTER STEAM/FEED CONTROL. LOAD REJECTION TESTS OF 30 AND 50 PERCENT HAVE SINCE BEEN SUCCESSFULLY RUN AS PART OF THE STARTUP PROGRAM.
455 | 4551987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987018R00.pdf | 1987-10-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 92 | POWER LEVEL - 092%. BYRON UNIT 2 WAS OPERATING AT 92% POWER WHEN THE 2B MAIN FEEDWATER PUMP TRIPPED. REACTOR TRIPPED DUE TO A LOW-2 STEAM GENERATOR LEVEL IN ONE STEAM GENERATOR. ALL SAFETY SYSTEMS RESPONDED AS DESIGNED. THE CAUSE WAS THE INADVERTENT ACTUATION OF THE OVERSPEED TRIP PLUNGER BY A CONTRACTOR WORKING ON THE 2B FEEDWATER PUMP HIGH PRESSURE STOP VALVE. TO PREVENT RECURRENCE THE OPERATING AND MAINTENANCE PERSONNEL WILL BE REQUIRED TO READ THIS REPORT. THE INSTALLATION OF A GUARD ON THE TRIP PLUNGER WILL BE INVESTIGATED.
455 | 4551987019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551987019R01.pdf | 1987-10-02 | QP5 | Excessive Feedwater Flow |  | X | [13 empty] | X | [29 empty] | Byron 2 | P | WE | SU | 13 | POWER LEVEL - 013%. ON OCTOBER 2, 1987, AT 0446, UNIT 2 WAS RETURNING TO SERVICE. WHEN UNIT 2 WAS SYNCHRONIZED TO THE GRID, THE STEAM GENERATOR (SG) LEVELS INCREASED AND CAUSED A HI-2 S/G LEVEL TRIP. EXCESSIVE 'LEAK BY' OF THE 2FW530 VALVE. THE HIGH S/G LEVEL CAUSED A TURBINE TRIP AND A SUBSEQUENT REACTOR TRIP BECAUSE REACTOR POWER WAS ABOVE 10%. AN EQUIPMENT OPERATOR (EO) WAS INSTRUCTED TO REALIGN THE SWITCHYARD RING BUS AFTER THE TRIP. THE EO OPENED THE SYSTEM AUX TRANSFORMER DISCONNECTS INSTEAD OF THE MAIN POWER TRANSFORMER DISCONNECTS. THE SAFETY RELATED 4KV BUSES WERE DEENERGIZED CAUSING THE EMERGENCY DIESEL GENERATORS TO START, REENERGIZE THE BUSES, AND SEQUENCE THE SAFE SHUTDOWN LOADS. THE ROOT CAUSE OF THE LOSS OF OFFSITE POWER WAS DUE TO PERSONNEL ERROR. THE EO OPENED THE WRONG DISCONNECT. THE CORRETIVE ACTIONS ARE AS FOLLOWS: DISCIPLINARY ACTION WAS TAKEN WITH THE EO; ADMINISTRATIVE PROCEDURES WERE REVISED TO ENSURE THAT NO SWITCHYARD OPERATIONS ARE PERFORMED WITHOUT A SECOND INDIVIDUAL PRESENT; PERMANENT, DESCRIPTIVE LABELS HAVE BEEN PLACED ON MPT & SAT SWITCHYARD DISCONNECTS; A WALK THROUGH OF THE SWITCHYARD WITH DIVISION SUPERINTENDENT OF POWER SUPPLY TO DEMONSTRATE PROPER OPERATIONS AND COMMUNICATIONS WAS CONDUCTED; THE SAT DISCONNECTS ARE LOCKED WITH UNIQUE LOCKS FOR EACH UNIT, ETC.
455 | 4551988001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988001R01.pdf | 1988-02-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 94 | POWER LEVEL - 094%. ON FEBRUARY 12, 1988, AT 1804 HOURS WITH BYRON UNIT 2 IN POWER OPERATION (MODE 1) AT 94% POWER, THE 2C FEEDWATER PUMP TRIPPED ON OVERSPEED. EFFORTS TO SHED LOAD WERE UNSUCCESSFUL DUE TO FAILURE OF THE DIGITAL ELECTROHYDRAULIC CONTROL SYSTEM TO RESPOND PROPERLY IN THE AUTOMATIC MODE. THIS RESULTED IN LOSS OF INVENTORY IN THE STEAM GENERATORS AND A REACTOR TRIP ON LOW STEAM GENERATOR LEVEL. ALL SAFEGUARD ACTUATION FEATURES FUNCTIONED AS DESIGNED. THE FEEDWATER PUMP TRIP WAS DUE TO A FAILED SERVOVALVE WHICH ALLOWED THE FEEDWATER PUMP TURBINE HIGH PRESSURE GOVERNOR VALVE TO FAIL OPEN. THIS CAUSED THE PUMP OVERSPEED AND TRIP. THE DEFECTIVE SERVOVALVE WAS REPLACED. THERE HAVE BEEN PREVIOUS REACTOR TRIPS DUE TO FEEDWATER PUMP TRIPS.
455 | 4551988004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988004R01.pdf | 1988-05-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 94 | POWER LEVEL - 094%. ON APRIL 27, 1988, AN OUT-OF-SERVICE CONDITION ON THE 2C MAIN FEEDWATER PUMP (MFP) WAS TEMPORARILY LIFTED TO PERMIT OPERATION OF THE MFP, AND THE PUMP WAS STARTED AND PLACED IN SERVICE. ON MAY 6 A LICENSED REACTOR OPERATOR (NSO) NOTED THAT THE TEMPORARY LIFT WAS DUE TO EXPIRE ON THAT DAY AND REQUESTED A DISPOSITION FROM A LICENSED SENIOR REACTOR OPERATOR (SCRE). THE SCRE DIRECTED THE NSO TO TERMINATE THE TEMPORARY LIFT BY RETURNING THE EQUIPMENT TO ITS ORIGINAL OUT-OF-SERVICE CONDITION. BOTH THE SCRE AND THE NSO INCORRECTLY BELIEVED THAT RETURNING THE VALVE LISTED ON THE TEMPORARY LIFT PAPERWORK TO ITS OUT-OF-SERVICE CLOSED POSITION WOULD NOT AFFECT THE OPERATION OF THE 2C MFP. AT 1214 ON MAY 6 WITH UNIT 2 AT 94 PERCENT POWER AN EQUIPMENT OPERATOR CLOSED THE VALVE, WHICH ISOLATED ELECTROHYDRAULIC (EH) FLUID SUPPLY TO THE 2C MFP. AT 1215 THE 2C MFP TRIPPED DUE TO LOW EH FLUID PRESSURE. STEAM GENERATOR LEVELS LOWERED RAPIDLY AND THE NSO MANUALLY TRIPPED THE REACTOR IN ANTICIPATION OF AN AUTOMATIC TRIP. OPERATOR ACTIONS TAKEN FOLLOWING THE REACTOR TRIP WERE CORRECT, AND STABLE PLANT CONDITIONS WERE ACHIEVED IN HOT STANDBY AT 1330. SEVERAL CAUSES CONTRIBUTED TO THE IMPROPER CLOSURE OF THE EH VALVE. THE NSO AND THE SCRE COMMITTED COGNITIVE PERSONNEL ERRORS BY FAILING TO RECOGNIZE THE CONSEQUENCES OF THE RETURN TO OUT-OF-SERVICE CONDITION.
455 | 4551988006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988006R00.pdf | 1988-06-02 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 2 | P | WE | PO | 94 | POWER LEVEL - 094%. AT 0640 ON JUNE 2, 1988, WITH THE REACTOR AT 94% POWER AND THE ROD CONTROL SELECTOR SWITCH IN AUTOMATIC, THE 'POWER RANGE FLUX RATE HIGH REACTOR TRIP' ANNUNCIATOR ACTUATED AND THE REACTOR TRIPPED. CONTROL ROOM OPERATORS ENTERED AND COMPLIED WITH 'REACTOR TRIP OR SAFETY INJECTION UNIT 2 EMERGENCY PROCEDURE.' THE AUXILIARY FEEDWATER PUMPS STARTED DUE TO LOW-LOW STEAM GENERATOR LEVELS THAT RESULTED FROM THE TRIP AT HIGH POWER. STABLE PLANT CONDITIONS WERE ACHIEVED IN HOT STANDBY AT 0730 ON JUNE 2, 1988. THE INTERMEDIATE CAUSE OF THE REACTOR TRIP WAS THE DROPPING OF CONTROL RODS INTO THE REACTOR CORE, WHICH RESULTED IN THE HIGH FLUX NEGATIVE RATE REACTOR TRIP. TROUBLESHOOTING EFFORTS FAILED TO DETERMINE A ROOT CAUSE OF THE DROPPED RODS. IT IS BELIEVED THAT AN INTERMITTENT COMPONENT FAILURE IN THE ROD DRIVE SYSTEM CAUSED THE EVENT, BUT THE COMPONENT DID NOT REMAIN IN THE FAILED MODE FOLLOWING THE REACTOR TRIP. TROUBLESHOOTING WAS CONDUCTED TO LOCATE COMPONENT FAILURES THAT MAY HAVE CAUSED THE ROD DROP. A NUMBER OF DEGRADED FUSES WERE IDENTIFIED IN THE ROD DRIVE POWER CABINETS AND ALL WERE REPLACED. ON JUNE 3, 1988, ALL APPROVALS REQUIRED TO START UP THE PLANT FOLLOWING A REACTOR TRIP FOR WHICH NO ROOT CAUSE HAS BEEN DETERMINED WERE OBTAINED AND THE UNIT ENTERED THE STARTUP OPERATIONAL MODE.
455 | 4551988008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988008R00.pdf | 1988-07-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Byron 2 | P | WE | PO | 95 | POWER LEVEL - 095%. THE FEEDER BREAKER FROM THE UNIT AUXILIARY TRANSFORMER TO NON-SAFETY RELATED BUS 243 HAD BEEN OPERATING AT ELEVATED TEMPERATURES, AND IT WAS DECIDED TO RACK THE BREAKER OUT FOR A VISUAL INSPECTION. AT 0110 ON JULY 14, 1988, UNIT 2 WAS AT 95 PERCENT POWER WHEN THE NUCLEAR STATION OPERATOR (NSO) CLOSED THE FEEDER BREAKER FROM THE SYSTEM AUXILIARY TRANSFORMER AND OPENED THE FEEDER BREAKER FROM THE UNIT AUXILIARY TRANSFORMER (UAT). THE NSO TURNED AWAY FROM THE CONTROL PANEL TO DISCUSS PLACING THE HOT UAT FEEDER BREAKER IN THE PULL-TO-LOCK POSITION WITH OTHER LICENSED OPEATORS. WHEN HE RETURNED TO THE CONTROL PANEL AT 0113, HE INADVERTENTLY OPERATED THE HANDSWITCH FOR THE FEEDER BREAKER FROM THE SYSTEM AUXILIARY TRANSFORMER WHICH DE-ENERGIZED BUS 243. THIS RESULTED IN THE LOSS OF SEVERAL SECONDARY SIDE PUMPS INCLUDING THE 2B AND 2C MAIN FEEDWATER PUMPS. STEAM GENERATOR LEVELS DECREASE RAPIDLY AND AT 0114 AN AUTOMATIC REACTOR TRIP OCCURRED DUE TO LOW-LOW STEAM GENERATOR LEVEL. PLANT CONDITIONS WERE STABILIZED IN HOT STANDBY AT APPROXIMATELY 0330. THE ROOT CAUSE OF THE EVENT WAS A COGNITIVE PERSONNEL ERROR BY THE NSO, WHO INADVERTENTLY OPENED THE WRONG BREAKER THAT DE-ENERGIZED BUS 243. THE HOT BREAKER WAS CAUSED BY A THERMOSTAT FAILURE IN THE BREAKER CUBICLE HEATER CONTROL CIRCUIT, WHICH CAUSED THE CUBICLE HEATER TO ENERGIZE CONTINUOUSLY.
455 | 4551988009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988009R00.pdf | 1988-07-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Byron 2 | P | WE | SU | 2 | POWER LEVEL - 002%. ON JULY 15, 1988, BYRON UNIT 2 REACTOR POWER WAS 2 PERCENT. AT 0436 A NUCLEAR STATION OPERATOR (NSO) ATTEMPTED TO OPEN THE STEAM GENERATOR PREHEATER BYPASS VALVES (2FW039A,B,C,D) TO FEED THE STEAM GENERATORS (S/G'S). THE A AND D VALVES OPENED PROPERLY, BUT THE B AND C VALVES FAILED TO OPEN AS DEMANDED. THE LEVELS IN THE 2B AND 2C S/G'S LOWERED TO THE LOW-LOW LEVEL REACTOR TRIP SETPOINT AT WHICH POINT THE REACTOR AUTOMATICALLY TRIPPED. THE LICENSED OPERATORS ENTERED AND COMPLIED WITH EMERGENCY OPERATING PROCEDURES. STABLE PLANT CONDITIONS WERE ACHIEVED IN HOTSTANDBY AT 0500. THE EVENT WAS CAUSED BY THE FAILURES OF VALVES 2FW039B AND 2FW039C TO OPEN ON DEMAND. THESE VALVES NEED TO BE OPEN TO PROVIDE SUFFICIENT FEEDWATER FLOW TO THE S/G'S AT 1 TO 2 PERCENT REACTOR POWER. THE LEVEL INSTABILITIES INDUCED BY THE VALVE FAILURES MADE LEVEL CONTROL DIFFICULT. INVESTIGATION REVEALED THAT THE VALVES HAD BECOME THERMALLY BOUND FOLLOWING THEIR AUTOMATIC CLOSURE DURING A REACTOR TRIP EVENT ON JULY 14, 1988. BOTH VALVES WERE OPENED USING HYDRAULIC LIFTS AND 2FW039C OPERATED PROPERLY, HOWEVER, 2FW039B STILL WOULD NOT OPEN WHEN DEMANDED BY THE HANDSWITCH. A NON-SAFETY RELATED AIR CHECK VALVE WAS REPLACED AND THE 2FW039B VALVE OPERATED PROPERLY. A PREVIOUS SIMILAR OCCURRENCE WAS REPORTED IN UNIT 2 LICENSEE EVENT REPORT 88-007.
455 | 4551988012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551988012R00.pdf | 1988-12-15 | QR8 | Spurious Reactor Trip | [45 empty] | Byron 2 | P | WE | PO | 40 | POWER LEVEL - 040%. AT 0849 ON 12/15/88 PERSONNEL ENTERED THE UNIT 2 CONTAINMENT BUILDING TO INSPECT FOR ACTIVE BORIC ACID LEAKAGE AS A PRE-REFUELING OUTAGE FUNCTION. THE UNIT WAS AT 40% POWER. THE INSPECTION TEAM OBSERVED BORIC ACID CRYSTALS AND A MINOR PACKING LEAK ON AN INSTRUMENT VALVE LABELED '2FT-434 VENT'. WHILE REMOVING THE ENCRUSTED BORIC ACID AND TIGHTENING THE PACKING NUT ABOUT ONE FLAT AT 1002, AN AUTOMATIC REACTOR TRIP OCCURRED DUE TO INDICATED LOW REACTOR COOLANT LOOP C FLOW. THE INSPECTION TEAM WAS UNAWARE OF THE REACTOR TRIP AND THE CONTROL ROOM OPERATORS COULD NOT CORRELATE ANY SPECIFIC INSPECTION TEAM ACTIVITIES WITH THE TRIP. AN AUTOMATIC FEEDWATER ISOLATION AND AUTOMATIC AUXILIARY FEEDWATER PUMP STARTS OCCURRED AS EXPECTED FOLLOWING THE TRIP. THE PLANT WAS STABILIZED IN HOT STANDBY AT APPROXIMATELY 1030. THE LOW REACTOR COOLANT FLOW SIGNALS WERE CAUSED BY A PRESSURE TRANSIENT IN THE HIGH PRESSURE SENSING LINE, WHICH IS COMMON TO ALL THREE FLOW TRANSMITTERS IN THE REACTOR COOLANT ELBOW FLOW METER DESIGN. BY REMOVING ENCRUSTED BORIC ACID FROM THE VENT VALVE AND TIGHTENING ITS PACKING, A MECHANIC INDUCED SUFFICIENT VIBRATION IN THE HIGH PRESSURE SENSING LINE TO CAUSE A PRESSURE DECREASE AT THE CONNECTIONS TO ALL THREE FLOW TRANSMITTERS. THE LOW FLOW INDICATION PERSISTED FOR APPROXIMATELY 200 MILLISECONDS.
455 | 4551990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551990001R00.pdf | 1990-01-18 | QR8 | Spurious Reactor Trip | [45 empty] | Byron 2 | P | WE | PO | 99 | On January 18, 1990, Unit 2 was operating at 99% power. An Instrument Maintenance Technician was performing a functional surveillance on steam pressure channel 526 when channel 525 spiked low. A reactor trip and safety injection followed. <br /><br /> The most probable cause of the event was the failure of the 525 pressure transmitter. The transmitter was replaced, and the spiking has not recurred. This is the first time the coincidence was satisfied during a pressure transmitter failure and resulted in a reactor trip.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) for any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System.
455 | 4551990010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551990010R00.pdf | 1990-12-20 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Byron 2 | P | WE | PO | 72 | On December 20, 1990 at 0400, a severe steam leak was reported in the Unit 2 Main Steam Tunnel. After verifying the size of the leak, the Reactor was manually tripped. By eliminating Steam Generator Blowdown and Feedwater as causes, it was determined that the leak was on the main steam side. The Main Steam Isolation Valves were then closed which isolated the leak. The Main Steam Dumps were opened to depressurize the Main Steam Header. <br /><br /> Upon entry into the Main Steam tunnel, the 2C Main Steam Sample probe was found lying on the floor. The weld for the probe had been improperly repaired during the previous refueling outage causing the probe and its isolation valve to be ejected leaving a one inch hole in the Main Steam line. Since this probe was needed only for initial start-up testing, the nozzle was capped. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) any event that results in a manual or automatic actuation of the Engineered Safety Features including Reactor Protection System.
455 | 4551991005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551991005R00.pdf | 1991-11-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 10 | At 0357, on 11/07/91, after Unit 2 startup and during preparation for the turbine roll, a Low-2 Steam Generator (S/G) level on the 2A S/G was received which initiated a Reactor Trip. All safeguard actuation features functioned as designed.<br /><br /> The Low-2 level in the Steam Generator was the result of difficulty in controlling the Westinghouse D-5 S/G level at low power and due to leak by of the main Feedwater Regulating Valve for the 2A Steam Generator. The level instrument taps in the Steam Generator are being moved during the next refueling outage to reduce this level instability. The Main Feedwater Regulatory valve was adjusted before the next startup. A revision will be made to the startup procedure to verify position of this valve for each Steam Generator. <br /><br /> This event is reportable in accordance with 10CFR50.73 (a)(2)(iv), any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature.
455 | 4551992003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551992003R01.pdf | 1992-06-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 100 | On 06/10/92, at 1315, a Feedwater (FW) JB! alarm (Steam Generator (S/G) 2C Level Deviation-Low) was received on the "C" loop steam generator. Initial attempts to stabilize steam generator level were successful, however, the 2FW530 ("C" loop Steam Generator Feedwater Regulating Valve) subsequently failed closed, and a manual reactor trip was initiated at 1325. All rods inserted and all systems functioned normally. In addition to the reactor trip, the Auxiliary Feedwater pumps Auto-started on Low-2 Steam generator level. Steam generator level was recovered to normal via the Auxiliary Feedwater system. <br /><br /> The cause of the this event was the failure of the valve operator diaphragm. This led to instantaneous loss of air pressure and immediate closure of the 2FW530 valve. <br /><br /> All Unit two feedwater regulating valve diaphragms were replaced based upon an external inspection of the diaphragm. Additionally the diaphragm casing torque value was increased per vendor recommendations.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System.
455 | 4551993003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551993003R00.pdf | 1993-05-11 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Byron 2 | P | WE | PO | 97 | At 22:38 on May 11, 1993, a Turbine Emergency Trip Oil Header Pressure Low Alert was received on Byron Unit 2, followed immediately by a Reactor Trip initiated by Turbine trip above P-8 (30% power). The Reactor Trip was initiated by a loss of Electro-Hydraulic fluid pressure in the Emergency Trip header. <br /><br /> The cause of the loss of pressure in the Emergency Trip header was a spurious actuation of the Overspeed Trip Relay due to a spiking power supply. <br /><br /> The immediate corrective action was to replace the faulty power supply board.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature including the Reactor Protection System.
455 | 4551993008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551993008R01.pdf | 1993-11-23 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Byron 2 | P | WE | PO | 100 | On November 23, 1993, at 0040, with Unit 2 at 100% power and Normal Operating Pressure and Temperature, the Instrument Maintenance Department (IMD) was performing surveillance 2BIS 3.1.1-024 which tested loop LB559C, 2D Steam Generator (SG) level (FW) [JB]. The loop was put in test as required and the appropriate alarms came up. Anticipated Transient Without Scram Mitigation System (AMS) was also put in test per the surveillance and the associated alarms came in. Six minutes into the loop functional check, the 2A Auxiliary Feedwater (AF) [BA] pump auto started and all steam generator blowdown isolation valves closed concurrently. Approximately 3.5 minutes later a reactor trip occurred with reactor trip breaker A opening. All related plant parameters were normal prior to the event. All operations and Instrument Maintenance personnel actions were appropriate prior, during and after the event. <br /><br /> The cause was suspected to be a failure of one of the circuit cards for train 'A' of Solid State Protection System (SSPS) (EF) [JE] SG level. The associated cards were replaced and the removed cards were tested 'on the bench'. One universal logic card showed signs of degrading voltage with time. <br /><br /> Operability tests and functional tests were performed to verify operability of the replaced circuit cards. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature including the Reactor Protection System.
455 | 4551994002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551994002R00.pdf | 1994-09-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 2 | P | WE | PO | 100 | To repair an intermittent indication-only Urgent Failure on the Unit Two Rod Control System (RD)[AA], Instrument Mechanics replaced a Moving Firing Card in the 2BD Power Cabinet. While performing a surveillance for post maintenance operability, a Stationary Regulation Urgent Failure developed that caused a mismatch of control rods. <br /><br /> Subsequent troubleshooting indicated possible problems with a Stationary Firing Card or a Stationary Regulation Card. During the testing of the effectiveness of the repairs, control rod C07 fell into the core which initiated a negative flux rate reactor trip. <br /><br /> The Urgent Failure was caused by a bad Stationary Firing Card. The dropped control rod was caused by a failed rack connector socket carrying the full current order to the Stationary Regulation Card.
455 | 4541996007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4541996007R00.pdf | 1996-05-23 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Byron 2 | P | WE | PO | 100 | On 5/23/96, Unit 1 experienced a Loss of Offsite Power (LOOP) for more that fifteen minutes. As a result of the LOOP, the Station Air Compressors and non-essential service water pumps were lost. This lead to a decision to manually trip Unit 2. <br /><br /> The LOOP resulted from a fault on Station Auxiliary Transformer (SAT) 142-2. The fault was caused by a failed insulator on the B phase on the non-segregated bus duct. The insulator failed due to water intrusion into the bus duct. Water leaked into the bus duct because of caulk that was leaking and a poor seal between the retaining bolts for the insulator and the bus duct.<br /><br /> The bus duct was repaired, the other bus ducts were inspected, and changes to the preventative maintenance of the non-segregated bus ducts are planned.<br /><br /> After Unit 2 was manually tripped, Source Range Detector, N31, failed to energize. The cause was a failed detector. The detector was replaced. <br /><br /> There was a previous event of water intrusion into the non-segregated bus ducts at Byron Station prior to 1984 (before fuel load). <br /><br /> These events are reportable in accordance with 10CFR50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS).
455 | 4551997003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4551997003R00.pdf | 1997-10-10 | QR3 | Reactivity Control Imbalance | [45 empty] | Byron 2 | P | WE | PO | 99 | A Unit 2 reactor trip occurred at 1112 on 10/10/97 following the failure of redundant Rod Drive Power cabinet power supplies. One or more rods fell into the core, causing a trip on high negative flux rate.The day before, a local Power Supply Failure alarm was noted. Troubleshooting on the day of the trip found voltage on both supplies dropping. As an attempt was being made to install a temporary supply, the conditions finally reached the point where one or more gripper coils released their respective rods.Testing of all Rod Drive power supplies found 4 more failures between both units. The average age of all failed supplies was 76 months. A search of Operating Experience only found one occurrence relating to age concerns of Lambda power supplies. This was a 1995 report stating a 5 year life for Lambda power supplies. Pending confirmation from offsite testing, the failure of the power supplies is age-related.A contributor was the failure of the alarm to annunciate the first power supply failure. This vulnerability was pointed out in a 1987 vendor bulletin. Due to the low failure rate in 1987, the station chose to inspect the power supplies instead of modifying the alarm circuit.Corrective actions will be to periodically replace the power supplies and evaluate changes to the alarm circuit. This event is reportable per 10CFR50.73(a)(2)(iv).(p:\regassur\pifler\ler\wp9565r.wpf\102997)
455 | 4552000001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552000001R00.pdf | 2000-01-13 | QR5 | Turbine Trip | [45 empty] | Byron 2 | P | WE | PO | 100 | At 0059 hours on January 13, 2000, Byron Station Unit 2 received an offsite transmission line 0622 trip alarm due to a phase B fault. A static line from another offsite line fell onto phase B of line 0622 causing the fault and direct transfer trip. As designed, the direct transfer trip opened oil circuit breakers (OCBs) 11-12 and 12-13 to isolate the line fault in the Byron Station switchyard. Unit 2 next received an unexpected main generator load rejection trip signal. The load rejection circuit provided a signal to actuate a main generator lockout relay, which opened air circuit breaker (ACB) 10-11 and tripped the Unit 2 turbine and reactor. The turbine and reactor trip occurred as designed and the unit was safely shut down.ACB 10-11 was closed at the time of the load rejection alarm which indicated one of the ACB 10-11 auxiliary contacts must have been closed at that time to complete the required load rejection trip logic. It was verified during subsequent troubleshooting that the ACB 10-11 phase A load rejection 'b' contact was found closed when the breaker was closed. The 'b' contact should have been open. The root cause of the switch failure is unknown.The immediate corrective action was to replace the defective contacts and verify proper operation. Also, a preventive maintenance activity will be developed to test these switches for both Byron Station Units. There were no actual safety consequences impacting plant or public safety. At 0155 hours on January 13, 2000, a NRC Emergency Notification System telephone call was initiated in accordance with 10 CFR 50.72.
455 | 4552000002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552000002R00.pdf | 2000-07-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 100 | On July 26, 2000, at 1833 hours, Byron Station, Unit 2 experienced a reactor trip due to Steam Generator 2C low level. The low level was caused by a Protection and Control Instrumentation Rack NTD circuit card failure in the Main Feedwater (FW) Regulating Valve (FRV) circuitry and inappropriate licensed operators' response to the card failure causing the FRV to close. Following the reactor trip, the circuit card was replaced and the unit returned to power operations. A Company wide task force has been formed to evaluate control circuit card issues in an effort to reduce failures. The inappropriate operator actions include not using alternate indications to validate their diagnosis, switching the FW control from automatic to manual, switching back to manual after returning to automatic control, and the delay in identifying the need to initiate a manual reactor trip which resulted in the automatic reactor trip. Procedural and training improvements will be made to help the operator better diagnose and respond to control circuit failures. Operations Management will reinforce the expectation to validate information and to manually trip the reactor prior to exceeding an automatic trip setpoint. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv).
455 | 4552001002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552001002R00.pdf | 2001-06-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 100 | At 0609 hours on June 26, 2001, the Unit 2 licensed Nuclear Station Operator (NSO) observed the Unit 2 “D" Steam Generator (SG) level begin to decrease. He attempted to further open the Unit 2 Main Feedwater (FW) Regulating Valve (i.e., 2FW540) for the 2D SG. The valve did not respond and the 2D SG level continued to decrease and approached the low level reactor trip setpoint. In anticipation of the automatic trip signal, the NSO initiated a manual reactor trip signal at 0609 hours, prior to reaching the low level setpoint on 2D SG. The reactor trip system responded as expected and shutdown the reactor. The Auxiliary Feedwater (AF) System started as expected to supply auxiliary feedwater to the SGs. During the post reactor trip recovery, an unexpected reactor trip and AF actuation signal was generated when the B SG level was allowed to drop below the actuation setpoint. The 2B AF pump had just been secured and consequently, restarted. The cause of the 2FW540 valve closing was due to a retaining clip in the valve's positioner (i.e., Bailey AV1) not being installed correctly. The cause of the second unexpected actuation signal was due to failure of the licensed Unit Supervisor (US) to verbalize a procedure step concerning SG levels. Corrective actions include revising work instructions to ensure the retaining clip in Bailey AV1 positioners are installed correctly and counseling the US. There were no safety consequences impacting plant or public safety. This event is reportable in accordance with 10 CFR 50.73 (a) (2)(iv).
455 | 4552005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552005001R00.pdf | 2005-10-19 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Byron 2 | P | WE | PO | 100 | On October 19 2005, attempts to execute an automatic Turbine Runback in response to a trip of a Condensate/Condensate Booster (CD/CB) Pump were ineffective and ultimately resulted in an automatic Reactor Trip on low Steam Generator Level. The root cause was determined to be the failure of the Digital Electro-Hydraulic system to automatically runback the turbine as designed. This was due to an application software fault. The software fault effectively rendered all automated Turbine Runbacks inoperable. Corrective actions include the development of procedural controls to monitor and identify software issues of this nature. There were no safety consequences impacting plant or public safety as a result of this event. The automatic turbine runback feature is a non safety related design feature and is not credited in any Updated Final Safety Analysis Report chapter 15 accident and transient analyses. The actuation of the reactor protection system was reported to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A).
455 | 4542012001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4542012001R01.pdf | 2012-01-30 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Byron 2 | P | WE | PO | 100 | Two events involving the loss of normal offsite power occurred on January 30, 2012 for Unit 2 and February 28, 2012 for Unit 1. The January 30, 2012, event was initiated by a mechanical failure of a 345 kilovolt (kV) Ohio Brass inverted porcelain insulator on the System Auxiliary Transformer (SAT) 242-1/2 A-Frame structure in the Switchyard resulting in an open phase non-faulted condition on phase C. The 4.16 kV Engineered Safety Feature (ESF) buses undervoltage protection scheme did not automatically switch over to the emergency Diesel Generators (DG). However, the 6.9 kV buses powering the Reactor Coolant Pumps did recognize the undervoltage condition and as designed generated a reactor trip signal. The 4.16 kV ESF buses remained energized with a voltage unbalance. Loads energized by SAT 242-1/2 tripped off due to a phase A overcurrent condition. Operators diagnosed the situation and manually isolated SAT 242-1/2 from the 4.16 kV ESF buses. The 2A and 2B Diesel Generators (DG) started and energized the 4.16 kV ESF buses. Loads sequenced onto the buses as designed. The February 28, 2012 event was also initiated by a failed inverted porcelain insulator. In this event, the 4.16 kV ESF buses did sense fault condition and separated SAT 242-1/2 from the 4.16 kV buses. The 1A and 1B DGs started and energized the 4.16 kV ESF buses. The insulator failures were caused by service propagation of a large manufacturing material defect. The defect was characterized as poorly vitrified porcelain, which contained a high density of porosity and micro-cracks. All Ohio Brass inverted insulators associated with both Unit's SATs and Main Power transformers have been replaced with insulators from a different manufacturer.
455 | 4552012001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552012001R01.pdf | 2012-02-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Byron 2 | P | WE | PO | 25 | At approximately 1700 hours, on February 6, 2012, the Unit 2 Operating crew was in the process of conducting a unit startup in accordance with startup procedures. The reactor was at approximately 25% power. During the step that switched Feedwater (FW) flow from the upper nozzle of the 2C Steam Generator (SG) to its lower nozzle via the 2C FW Isolation Valve (FWIV), the Reactor Operator controlling the SG levelsmanually was also focused on maintaining subcooling in the tempering line and satisfying water hammer interlocks. Consequently, the RO was not closely monitoring the 2C SG level increase. Another assisting RO recognized the level increase was approaching the high level setpoint and informed the RO. Subsequently, the RO reduced FW flow; however, the level continued to increase and approach the high level setpoint of 80.8% (i.e., P-14), which causes an automatic turbine trip and FW isolation. In anticipation of reaching this setpoint, the Unit 2 Senior RO directed a manual reactor trip at 1719 hours. Almost simultaneous to the manual reactor trip the 2C SG level reached the P-14 setpoint. The reactor trip signal and P-14 both generate an automatic turbine trip and FW isolation. The turbine tripped and FW isolated, as designed. In accordance with reactor trip response procedures, the 2A and 2B Auxiliary Feedwater pumps were started. The cause of the event was determined to be an overly complex startup procedure and weak Operating crew performance. The startup procedure will be revised and personnel performance issues were remediated.
455 | 4552013001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552013001R00.pdf | 2013-03-20 | QR6 | Manual Reactor Trip | [45 empty] | Byron 2 | P | WE | PO | 100 | At 19:51 hours on March 20, 2013, Byron Unit 2 was manually tripped due to a loss of all Generator Stator Cooling Water (GC) when the 2A Generator Stator Cooling Water pump (2A GC) tripped and the redundant (2B GC) pump was unavailable due to a previous pump failure on February 17, 2013. The 2BEP -0, "Reactor Trip or Safety Injection Unit 2" procedure was entered and a transition was made to 2BEP ES 0.1, "Reactor Trip Response Unit 2." The root cause was the failure of the inboard motor bearing on the 2A GC pump motor due to insufficient lubrication as supplied by the vendor. This failure resulted in contact between the rotor and stator windings causing the electrical failure of the motor. Corrective actions include replacement of the failed motor and inspection of the remaining GC pump motors. All other plant systems operated as designed in response to the shutdown and, there were no safety consequences impacting plant or public safety as a result of this event. The Generator Cooling System is a non-safety related design feature and is not credited in any Updated Final Safety Analysis Report chapter 15 accident and transient analyses. The actuation of the reactor protection system was reported to the NRC in accordance with 10CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A).
455 | 4552016001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4552016001R01.pdf | 2016-10-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Byron 2 | P | WE | PO | 90 | On October 12, 2016 at 1338 hours, Byron Station Operations initiated a manual reactor trip of Unit 2 due to decreasing water levels in the loop B and loop C Steam Generators. A trip of a bus feed breaker resulted in the loss of power feed to multiple normally energized relays associated with the Feedwater (FW) Water Hammer Prevention System (WHPS) circuit, which resulted in automatic closure of related Feedwater Isolation Valves.<br /><br /> The apparent cause of the feed breaker trip was due to a manufacturing defect on the feed breaker amptector circuit board. <br /><br /> The corrective actions planned include revising refurbishment testing requirements for the main feed breaker and performing modifications in subsequent refuel outages to the FW Water Hammer Prevention System to address power supply single point vulnerability. <br /><br /> The Unit 2 Reactor Protection System was actuated by the manual reactor trip and the Auxiliary Feedwater system actuated automatically as expected. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
456 | 4561987032 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987032R00.pdf | 1987-07-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 1 | P | WE | SU | 1 | POWER LEVEL - 001%. ON JUNE 29, 1987 AT 0710 HOURS A ROD CONTROL URGENT FAILURE ALARM WAS RECEIVED IN THE CONTROL ROOM. TECHNICAL STAFF FOUND A PHASE FAILURE IN THE ROD CONTROL SYSTEM POWER CABINET 1AC. A MOVABLE GRIPPER COIL FUSE WAS REPLACED AND RODS WERE MOVED AFTER THE ALARM WAS RESET. AT 1352 HOURS ANOTHER URGENT FAILURE ALARM WAS RECEIVED. THE SAME FAILURE WAS INDICATED. TECH SPEC ACTION REQUIREMENT 3/4.1.3 WAS ENTERED. ALL FUSES WERE CHECKED AND WERE FOUND TO BE GOOD. THE FIRING CARD AND PHASE FAILURE CARD WERE REPLACED. RODS AGAIN MOVED AFTER THE ALARM WAS RESET. RODS WERE RESTORED TO AN OPERABLE STATUS AFTER BEING TESTED. ON JUNE 30, 1987 WHILE TAKING TRACES ON THE 1AC POWER CABINET, THE PHASE FAILURE ROD CONTROL URGENT ALARM ANNUNCIATED. ROD CONTROL WAS DECLARED INOPERABLE AT 1850 AND THE REACTOR WAS TRIPPED ON JULY 1, 1987 AT 0022 HOURS IN ACCORDANCE WITH TECH SPEC 3/4.1.3.1. THE CAUSES OF THE EVENT WERE LOOSE CONNECTIONS AND BAD FUSES IN THE 1AC MOVABLE DISCONNECT SWITCH CABINET LOCATED ABOVE THE 1AC POWER CABINET. THE 30 AMPERE FUSES WERE REPLACED AND ALL LOOSE CONNECTIONS TIGHTENED. ALL OTHER POWER CABINET DISCONNECT SWITCH CABINETS WERE INSPECTED AND LOOSE CONNECTIONS TIGHTENED. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF THIS PROBLEM.
456 | 4561987035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987035R00.pdf | 1987-07-05 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 1 | P | WE | SU | 1 | POWER LEVEL - 001%. WHILE TROUBLESHOOTING SPURIOUS TRIPS OF THE 1B ROD CONTROL SYSTEM MOTOR GENERATOR (M/G) SET, REACTOR TRIP OCCURRED DUE TO MISCOMMUNICATION ERROR. A TECHNICAL STAFF ENGINEER REQUESTED AN OPERATOR (A-MAN) BE SENT TO CLOSE THE OUTPUT BREAKER OF THE M/G SET. CONTROL ROOM PERSONNEL INSTRUCTED THE A-MAN TO ASSIST THE OAD ENGINEER. UPON ARRIVAL AN OPERATIONAL ANALYSIS DEPARTMENT (OAD) ENGINEER INSTRUCTED THE A-MAN TO CLOSE THE BREAKER. THE A-MAN NOTICED NUMEROUS PIECES OF TESTING EQUIPMENT, AND NOT KNOWING WHAT BYPASSES HAD BEEN DISABLED, CLOSED THE BREAKER, WITHOUT USING PROCEDURE BWOP RD-5, CONTROL ROD DRIVE M/G SET STARTUP AND PARALLELING TO OPERATING M/G SET. THIS CAUSED BOTH 1A AND 1B M/G SET BREAKERS TO OPEN, DROPPING CONTROL RODS INTO THE CORE. CAUSE OF THIS EVENT WAS MISCOMMUNICATION BETWEEN THE PERSONNEL INVOLVED. IT WAS NOT SPECIFIED THAT PROCEDURE BWOP RD-5 SHOULD BE USED. CORRECTIVE ACTIONS WERE TO REPLACE 2 RESISTORS, A VARISTOR, AND A DIODE. OPERATING WILL ENSURE THAT PROCEDURE BWOP RD-5 IS IN HAND WHEN PERFORMING PARALLELING OPERATION OF M/G SETS; THIS EVENT WILL BE REVIEWED BY OPERATING, OAD, AND TECHNICAL STAFF PERSONNEL, AND THIS EVENT WILL BE INCLUDED IN AN UPCOMING ISSUE OF TOPICS FOR SUCCESS, AN INFORMATION DISSEMINATING PROGRAM.
456 | 4561987050 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987050R00.pdf | 1987-09-23 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 38 | POWER LEVEL - 038%. AT 2153 ON SEPTEMBER 23, 1987, MAINTENANCE PERSONNEL WERE REINSTALLING THE HANDLE ON TRANSFORMER 141-1 DELUGE ALARM TEST VALVE 1FP5098F WHEN THEY UNINTENTIONALLY TURNED THE VALVE STEM APPROXIMATELY FIVE DEGREES. THIS ACTUATED THE DELUGE SYSTEM ON THE UNIT AUXILIARY TRANSFORMER (UAT) AND CAUSED THE EIGHTY-SIX LOCKOUT RELAY TO ACTUATE CAUSING BOTH UATS TO BE ELECTRICALLY ISOLATED FROM THE 345 KV SWITCHYARD AND THE 6.9 AND 4 KV BUSES FROM THE UNIT; THIS LED TO A TURBINE TRIP FOLLOWED BY A REACTOR TRIP. THE 1FP5098F VALVE IS A BALL VALVE WITH NINETY DEGREES FROM FULLY CLOSED TO FULLY OPEN. THE HANDLE WAS BEING DRILLED TO ALLOW INSTALLATION OF TAMPER SEALS DUE TO THE PREVIOUS OCCURRENCE DISCUSSED BELOW. CAUSE OF THE UAT TRIP WAS MAINTENANCE PERSONNEL INADVERTENTLY TURNING THE STEM OF THE VALVE APPROXIMATELY FIVE DEGREES. CONTRIBUTING TO THIS WAS THE DECISION TO NOT REMOVE THE DELUGE SYSTEMS FROM SERVICE PRIOR TO ALLOWING THE WORK TO BE PERFORMED. STABLE PLANT CONDITIONS WERE ESTABLISHED AT 2206. THIS EVENT HAS BEEN REVIEWED WITH APPROPRIATE PERSONNEL STRESSING THE IMPORTANCE OF PERFORMING THIS TYPE OF ACTIVITY WITH THE SYSTEMS REMOVED FROM SERVICE. PREVIOUS OCCURRENCE INVOLVING A DELUGE SYSTEM ACTUATION AND TRANSFORMER TRIP, AND ALL THE CORRECTIVE ACTIONS ASSOCIATED WITH IT HAVE NOT BEEN COMPLETED.
456 | 4561987052 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987052R00.pdf | 1987-09-24 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 13 | POWER LEVEL - 013%. AT 2210 ON SEPTEMBER 24, 1987, BWGP 100-3, POWER ASCENSION 5% TO 100%, WAS IN PROGRESS. THE MAIN TRANSFORMER OVEREXCITATION RELAY ACTUATED DURING THE PROGRESS OF SYNCHRONIZING THE MAIN GENERATOR TO THE SYSTEM GRID. THIS ACTIVATED THE EIGHTY-SIX LOCKOUT RELAY WHICH CAUSED THE MAIN GENERATOR, MAIN POWER TRANSFORMER AND UNIT AUXILIARY TRANSFORMER TO BE ELECTRICALLY ISOLATED FROM THE GRID. THE ROOT CAUSE OF THE EVENT IS UNKNOWN. INVESTIGATIONS HAVE REVEALED A LOOSE CONNECTION ON A MOVABLE CONTACT BLOCK LOCATED ON C PHASE OF THE 25 KV REGULATING POTENTIAL TRANSFORMER. THIS DID CONTRIBUTE TO THE EVENT. HOWEVER, IT WAS NOT THE ROOT CAUSE. OPERATOR ERROR IS RULED OUT AS THE PROCEDURE WAS FOLLOWED AND THIS EVOLUTION DOES NOT REQUIRE ANY SPECIAL TRAINING OR PRACTICE. DURING THE SUBSEQUENT PLANT STARTUP AND POWER ASCENSION, THE A AND C PHASE POTENTIAL TRANSFORMERS WERE MONITORED. INCLUDED IN THIS COMPREHENSIVE MONITORING PROGRAM WERE THE OVEREXCITATION RELAY, WHICH ACTIVATED DURING THIS EVENT, AND THE VOLTAGE REGULATOR. THIS TESTING REVEALED THAT ALL READINGS WERE NORMAL. SHOULD ANY ADDITIONAL INFORMATION CONCERNING THE CAUSE OF THIS EVENT BECOME AVAILABLE, THIS REPORT WILL BE SUPPLEMENTED.
456 | 4561987057 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987057R01.pdf | 1987-10-09 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 49 | POWER LEVEL - 049%. AT 1700 ON 10/9/87, 1BWOS 3.4.2.A-1, TURBINE THROTTLE, GOVERNOR, REHEAT AND INTERCEPT VALVE MONTHLY SURVEILLANCE WAS IN PROGRESS. DIGITAL ELECTRO HYDRAULIC CONTROL SYSTEM (DEH) WAS IN AUTOMATIC. MEGAWATT (MW) FEEDBACK LOOP WAS OUT, PER PROCEDURE, AND THE TURBINE THROTTLE VALVES WERE IN TEST. AT APPROXIMATELY 1725, AS THROTTLE VALVE #2 WAS BEING CYCLED, MW OUTPUT BECAME ERRATIC. GOVERNOR VALVES WENT TO THEIR FULLY CLOSED POSITION. ATTEMPTS WERE MADE TO MANUALLY OPEN THE GOVERNOR VALVES, BUT WERE UNSUCCESSFUL. A TURBINE TRIP ON ANTI-MOTORING RESULTED IN A REACTOR TRIP AT 1726. ROOT CAUSE IS INDETERMINATE. IMMEDIATE ACTION WAS TO ESTABLISH STABLE PLANT CONDITIONS. TEMPORARY INSTRUMENTATION VERIFIED THAT THE SENSING LINE ARRANGEMENT DID NOT CAUSE THE TRIP. ALSO, SIMULATOR TESTING DONE BY WESTINGHOUSE AUTOMATION DIVISION REVEALED THAT NO SOFTWARE PROBLEMS EXIST WITH THE DEH CONTROL SYSTEM. PROPOSED ACTIONS BY WESTINGHOUSE INCLUDE; REDUCE IMPULSE PRESSURE FEEDBACK LOOP SENSITIVITY, INCREASE IMPULSE FEEDBACK LOOP RESPONSE TIME, REDUCE DEADBAND OF IMPULSE PRESSURE FEEDBACK LOOP, AND INSTALL DIAGNOSTIC TAPES TO THE DEH SYSTEM TO ANALYZE ANY HARDWARE PROBLEMS. NO PREVIOUS OCCURRENCES.
456 | 4561987060 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561987060R00.pdf | 1987-12-06 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Braidwood 1 | P | WE | PO | 89 | POWER LEVEL - 089%. AT 1953 ON DECEMBER 6, 1987, UNIT 1 WAS MANUALLY TRIPPED IN RESPONSE TO RAPIDLY DECREASING STEAM GENERATOR LEVELS. CONDENSATE PUMP SUCTION STRAINER DIFFERENTIAL PRESSURE HIGH AND FEEDWATER PUMP NET POSITIVE SUCTION HEAD LOW ALARMS WERE RECEIVED IMMEDIATELY PRIOR TO THE TRIP. ADDITIONALLY, STATION PERSONNEL REPORTED CONDENSATE SYSTEM PIPING SHAKING. THE ROOT CAUSE OF THE EVENT IS ATTRIBUTED TO BLOCKAGE OF THE CONDENSATE/CONDENSATE BOOSTER PUMP SUCTION STRAINERS. CORRECTIVE ACTION INCLUDED A WALKDOWN OF THE CONDENSATE SYSTEM TO LOOK FOR PIPING/HANGER DAMAGE. PRIOR TO REACTOR STARTUP, ALL FOUR CONDENSATE PUMP SUCTION STRAINERS WERE MANUALLY CLEANED, AND ALL FOUR CONDENSATE BOOSTER PUMP STRAINERS WERE BACKWASHED. THE CONDENSER HOT WELL WILL BE CLEANED AND INSPECTED DURING THE NEXT OUTAGE. THERE HAVE BEEN NO PREVIOUS OCCURRENCES.
456 | 4561988016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561988016R00.pdf | 1988-08-11 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON AUGUST 11, 1988, THE ROD CONTROL URGENT ALARM ANNUNCIATED THREE TIMES. ALSO, THE C-11 ROD STOP ALARM WAS ANNUNCIATING PRIOR TO 223 STEPS ON BANK D CONTROL RODS. PREPARATIONS WERE MADE TO CHECK THE POWER CABINET 1BD FUSES. SEPARATE DISCUSSIONS WERE HELD TO DISCUSS THE DETAILS OF CHECKING THE FUSES. THE UNIT OPERATOR WAS INSTRUCTED TO PLACE ROD CONTROL IN MANUAL AND TO PERFORM NO ROD MOVEMENT DURING THE TIME THE POWER DISCONNECT SWITCH WAS OPEN. THE UNIT OPERATOR WAS OCCUPIED WITH NORMAL DUTIES AND OBSERVED THAT THE C-11 ROD STOP ALARM HAD ANNUNCIATED AGAIN AND ATTEMPTED TO CLEAR IT BY MANUALLY MOVING RODS. WHEN ROD MOTION WAS DEMANDED, THE STATIONARY GRIPPER COILS DEENERGIZED AND CONTROL BANK D GROUP 1, RODS DROPPED. THIS CAUSED AN AUTOMATIC REACTOR TRIP ON HIGH FLUX NEGATIVE RATE. CONTRIBUTING TO THIS EVENT WAS A LACK OF ADMINISTRATIVE CONTROLS TO INDICATE AN OFF-NORMAL SYSTEM STATUS. THE CAUSE OF THE ROD URGENT ALARMS IS ATTRIBUTED TO TWO BAD FUSES IN CABINET 1BD WHICH WERE REPLACED. THIS EVENT HAS BEEN REVIEWED WITH THE INDIVIDUALS INVOLVED. ADDITIONAL ADMINISTRATIVE CONTROLS WILL BE DEVELOPED TO AID THE OPERATOR IN IDENTIFYING OFF-NORMAL EQUIPMENT STATUS. THIS REPORT WILL BE INCLUDED IN THE LICENSED OPERATOR REQUIRED READING PROGRAM. THERE HAVE BEEN NO PREVIOUS OCCURRENCES.
456 | 4561988022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561988022R00.pdf | 1988-10-16 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Braidwood 1 | P | WE | PO | 96 | POWER LEVEL - 096%. AT 2021 ON OCTOBER 16, 1988, A POTENTIAL TRANSFORMER FAILURE ON AN OFF SITE 138 KV LINE CAUSED A LINE TRIP FOLLOWED BY A POLE DISAGREEMENT ON A 345 KV YARD BREAKER IN THE BRAIDWOOD SWITCHYARD AND RESULTED IN A LOSS OF OFF SITE AC POWER FEED CAPABILITY TO UNIT ONE. A BLOCKED RELAY CONTACT ASSOCIATED WITH THE 1C REACTOR COOLANT PUMP (RCP) ALLOWED IT TO TRIP ON INSTANTANEOUS OVERCURRENT DURING THE BUS TRANSFER. ABOVE 30% POWER AND WAS FOLLOWED BY A TURBINE/GENERATOR TRIP AS DESIGNED. OFF SITE AC POWER WAS RESTORED AND NORMAL HOT STANDBY CONDITIONS WERE ESTABLISHED. THE 345 KV YARD BREAKER WAS RETIMED TO WITHIN ACCEPTABLE TOLERANCE. THE POTENTIAL TRANSFORMER ON THE OFF SITE 138 KV LINE HAS BEEN REPLACED AND THE LINE RETURNED TO SERVICE. THE RELAY BLOCK ASSOCIATED WITH THE 1C RCP HAS BEEN REMOVED. UNIT ONE 6.9 KV AND 4 KV BUSSES HAVE BEEN VISUALLY INSPECTED FOR BLOCKS. NO BLOCKS WERE FOUND IN ANY OF THE INSPECTED RELAYS. ADDITIONAL ADMINISTRATIVE CONTROLS ON THE USE AND REMOVAL OF BLOCKS AND/OR JUMPERS ON RELAYS DURING PERIODIC PROTECTIVE RELAY CALIBRATION HAVE BEEN ISSUED. ADDITIONAL EMPHASIS AND GUIDANCE ON TIMELY RESTORATION OF OFF SITE POWER HAS BEEN GIVEN. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF A LOSS OF OFF SITE POWER DUE TO A LINE PERTURBATION.
456 | 4561988025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561988025R00.pdf | 1988-11-15 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [9 empty] | X | [5 empty] | X | [24 empty] | X | Braidwood 1 | P | WE | PO | 96 | POWER LEVEL - 096%. AT 0904 ON NOVEMBER 15, 1988 LOW INSTRUMENT AIR PRESSURE WAS OBSERVED. THE RAPID DECREASE IN THE INSTRUMENT AIR HEADER PRESSURE CAUSED THE FEEDWATER REGULATING VALVES TO GO CLOSED. THIS DECREASED FLOW TO THE STEAM GENERATORS ON BOTH UNITS. AT 0908 BOTH UNITS WERE MANUALLY TRIPPED DUE TO DECREASING STEAM GENERATOR LEVELS. THE CAUSE OF THIS EVENT WAS INADEQUATE INSTALLATION OF A COUPLING IN THE INSTRUMENT AIR HEADER, LINE 0IA05B DURING CONSTRUCTION. THE INADEQUATE SOLDER JOINT WAS STRESSED BY CONTRACT PERSONNEL STANDING ON THE LINE. THE INSTRUMENT AIR HEADER WAS ISOLATED AND THE LINE REPAIRED BY REPLACING THE JOINT. THE LINE WAS INSPECTED UPSTREAM AND DOWNSTREAM OF THE BREAK FOR OTHER POSSIBLE LEAKS THAT MAY HAVE OCCURRED AS A RESULT OF THE BREAK. TWO OTHER JOINTS WERE REPAIRED FOR PINHOLE LEAKS. ADDITIONAL PIPE SUPPORTS WILL BE ADDED TO THE HEADER. A LETTER WAS ISSUED ON NOVEMBER 16, 1988 TO ALL SITE PERSONNEL REEMPHASIZING THE NEED FOR ALL PERSONNEL TO EXERCISE CARE IN WORKING AROUND ALL PLANT EQUIPMENT. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF A REACTOR TRIP AS A RESULT OF A LOSS OF INSTRUMENT AIR.
456 | 4561989004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561989004R00.pdf | 1989-03-06 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Braidwood 1 | P | WE | PO | 97 | POWER LEVEL - 097%. AT 0100 ON 3/6/89 A SURVEILLANCE WAS IN PROGRESS TO TEST TRAIN B TURBINE TRIP RELAY K640. DURING THE INITIAL PREPARATION STEPS OF THE PROCEDURE THE INTERFACE DIAPHRAGM VALVE TEST VALVE CONTROL SWITCH, CS/DVT, IS TAKEN FROM THE NORM (NORMAL) TO THE PERM (PERMISSIVE) POSITION. THE PERM SET (TEST PERMISSIVE ENABLED) LIGHT IS VERIFIED ILLUMINATED ON THE CONTROL PANEL. THIS INITIAL SETUP PROVIDES FOR TESTING WITHOUT TRIPPING THE MAIN TURBINE. AT 0154, A NUCLEAR STATION OPERATOR DEPRESSED THE RELAY TEST SWITCH. THE GOVERNOR VALVES DRIFTED TO THE CLOSED POSITION. THE CLOSURE OF THE GOVERNOR VALVES RESULTED IN A DECREASE IN STEAM FLOW AND AN INCREASE IN STEAM PRESSURE WHICH HAD A 'SHRINK' EFFECT ON STEAM GENERATOR LEVEL INSTRUMENTATION. THE INDICATED LEVELS OF 1C AND 1D STEAM GENERATORS DECREASED TO THE LOW LOW LEVEL REACTOR TRIP SETPOINT AND THE REACTOR TRIPPED, TURBINE TRIPPED, AND THE AUXILIARY FEEDWATER PUMPS AUTO STARTED. THE CAUSE OF THIS EVENT WAS A DEFECTIVE TEST SWITCH, CS/DVT. THE FAILURE OF THE SWITCH RESULTED IN THE CONTROL SYSTEM REDUCING THE GOVERNOR VALVE POSITION LIMITS TO ZERO. THE SWITCH WILL BE REPLACED. PREVIOUS EVENT CORRECTIVE ACTION WAS NOT APPLICABLE TO THIS EVENT.
456 | 4561989006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561989006R00.pdf | 1989-07-18 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 1 | P | WE | PO | 86 | POWER LEVEL - 086%. AT 2020 AND 2026 ON 7/18/89 THE STATION EXPERIENCED LIGHTNING INDUCED VOLTAGE TRANSIENTS CAUSING MULTIPLE ROD DRIVE OVERVOLTAGE PROTECTION DEVICES TO ACTUATE ON UNIT 1 AND 2, RESPECTIVELY. ON UNIT 1 TEN OUT OF TEN OVERVOLTAGE PROTECTORS ACTUATED. ON UNIT 2 SEVEN OUT OF TEN OVERVOLTAGE PROTECTORS ACTUATED. THIS REMOVED POWER TO VARIOUS ROD DRIVE CONTROL CARDS AND ALLOWED NUMEROUS CONTROL RODS TO DROP. BOTH REACTORS TRIPPED DUE TO NEGATIVE RATE TRIP ON THE POWER RANGE. IMMEDIATE CORRECTIVE ACTIONS WERE TO STABILIZE THE PLANT, RESET THE OVERVOLTAGE PROTECTORS, AND VERIFY ROD CONTROL OPERABILITY. THE EXACT LOCATION OF THE LIGHTNING STRIKES ARE UNKNOWN. THE ROOT CAUSE IS INADEQUATE PROTECTION AND ISOLATION OF THE ROD CONTROL SYSTEM FROM LIGHTNING INDUCED TRANSIENTS. THE IMMEDIATE CORRECTIVE ACTIONS WERE TO RESET THE OVERVOLTAGE PROTECTORS. NO DAMAGE OCCURRED TO THE ROD CONTROL SYSTEM. THERE HAS BEEN ONE PREVIOUS OCCURRENCE OF A LIGHTNING INDUCED VOLTAGE TRANSIENT RESULTING IN A REACTOR TRIP. CORRECTIVE ACTIONS WERE IMPLEMENTED ADDRESSING BOTH ROOT AND CONTRIBUTING CAUSES FOR THE ABOVE EVENT. THE PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE TO THIS EVENT.
456 | 4561990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561990001R00.pdf | 1990-01-12 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 99 | A DC ground investigation was in progress on 125V DC Bus 114 in accordance with procedure. An Equipment Operator(EO) and a Shift Foreman were systematically isolating and restoring loads to identify the ground. Circuit number 19 was identified as the feed to the Generator Relay Normal Power. The procedure specified transferring to reserve power using a dead bus transfer procedure. At 1324 the EO opened circuit number 19 per procedure. When the circuit was opened an auxiliary relay was deenergized which provided input to Electo-Hydraulic Control System (DEHC). When the relay deenergized the DEHC system sensed that the Main Generator was disconnected from the transmission system with turbine load above 30%. This initiated a Load Drop Anticipation (LDA) sequence causing the Turbine Governor Valves to close. This caused steam pressure to increase and steam flow to decrease resulting in a Low Low Steam Generator Water Level Reactor Trip from the shrink effects on level indication. The cause of the event was a procedural deficiency. The procedure did not caution that an LDA would occur if turbine power was above 30%. The DC ground disappeared shortly after the Reactor Trip and did not return when the unit returned to power. The procedure has been temporarily revised. An evaluation of the methodology and content of the procedure will be conducted. No previous occurrences. occurrences.
456 | 4561990008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561990008R00.pdf | 1990-06-08 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On June 8, 1990 there was heavy thunderstorm activity in the Braidwood Station area. At 0618 a reactor trip occurred on Unit 1 due to a high flux rate trip signal from the Power Range Nuclear Instrumentation. The Reactor Operators verified all automatic actions. All systems functioned as designed. Stable plant conditions were immediately established. An examination of the Rod Drive (RD) Power Cabinets indicated the power supply over voltage protectors (PSOVP) had tripped in three of the RD Cabinets. There were no blown fuses identified in any of the cabinets. The PSOVP's were reset and all voltages were checked. The root cause of this event was a voltage transient. It is believed that lightning struck the Unit 1 Containment and caused a voltage surge in the station ground system. This caused the activation of PSOVPs in the three RD Power Cabinets. This shut off the current to the stationary gripper coils of the rods powered by the cabinets, and caused them to drop, resulting in a negative flux rate. The negative flux rate was of sufficient magnitude to activate the reactor trip signal from the Power Range Nuclear Instrumentation. No damage occurred to the RD system. A review of the station lightning protection system is being conducted. The Station had made modifications to the RD power supply system and the station grounding system as corrective measures from previous events.
456 | 4561990018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561990018R00.pdf | 1990-09-29 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Braidwood 1 | P | WE | PO | 92 | At 0345 on September 29, 1990 the Train B Solid State Protection System (SSPS) initiated a Containment Ventilation Isolation Signal. No components repositioned as all were in their required state. At 1735 a spurious Train B Safety Injection Signal (SI) occurred causing a Reactor Trip and Containment Isolation to occur as well as starting Train B ECCS components. The B Train of SSPS was declared inoperable and a plant cooldown was initiated. At 0013 on September 30, 1990 a Reactor Operator was performing an SSPS test procedure when the Train B SSPS Memories Test switch was inadvertently rotated from Off to position 23. This enabled the Pressurizer and Steamline Low pressure SI and Steamline Isolation circuits which had been blocked. With both pressures below their respective setpoints, a Train B SI and a Steamline Isolation occurred. Due to the Steamline isolation, the RCS temperature increased about 12 degrees from 340 to 352 degrees F over the next 14 minutes until cooling was re-established. 350 degrees F is the lower limit of Mode 3 operation. At 1020 on October 3, 1990 a spurious Train B Feedwater Isolation occurred with the Unit in Cold Shutdown. The causes of the event were component failure, personnel error, and component design interface. Train B SSPS was repaired, training will be provided, and the Memories Test Switch was re-oriented. Previous Corrective actions are not applicable to this event.
456 | 4561990021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561990021R00.pdf | 1990-12-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 1 | P | WE | PO | 99 | At 1645 on December 1, 1990 the 1B Feedwater Pump (FW), one of the two on line FW pumps, tripped. The Nuclear Station Operator (NSO) initiated a turbine runback to 60% power in accordance with procedure. Steam Generator (SG) levels decreased due to both the reduction in FW flow from the loss of the FW pump and the "shrink" effect on the SG level instrumentation from the reduction in Steam Flow as a result of the turbine runback. At 1647 the level in the 1B SG reached the Lo-2 reactor trip setpoint and a Reactor Trip, Turbine Trip, Feedwater Isolation, and Auxiliary FW automatic initiation occurred as designed. All components associated with these actuations functioned as designed. The cause of the FW pump trip was low oil pressure. It is believed that the suction of the high pressure oil pump became partially plugged from a sludge burst. The standby oil pump started but the low pressure "dip" that occurred was of sufficient magnitude to reach the low oil pressure trip setpoint. The turbine runback was initiated, but equilibrium FW flow /Steam flow was not achieved prior to reaching the Reactor Trip setpoint. A contributing cause to the event was a procedural deficiency. The procedure did not address closing the recirculation valve on the tripped FW pump. The oil system has been cleaned and is being monitored. The procedure has been revised. No previous occurrences.
456 | 4561990023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561990023R00.pdf | 1990-12-30 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 98 | On December 30, 1990, Unit 1 was load following to accommodate system demand for the Commonwealth Edison Company system load dispatcher. At 0815 the Unit completed a power ascension to full capability. At 0821 a Generator Neutral Ground Overcurrent protective relay actuated and tripped the Unit 1 Main Generator. A turbine and reactor trip followed as designed. Megger testing revealed a ground on the "C" phase of the Main Generator. The cause of the ground was an internal generator defect. The generator vendor, Westinghouse, was contacted to provide assistance in locating the fault. Upon application of Hi Potential Alternating Current to the "C" Phase, observation of smoke and electrical arcing revealed that the fault was in the bottom coil in slot 29 of the stator. Damage to the coil was attributed to a vent spacer that came loose. Vibration during normal operation allowed the spacer to rub and wear down insulation protecting the coil. The ground was created as a result of insulation breakdown. The coil was removed from the stator and sent to the vendor. This component failure is considered to be an isolated event. There have been previous occurrences of a reactor trip caused by a generator trip. Previous corrective actions and contributing root cause are not applicable to this event.
456 | 4561991012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561991012R00.pdf | 1991-11-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 1 | P | WE | PO | 100 | Prior to the event, significant leakage had been identified on Main Feedwater (FW) motor-operated isolation valve 1FW006A. The valve is in the flowpath to the 1A Steam Generator (S/G). Attempts to reduce leakage had been unsucessful due to the high temperature and pressure of the water spraying from the valve body. Repairing the valve required a unit shutdown. The plant was scheduled to be taken off-line on November 2, 1991. On November 1, 1991 due to a low reserve margin on the Commonwealth Edison Co. system grid, the load dispatcher requested that the outage be postponed. The leakage was not affecting unit capacity, since all S/G levels could be maintained at their normal level (66%). At 0013 on November 6, 1991 an Electro-Hyrdaulic (EH) fluid leak tripped the 1B FW pump. Control room personnel initiated a turbine runback. S/G levels in all four S/G's decreased due to the reduction in total FW flow. After the turbine runback was completed, S/G levels in the 1B, 1C and 1D S/G's stabilized at 45%. However, the 1A S/G level continued to decrease. At 0017 the level in the 1A S/G reached the Low-Low level reactor trip setpoint (40.8%) and a Reactor Trip occurred. The root cause of the 1B FW pump trip was a crack in a 5/8 inch EH supply line. The line was repaired. A contributing cause to the reactor trip was the 1FW006A valve leakage on the FW supply line to the 1A S/G. Valve FW006A was repaired and returned to service.
456 | 4561993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561993001R00.pdf | 1993-01-07 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On January 7, 1993 while performing Unit One Reactor Coolant Pump Underfrequency Quarterly Surveillance, Unit One experienced a Reactor Trip. The failed component was on the A215 Universal Logic Card which is the decision maker for the 2 out of 4 logic in the RCP-UF circuit. The A215 card was replaced and the SSPS Bi-monthly Diagnostics test was reperformed to ensure the replacement card functioned properly and verify the complete SSPS system was operational. The failed Universal Logic card was sent to the vendor for a detailed failure analysis. There have been previous occurrences of spurious ESF actuations due to problems in the Train B SSPS circuitry.
456 | 4561994012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561994012R00.pdf | 1994-08-11 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Braidwood 1 | P | WE | PO | 100 | At approximately 1028 a.m. on August 11, 1994, Braidwood Unit 1 experienced a spurious Train 'A' Main Steam Line Isolation followed by an automatic reactor trip from Low Low water level on the 1C Steam Generator. Both Pressurizer PORV's cycled as designed to relieve the RCS pressure transient. Steam was released to the atmosphere via the steam generator PORV's and Main Steam safety valves. Control Room Operators stabilized the plant using the Emergency Operating Procedures. All systems operated as designed following the MSIV closure to mitigate the transient. During subsequent cooldown of the RCS a second Main Steam Line Isolation signal was received which closed all four MSIV Bypass valves. failure of the Q7 output transistor on the A516 Safeguards Output Driver Board in Train A of the Solid State Protection System. The failed A516 circuit board was replaced and the Train 'A' SSPS bimonthly surveillance was performed satisfactorily.
456 | 4561995004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561995004R00.pdf | 1995-04-09 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Braidwood 1 | P | WE | PO | 100 | At 0310 on 04/09/95, with unit 1 at 99% power, Instrument Inverter 111 failed, causing a loss of the Vital AC Instrument Bus 111 and failure of twenty-five 7300 Process Control Cabinet cards. Two of the 7300 card failures, FT-510 for 1A Steam Generator feedwater flow and PT-508 for Main Feed header pressure, resulted in the 1A Steam Generator feedwater regulating valve failing open and the master feedwater pump speed controller failing to maximum demand. The NSO took manual control of the 1A feedwater regulating valve but was unable to prevent the Steam Generator from reaching the P-14 trip setpoint. A Turbine trip above P-8 Reactor Trip occurred from the 1A Steam Generator level above the P-14 setpoint. <br /><br /> At 0326 the Instrument Bus was energized from it's associated Constant Voltage Transformer (CVT). Subsequent investigation revealed a blown fuse in Instrument Inverter 111 caused by a failed firing card. The 7300 cards failed due to a voltage spike from the inverter prior to the fuse blowing.<br /><br /> The unit was stabilized in Mode 3 and remained in Mode 3 at NOT/NOP while the Instrument Inverter was repaired and all failed 7300 cards that failed were repaired or replaced.
456 | 4562007001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4562007001R00.pdf | 2007-06-27 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On June 27, 2007, at 0921 hours, Braidwood Unit 1 reactor tripped from 100% power following a grid disturbance on a 345 Kv transmission line due to a lightning strike. This disturbance caused an actuation of protective relays for the 1D reactor coolant pump. The shutdown of the reactor coolant pump (RCP) resulted in a rapid reduction of coolant flow in the 1D reactor coolant loop and subsequent Reactor Protection System actuation to trip the Unit 1 reactor. Operator response to the trip was proper and all safety related systems, structures and components operated normally during this event.The Root Cause of the Unit 1 trip was determined to be a latent design weakness in the RCP protective scheme that permitted the existence of an undetected component failure creating a grid disturbance-intolerant vulnerability. Corrective actions in response to this issue include revising identified procedures to perform monitoring of the integrity of critical fuses within trip-sensitive protective relaying circuits, and implementation of design changes to reduce or eliminate the identified vulnerability from the RCP protective relaying system, or if design changes are not appropriate, develop alternate actions to address the vulnerability.There were no safety consequences impacting plant or public safety as a result of this event.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System (Reactor Trip) and the Auxiliary Feedwater System.
456 | 4562010001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4562010001R01.pdf | 2010-08-16 | QL7 | Degraded condenser vacuum | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On August 16, 2010, as a result of a Unit 2 reactor trip, condensate water overflowed from the auxiliary feedwater (AF) standpipes onto the turbine deck. The water spread through openings in the floor to the elevation below, and entered a Unit 1 substation cabinet. This water intrusion resulted in the trip of electrical buses that caused the 1A and 1C circulating water (CW) pumps to trip. Additionally, power to the respective CW pump discharge valves was lost. These conditions caused the Unit 1 condenser vacuum to degrade. At 0219, the Unit 1 main turbine received an automatic trip on low condenser vacuum, resulting in an automatic reactor trip. Following the reactor trip, the auxiliary feedwater pumps auto started on low-low steam generator water levels.The root causes were determined to be: 1) an inadequate design of the AF standpipes; and 2) a lack of sensitivity evolved that tolerated long-term uncontained water issues with inadequate evaluation for potential impacts. The corrective action to prevent recurrence is to install a design feature on the AF suction standpipe which prevents water spill events. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
456 | 4562010004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4562010004R00.pdf | 2010-09-20 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On September 20, 2010, Maintenance initiated performance of a Technical Specification surveillance calibration of a steam generator water level channel. At 1704, when a bistable for the channel under test was placed in the tripped condition per the surveillance, an automatic turbine trip was received. The turbine trip was immediately followed by an automatic reactor trip due to the turbine trip while the reactor was greater than 30% power. Following the reactor trip, the auxiliary feedwater pumps auto started on low-2 steam generator water levels. Investigation determined that a universal logic card in the solid state protection system failure resulted in one input being in the tripped state, creating an unknown half trip condition. During performance of the channel calibration when the coincident loop bistable was tripped, the 2-of-4 logic was met which caused an immediate turbine trip. The direct cause for this event was failure of the universal logic card. The root cause evaluation has not been completed.The corrective actions to prevent recurrence include implementing first time preventative maintenance replacements of the SSPS universal logic cards for Unit 1 (completed) and Unit 2 (scheduled).There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
456 | 4562018005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4562018005R00.pdf | 2018-04-30 | QR5 | Turbine Trip | [45 empty] | Braidwood 1 | P | WE | PO | 48 | On April 30, 2018, at 1124 hours, during power ascension from refueling outage A1R20, Unit 1 tripped from approximately 48 percent power as a result of a turbine motoring generator trip. At 1126 hours, the 1A auxiliary feedwater (AF) pump was manually started to provide feedwater flow to all four steam generators. <br /><br /> The cause of the event was due to a welded-over sensing inlet line from the turbine exhaust piping in 2015, in combination with a failed differential pressure switch assembly, which allowed pressurization of all three differential pressure sensing devices resulting in the 2-out-of-3 turbine trip logic being satisfied. Corrective actions taken included installing a temporary modification opening a test switch in the Unit 1 anti-motoring circuit, and revoking the welding qualification for the welder involved in welding over the instrument sensing line. Actions planned include repairing the sensing line in the next Unit 1 refueling outage to restore function. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..."
456 | 4562018006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4562018006R00.pdf | 2018-06-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 1 | P | WE | PO | 100 | On June 4, 2018, at 0920 hours, Braidwood Unit 1 was manually tripped due to lowering steam generator water levels following a trip of the 1C turbine driven feedwater pump. The 1A and 1B auxiliary feedwater (AF) pumps auto started as expected due to low steam generator levels. <br /><br /> The cause of the event was due to the inclusion of a digital input module in the turbine driven feedwater pump control circuitry, which affected only the safeguards testing function of the circuit, and which was not identified as a design input per the design input and configuration change impact screening procedure. Corrective actions planned include implementing the changes to eliminate the design deficiency, and revising the design input and configuration change impact screening procedure. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..." Specifically, for 1) 10 CFR 50.73(a)(2)(iv)(B)(1) for the "Reactor protection system (RPS) including: reactor scram or reactor trip," and 2) 10 CFR 50.73(a)(2)(iv)(B)(6) for the "PWR auxiliary or emergency feedwater system."
457 | 4571988012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988012R01.pdf | 1988-06-20 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 48 | POWER LEVEL - 048%. AT 1212 ON JUNE 20, 1988, PREPARATIONS IN PROGRESS TO TAKE CURRENT READINGS ON PHASE B OVERCURRENT PROTECTIVE RELAY CO-7 ON UNIT AUXILIARY TRANSFORMER (UAT) 241-2. A SHORTING SWITCH ON THE RELAY CASING WAS INTENTIONALLY OPENED AS PART OF THE PREPARATIONS. THIS RESULTED IN A VOLTAGE SPIKE AND ACTUATED THE INSTANTANEOUS OVERCURRENT PROTECTIVE RELAY; SI. THIS ACTUATED LOCKOUT RELAY 86G2A WHICH ISOLATED UAT 241-2 FROM THE GIRD AND TRIPPED THE UNIT 2 MAIN GENERATOR. THIS INITIATED A TURBINE AND REACTOR TRIP. THE TURBINE MAIN FEEDWATER PUMP TRIPPED WHICH RESULTED IN A LO-LO STEAM GENERATOR LEVEL. THE AUXILIARY FEEDWATER PUMPS (AF) AUTOMATICALLY STARTED TO RESTORE STEAM GENERATOR LEVEL. AT 1225, THE STARTUP FEEDWATER PUMP WAS MANUALLY STARTED. AT 1229, FEEDWATER FLOW WAS RESTORED TO THE NORM RANGE. AT 1236, THE PLANT WAS STABILIZED. AT 1236, THE AF PUMPS WERE MANUALLY TRIPPED. AT 1242, THE PROTECTIVE RELAYS WERE RESET. THE ROOT CAUSE OF THIS EVENT IS ATTRIBUTED TO A DEFECTIVE CURRENT TEST SWITCH ON THE B PHASE OF THE CO-7 OVERCURRENT RELAY. THE DEFECTIVE TEST SWITCH ON THE PHASE B CO-7 RELAY CASE WAS REPLACED AND THE INTEGRITY OF THE CURRENT CIRCUITRY WAS RE-VERIFIED. THIS IS CONSIDERED AN ISOLATED EVENT, NO FURTHER CORRECTIVE ACTION IS PROPOSED. NO PREVIOUS OCCURRENCES.
457 | 4571988013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988013R00.pdf | 1988-06-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | SU | 3 | POWER LEVEL - 003%. AT 0107 ON JUNE 21, 1988, A REACTOR TRIP OCCURRED AS THE RESULT OF A LO-LO STEAM GENERATOR LEVEL. THIS WAS DUE TO INSUFFICIENT FEEDWATER FLOW TO THE 2A STEAM GENERATOR. THE LOW FLOW WAS THE RESULT OF AN OUT-OF-SERVICE ASSOCIATED WITH FEEDWATER REGULATING VALVE. THE CAUSE OF THIS EVENT WAS A PROCEDURAL DEFICIENCY IN THAT THE PLANT STARTUP PROCEDURE DID NOT ADDRESS THE PROPER FEEDWATER REGULATING STATION LINEUP PRIOR TO INCREASING REACTOR POWER TO APPROXIMATELY 3%. ACTION TO PREVENT RECURRENCE INCLUDED: 1) PROCEDURE BWGP 100-2 WAS REVISED TO VERIFY THE LINE UP FOR THE MANUAL VALVES AT THE FEEDWATER REGULATING STATION ARE CORRECT PRIOR TO INCREASING REACTOR POWER FROM THE POINT OF ADDING HEAT; 2) A REVIEW OF THE EVENT WAS CONDUCTED WITH THE INDIVIDUALS INVOLVED STRESSING THE NEED FOR AWARENESS OF SYSTEM CONFIGURATION STATUS; AND 3) A MEMO WAS ISSUED TO SHIFT AND NSO PERSONNEL EXPLAINING THE EVENT, IMMEDIATE CORRECTIVE ACTIONS, ACTIONS TO PREVENT RECURRENCE AND THE NEED TO USE PROCEDURE BWAP 300-1 WHICH OUTLINES WAYS THE NSO IS TO BE MADE AWARE OF NON-STANDARD LINEUPS THAT ARE BROUGHT TO HIS ATTENTION. THERE HAVE BEEN NO PREVIOUS REACTOR TRIPS AS THE RESULT OF FEEDWATER VALVE OUT OF SERVICE.
457 | 4571988014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988014R01.pdf | 1988-06-22 | QP5 | Excessive Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 25 | POWER LEVEL - 025%. AT 0029 ON JUNE 22, 1988, A REACTOR TRIP OCCURRED AS THE RESULT OF A LO-LO LEVEL ON STEAM GENERATOR (S/G) 2B. DURING THE TRANSFER OF THE FEEDWATER SYSTEM FROM THE FEEDWATER REGULATING BYPASS VALVES (FWRBPV) TO THE MAIN FEEDWATER REGULATING VALVES (MFWRV), THE MFWRV INADVERTENTLY OPENED TO APPROXIMATELY 15%. THE MFWRV DID NOT RESPOND TO A CLOSURE SIGNAL AND S/G WATER LEVEL INCREASED TO THE HI-HI LEVEL SET POINT. THIS RESULTED IN A TURBINE TRIP, FEEDWATER ISOLATION, AND A FEEDWATER PUMP TRIP. S/G LEVEL RAPIDLY FELL, AND 18 SECONDS LATER S/G 2D REACHED THE LO-LO LEVEL SETPOINT RESULTING IN A REACTOR TRIP AND AUTOMATIC START OF BOTH AUXILIARY FEEDWATER PUMPS AS DESIGNED. THE CAUSE OF THIS EVENT WAS LOW STATIC SPRING PRELOAD, DIRT AND GREASE PARTIALLY BLOCKING THE VOLUME BOOSTER, AND DYNAMIC SYSTEM TUNING WAS IDENTIFIED AS NEEDED TO PROVIDE PROPER FEEDWATER REGULATING VALVE ACTION IN RESPONSE TO VALVE DEMAND. IMMEDIATE CORRECTIVE ACTION WAS TO RESTORE S/G WATER LEVEL TO NORMAL. THE FEEDWATER REGULATING VALVE WAS REPAIRED PRIOR TO BEING RETURNED TO SERVICE. THERE HAVE BEEN NO PREVIOUS OCCURRENCES AS A RESULT OF ERRATIC FEEDWATER REGULATING VALVE OPERATIONS.
457 | 4571988016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988016R00.pdf | 1988-06-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 21 | POWER LEVEL - 021%. AT 1221 ON JUNE 24, 1988, A REACTOR TRIP OCCURRED ON 2B STEAM GENERATOR (S/G) LOW-LOW LEVEL. THE AUXILIARY FEEDWATER PUMPS AUTOMATICALLY STARTED TO MAINTAIN S/G LEVELS AS DESIGNED. THE CAUSE OF THE LOW-LOW S/G LEVEL WAS THE FAILURE OF 2HD122, HEATER DRAIN TANK MAKEUP VALVE. THE VALVE FAILED OPEN AS A RESULT OF THE FEEDBACK CAM FALLING OFF. THE CAM PROVIDES APPROPRIATE SUPPLY AND POSITIONING CONTROL AIR TO THE MAKEUP VALVE. FAILURE OF 2HD122 IN THE FULLY OPEN POSITION CAUSED THE CONDENSATE BOOSTER PUMP DISCHARGE PRESSURE TO DECREASE RESULTING IN A LOSS OF FEEDWATER FLOW. THE REACTOR TRIP OCCURRED APPROXIMATELY 60 SECONDS AFTER THE LOSS OF FEEDWATER FLOW. SYSTEM PARAMETERS DID NOT DECREASE TO THE AUTOMATIC ACTUATION SETPOINT TO START THE STANDBY CONDENSATE/CONDENSATE BOOSTER PUMP. THE IMMEDIATE CORRECTIVE ACTION WAS TO RECOVER THE STEAM GENERATOR LEVELS AND ESTABLISH STABLE CONDITIONS. VALVE 2HD122 WAS REPAIRED UTILIZNG LOC-TITE PRIOR TO RETURNING THE UNIT TO SERVICE. MONITORING OF THIS VALVE BY THE INSTRUMENT MAINTENANCE DEPARTMENT, SINCE ITS REPAIR, HAS SHOWN NO DEGRADATION. A WALKDOWN OF SECONDARY FEEDWATER LOOP SYSTEMS WAS PERFORMED WITH NO ABNORMALITIES FOUND. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF A FEEDBACK CAM FAILURE.
457 | 4571988018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988018R00.pdf | 1988-07-02 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 2 | P | WE | PO | 40 | POWER LEVEL - 040%. AT 2304 ON JULY 2, 1988, A REACTOR TRIP OCCURRED WHILE CONDUCTING STARTUP TEST BWSU NR-75A, AXIAL FLUX DIFFERENCE CALIBRATION. PER THE TEST PROCEDURE, PRESSURIZER PRESSURE CHANNEL 455C BISTABLE WAS PLACED IN THE TRIPPED CONDITION. DURING THE TEST, PRESSURIZER PRESSURE (AB) BISTABLE 457C FAILED, COMPLETING THE 2 OUT OF 4 LOGIC NEEDED FOR A REACTOR TRIP. POST TRIP RESPONSE WAS NORMAL EXCEPT THAT BUS 243, A NON SAFETY RELATED BUS, DID NOT AUTO TRANSFER FROM THE UNIT AUXILIARY TRANSFORMER TO THE SYSTEM AUXILIARY TRANSFORMER. THIS WAS DONE MANUALLY BY AN EQUIPMENT ATTENDANT. A FEEDWATER ISOLATION OCCURRED BECAUSE OF THE LOW AVERAGE TEMPERATURE AND REACTOR TRIP. BOTH AUXILIARY FEEDWATER PUMPS AUTO STARTED BECAUSE OF A LO-LO LEVEL IN THE STEAM GENERATORS (SJ). CONDITIONS WERE STABILIZED BY 2330. THE ROOT CAUSE OF THE EVENT WAS THE FAILURE OF PRESSURIZER PRESSURE BISTABLE 457C IN CONJUNCTION WITH PRESSURIZER PRESSURE BISTABLE 455C BEING IN A TRIPPED CONDITION. THE FAILURE OF THE 457C BISTABLE WAS CAUSED BY A FAILURE OF THE COMPARATOR CARD. CORRECTIVE ACTIONS INCLUDED REPLACING THE FAILED CARD AND TO REPAIRING THE BREAKER. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF A REACTOR TRIP AS THE RESULT OF A FAILED BISTABLE CARD WHILE CONDUCTING A STARTUP TEST.
457 | 4571988019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988019R00.pdf | 1988-07-24 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Braidwood 2 | P | WE | PO | 74 | POWER LEVEL - 074%. AT 1432 ON JULY 24, 1988, THE REACTOR WAS MANUALLY TRIPPED DUE TO DECREASING STEAM GENERATOR LEVELS. THE 2A AND B AUXILIARY FEEDWATER PUMPS AUTO STARTED ON LO LO STEAM GENERATOR LEVELS. CAUSE OF THIS EVENT IS ATTRIBUTED TO MISPOSITIONING OF AN INSTRUMENT AIR (IA) ISOLATION VALVE IN THE 90% CLOSED POSITION AS OPPOSED TO ITS CORRECT POSITION OF 100% OPEN. THIS VALVE SUPPLIES IA TO VARIOUS HEATER DRAIN VALVES AND CONTROLLERS. IT IS STRONGLY SUSPECTED BY PHYSICAL EVIDENCE AND A RE-ENACTMENT OF THE PATH TAKEN BY THE CONTRACTOR WORKING IN THE AREA THAT THE VALVE COULD HAVE BEEN UNKNOWINGLY MISPOSITIONED. IMMEDIATE CORRECTIVE ACTIONS WERE TO RECOVER STEAM GENERATOR LEVELS AND ESTABLISH STABLE CONDITIONS. THE 25 AND 26 HEATERS NORMAL AND EMERGENCY DRAIN VALVES WERE STROKED TO ENSURE OPERABILITY. THE NORMAL AND EMERGENCY LEVEL CONTROLLERS FOR THE 25, 26, AND 27 HEATERS WERE CHECKED AND NO PROBLEMS WERE FOUND. A CHECK OF THE INSTRUMENT AIR VALVES IN THE TURBINE BUILDING IN AREAS OF ONGOING WORK WAS MADE WITH NO MISPOSITIONED VALVES FOUND. THIS IS CONSIDERED AN ISOLATED EVENT SINCE SCAFFOLDING WAS NEEDED FOR INSULATION WORK IN THE AREA OF THE VALVE. THERE HAS BEEN NO PREVIOUS OCCURRENCES OF A MISPOSITIONED VALVE RESULTING IN A REACTOR TRIP DUE TO PERSON OR PERSONS UNKNOWN.
457 | 4571988020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988020R00.pdf | 1988-09-04 | QP3 | Loss of Condensate Flow | [45 empty] | Braidwood 2 | P | WE | PO | 81 | POWER LEVEL - 081%. THE MOISTURE SEPARATOR REHEATER (MSR) FIRST STAGE REHEATER DRAIN TANK NORMAL DRAIN VALVE WAS OUT OF SERVICE, WITH THE EMERGENCY DRAIN VALVE MAINTAINING LEVEL. APPROXIMATELY 0238, AN INCREASE IN STEAM/FEEDWATER FLOW, AND REACTOR POWER WAS OBSERVED. TURBINE POWER WAS MANUALLY REDUCED. THE CONDENSATE PUMP SUCTION STRAINERS STARTED TO PLUG. AT 0253, THE REACTOR WAS MANUALLY TRIPPED DUE TO DECREASING 2D STEAM GENERATOR LEVEL. THIS CAUSE WAS A FAILURE OF THE EMERGENCY DRAIN VALVE WHICH ROUTED EXTRACTION STEAM INTO THE MAIN CONDENSER, DISCHARGING INTERNAL SCALING INTO THE CONDENSATE PUMP SUCTION STRAINERS. THE IMMEDIATE CORRECTIVE ACTION WAS TO RECOVER STEAM GENERATOR LEVELS AND ESTABLISH STABLE CONDITIONS. THE CONTROLLER FOR EMERGENCY DRAIN VALVE WAS CHECKED, NO PROBLEMS FOUND; THE VALVE WAS EXERCISED MANUALLY SEVERAL TIMES. NO APPARENT REASON FOR THE VALVE STICKING COULD BE IDENTIFIED. THE VALVE WAS LEFT IN AN OPERABLE STATUS. THERE HAVE BEEN TWO PREVIOUS OCCURRENCES OF A REACTOR TRIP AS A RESULT OF HEATER DRAIN SYSTEM PERTURBATIONS, CORRECTIVE ACTIONS WERE IMPLEMENTED. THE ROOT CAUSE OF THIS EVENT IS DIFFERENT. PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE TO THIS EVENT.
457 | 4571988022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988022R00.pdf | 1988-09-19 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Braidwood 2 | P | WE | SU | 3 | POWER LEVEL - 003%. AT 1800 ON SEPTEMBER 19, 1988 A REACTOR TRIP OCCURRED DUE TO SOURCE RANGE CHANNEL N31 EXCEEDING ITS SETPOINT OF 1.0XE5 COUNTS PER SECOND (CPS). 'A' REACTOR TRIP BREAKER OPENED AUTOMATICALLY. THE NUCLEAR STATION OPERATOR INITIATED A MANUAL TRIP TO OPEN THE 'B' REACTOR TRIP BREAKER. THE CAUSE OF THIS EVENT WAS DUE TO A LOOSE CONNECTION IN MAIN CONTROL ROOM PANEL 2PM05J, WHICH ALLOWED CHANNEL N-31 TO RE-ENERGIZE. SINCE REACTOR POWER WAS APPROXIMATELY 3%, THE REACTOR TRIP OCCURRED. SUBSEQUENT INVESTIGATION REVEALED THAT AN ACTUATION HAD ONLY OCCURRED ON TRAIN 'A' AND NO FAILURE OF TRAIN 'B' ACTUALLY OCCURRED. THE INVESTIGATION REVEALED LOOSE CONNECTIONS AT THE BACK OF 2PM05J WHICH WERE ASSOCIATED WITH THE VARIOUS NUCLEAR INSTRUMENTATION SYSTEM BLOCKING FUNCTIONS. THESE CONNECTIONS WERE TIGHTENED TO PREVENT ANY FURTHER BREAKERS IN THE BLOCKING CIRCUITS. ADDITIONAL TERMINAL STRIPS WERE CHECKED FOR LOOSE CONNECTIONS ON BOTH UNITS. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF LOOSE CONNECTIONS IN THE SOURCE RANGE RESULTING IN A REACTOR TRIP.
457 | 4571988026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988026R00.pdf | 1988-09-23 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Braidwood 2 | P | WE | PO | 38 | POWER LEVEL - 038%. IN RESPONSE TO AN ANOMALY IDENTIFIED ON ONE OF THE 2A STEAM GENERATOR LEVEL TRANSMITTERS, IT WAS DETERMINED THAT SIMULTANEOUS DATA COLLECTION WAS REQUIRED. THE METHOD WAS REVIEWED BY THE APPROPRIATE PERSONNEL INVOLVED WITH THE TASK AND APPROVAL WAS GIVEN TO START. AT 1347 WHEN THE SECOND CHANNEL OF THE SECOND PHASE OF DATA COLLECTION WAS ATTACHED, A TURBINE TRIP AND REACTOR TRIP OCCURRED. CAUSE OF THE EVENT WAS PERSONNEL ERROR IN THAT THE REVIEW PROCESS FAILED TO IDENTIFY THE NORMALLY GROUNDED CONNECTION ON THE TEST EQUIPMENT. CONTRIBUTING FACTORS WERE: 1) EQUIPMENT HAD BEEN USED IN THE PAST HOWEVER, NOT THE CONFIGURATION, 2) PROPER COMMUNICATIONS BETWEEN THE PERSONNEL PERFORMING THE TASK WERE NOT MAINTAINED, AND 3) CONNECTION ON THE TEST EQUIPMENT WAS NOT PROPERLY LABELLED. THE TEST EQUIPMENT WAS REMOVED AND THE PLANT STABILIZED. EVENT HAS BEEN FORMALLY REVIEWED WITH THE PERSONNEL INVOLVED AND WILL BE FORMALLY REVIEWED WITH STATION PERSONNEL BY UPPER STATION MANAGEMENT STRESSING THE LESSONS LEARNED FROM THIS EVENT IN THE AREAS OF COMMUNICATIONS, WORK PRACTICES AND CONCURRENT ACTIVITIES. OTHER ACTION ITEMS RELATIVE TO THE STARTUP TESTING PROGRAM WILL BE REVIEWED TO ENSURE APPROPRIATE DISPOSITIONING. THE TEST EQUIPMENT WILL BE PROPERLY LABELLED. NO PREVIOUS OCCURRENCES.
457 | 4561988023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561988023R00.pdf | 1988-10-17 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 2 | P | WE | PO | 88 | POWER LEVEL - 000%. A SEVERE LIGHTNING STORM OCCURED AT THE PLANT SITE. UNIT 1 WAS SHUTDOWN. AT 1542 ON OCTOBER 17, 1988 VARIOUS UNIT 1 INDICATIONS REVEALED ERRATIC BEHAVIOR AND THE OVER PRESSURE DELTA TEMPERATURE (OP DELTA T) AND OVER TEMPERTURE DELTA TEMPERATURE (OT DELTA T) COINCIDENCE WAS MET FOR A REACTOR TRIP. ON UNIT 2 A REACTOR TRIP AND A LOCK UP OF THE COMPUTER MEMORY FOR THE REACTOR VESSEL LEVEL INDICATING SYSTEM (RVLIS) OCCURRED. THE ROOT CAUSE IS A VOLTAGE TRANSIENT INTO THE STATION GROUND SYSTEM FROM LIGHTNING STRIKES WHICH ACTUATED THE OVERVOLTAGE PROTECTION FOR THE RD POWER SUPPLIES, FOR BOTH UNITS, SUBSEQUENTLY RESULTING IN THE UNIT 2 REACTOR TRIP. RVLIS FAILED FROM AN OVERVOLTAGE CONDITION. ON UNIT 1, THE INSTRUMENT LOOP TRANSMITTERS WERE REPLACED AND ALL POWER SUPPLIES WERE RESET. THERE WERE NO EQUIPMENT FAILURES WITH THE OP DELTA T AND OT DELTA T INSTRUMENT CHANNELS. INVESTIGATION REVEALED THE STATION GROUNDING SCHEME IS ADEQUATE; HOWEVER, THE VENT STACK GROUNDING IS INCOMPLETE. THIS DID NOT CONTRIBUTE TO THE UNIT 2 TRIP. ADDITIONAL GROUNDING AND ADDITIONAL PROTECTIVE MEASURES FOR THE RD SYSTEM ARE BEING INVESTIGATED. THERE WERE NO PREVIOUS OCCURRENCES.
457 | 4571988029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988029R01.pdf | 1988-10-25 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Braidwood 2 | P | WE | PO | 89 | POWER LEVEL - 089%. IN ACCORDANCE WITH TECH SPECS, RCS INVENTORY BALANCE (RCSIB) WAS BEING PERFORMED ONCE EVERY EIGHT HOURS. BETWEEN 1322 AND 1500 ON 10/25/88 ALL FOUR CONDENSATE/CONDENSATE BOOSTER (CD/CB) PUMPS WERE ALTERNATELY SHUTDOWN FOR SUCTION STRAINER BACKWASHING. AT 1530 THE RCSIB WAS STARTED. IN AN EFFORT TO REDUCE FEEDWATER (FW) FLOW REQUIREMENTS, POWER WAS REDUCED WITH AN UNEXPECTED DECREASE IN CD HEADER PRESSURE. AT 1602, WITH STEAM GENERATOR LEVELS RAPIDLY DECREASING, THE REACTOR WAS MANUALLY TRIPPED. ALL PLANT SYSTEMS OPERATED AS DESIGNED. AT 1709 THE RCSIB WAS TERMINATED, BUT IT WAS COMPLETED WITHIN ACCEPTABLE CRITERIA UPON ESTABLISHMENT OF STABLE PLANT CONDITIONS. THE CAUSE OF STRAINER PLUGGING WAS DETERIORATED MATERIAL FROM A DENIM SERVICE COAT. THE MAIN CONDENSER AND ALL FOUR CD PUMP SUCTION STRAINERS AND HEADERS WERE CLEANED AND INSPECTED. THE 2C CB PUMP, THE 2A HEATER DRAIN PUMP AND THE 2B FW PUMP SUCTION STRAINERS WERE INSPECTED, ALONG WITH THE UPPER AND LOWER AREAS OF THE MAIN CONDENSER. THERE HAVE BEEN PREVIOUS OCCURRENCES OF PLUGGING OF THE CD PUMP SUCTION STRAINERS WHICH HAVE RESULTED IN A REACTOR TRIP, BUT THE PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE.
457 | 4571988031 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988031R00.pdf | 1988-11-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 2 | P | WE | PO | 88 | POWER LEVEL - 088%. AT 1307 ON NOVEMBER 5, 1988 DURING ROD CONTROL (RD) SYSTEM TROUBLESHOOTING, THE 2B MOTOR GENERATOR (M/G) SET'S IRV A RELAY (WHICH WAS OSCILLATING) WAS ISOLATED TO REPLACE A BLOWN FUSE. THIS RESULTED IN A LOSS OF EXCITATION TO THE 2B M/G SET AND THE 2A M/G SET WAS DEMANDED TO CARRY THE ENTIRE RD SYSTEM LOAD. THE 2A M/G SET'S OVERVOLTAGE RELAY (1H) WAS PICKED UP, RESULTING IN A TOTAL LOSS OF POWER TO THE RD SYSTEM. AT 1308 A REACTOR TRIP DUE TO A NEGATIVE RATE TRIP ON ALL NUCLEAR INSTRUMENTATION SYSTEM POWER RANGE CHANNELS OCCURRED. THE CAUSE OF THIS EVENT IS AN INCORRECT 1H RELAY SETTING DUE TO CONFLICTING INFORMATION IN THE TECHNICAL MANUAL. THE IMMEDIATE CORRECTIVE ACTIONS TAKEN WERE TO RESET THE 1H RELAY, REPLACE THE BLOWN FUSE, AND TO SIMULATE THE IDENTICAL CONDITIONS THAT LED TO THE TRIP (VERIFYING THAT THE INCORRECT RELAY SETTING WAS THE CAUSE). THE 1H RELAYS FOR EACH M/G SET OF BOTH UNITS HAVE BEEN VERIFIED AT THE CORRECT SETPOINTS. ALL FUTURE RELAY SETTINGS WILL BE GIVEN BY M/G OUTPUT VOLTAGE. TESTING OF THE M/G SET SETPOINTS WILL BE PERFORMED DURING EACH REFUELING OUTAGE. THERE HAVE BEEN PREVIOUS OCCURRENCES OF ROD CONTROL SYSTEM PERTURBATIONS THAT RESULTED IN A REACTOR TRIP. PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE TO THIS EVENT.
457 | 4561988025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561988025R00.pdf | 1988-11-15 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [9 empty] | X | [5 empty] | X | [24 empty] | X | Braidwood 2 | P | WE | PO | 79 | POWER LEVEL - 096%. AT 0904 ON NOVEMBER 15, 1988 LOW INSTRUMENT AIR PRESSURE WAS OBSERVED. THE RAPID DECREASE IN THE INSTRUMENT AIR HEADER PRESSURE CAUSED THE FEEDWATER REGULATING VALVES TO GO CLOSED. THIS DECREASED FLOW TO THE STEAM GENERATORS ON BOTH UNITS. AT 0908 BOTH UNITS WERE MANUALLY TRIPPED DUE TO DECREASING STEAM GENERATOR LEVELS. THE CAUSE OF THIS EVENT WAS INADEQUATE INSTALLATION OF A COUPLING IN THE INSTRUMENT AIR HEADER, LINE 0IA05B DURING CONSTRUCTION. THE INADEQUATE SOLDER JOINT WAS STRESSED BY CONTRACT PERSONNEL STANDING ON THE LINE. THE INSTRUMENT AIR HEADER WAS ISOLATED AND THE LINE REPAIRED BY REPLACING THE JOINT. THE LINE WAS INSPECTED UPSTREAM AND DOWNSTREAM OF THE BREAK FOR OTHER POSSIBLE LEAKS THAT MAY HAVE OCCURRED AS A RESULT OF THE BREAK. TWO OTHER JOINTS WERE REPAIRED FOR PINHOLE LEAKS. ADDITIONAL PIPE SUPPORTS WILL BE ADDED TO THE HEADER. A LETTER WAS ISSUED ON NOVEMBER 16, 1988 TO ALL SITE PERSONNEL REEMPHASIZING THE NEED FOR ALL PERSONNEL TO EXERCISE CARE IN WORKING AROUND ALL PLANT EQUIPMENT. THERE HAVE BEEN NO PREVIOUS OCCURRENCES OF A REACTOR TRIP AS A RESULT OF A LOSS OF INSTRUMENT AIR.
457 | 4571988028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571988028R00.pdf | 1988-11-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 6 | POWER LEVEL - 006%. PRIOR TO THE EVENT, FEEDWATER (FW) FLOW TO THE STEAM GENERATOR (S/G'S) WAS FROM THE FW TEMPERING LINES. WHILE CHANGING THE FLOWPATH TO THE FW PREHEATER BYPASS LINES, THE NUCLEAR STATION OPERATOR (NSO) OPENED THE FW BYPASS MANUAL ISOLATION VALVES AND THE FW SHUTOFF VALVES (2FW006A, B, C, & D). THIS RESULTED IN GREATER THAN REQUIRED FW FLOW WHICH FORCED THE NSO TO OPEN AND CLOSE THE PREHEATER BYPASS ISOLATION VALVES TO MAINTAIN S/G WATER LEVEL. AT 2006 ON NOVEMBER 17, 1988 THE REACTOR TRIPPED DUE TO A LOW-LOW LEVEL IN THE 2B S/G (AS A RESULT OF FEEDING IN RELATIVELY COLD WATER). THE ROOT CAUSE OF THE EVENT WAS A PROCEDURAL DEFICIENCY IN BWGP 100-2, PLANT STARTUP, THAT REQUIRED THE 2FW006A-D VALVES TO BE OPENED PRIOR TO 3% POWER. S/G LEVELS WERE RESTORED TO THEIR NORMAL OPERATING BAND. THE PNEUMATIC CONVERTERS AND POSITIONERS OF THE FW REGULATING BYPASS VALVES WERE ALSO RECALIBRATED. TEMPORARY CHANGES TO APPLICABLE PROCEDURES WERE ISSUED TO KEEP THE 2FW006A-D VALVES CLOSED UNTIL TURBINE OPERATION. THERE HAVE BEEN PREVIOUS OCCURRENCES OF AN ENGINEERED SAFETY FEATURES ACTUATION AS A RESULT OF S/G LEVEL PERTURBATIONS. PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE TO THIS EVENT.
457 | 4571989002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571989002R00.pdf | 1989-05-11 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 67 | POWER LEVEL - 067%. AT 0447 ON 5/11/89, BRAIDWOOD 345 KV BUS 11 RECEIVED A TRIP SIGNAL FROM TRANSMISSION SUB STATION (TSS) 177. THE A PHASE OF BUS TIE (BTCB) 10-11 OPENED MORE SLOWLY THAN THE 'B' AND 'C' PHASES. A LOCAL BREAKER BACKUP (LBB) SIGNAL WAS INITIATED. THIS SENT A TRIP SIGNAL TO UNIT 2 MAIN GENERATOR LOCKOUT RELAYS. THIS CAUSED A REACTOR TRIP. THE 2C STEAM GENERATOR (SG) LEVEL SPIKED RESULTING IN A FEEDWATER ISOLATION. THE AUX. FEEDWATER PUMPS (AF) AUTO STARTED. STABLE PLANT CONDITIONS WERE IMMEDIATELY ESTABLISHED. AT 0540 THE FLOW CONTROL VALVE FROM THE 2A AF PUMP TO THE 2A SG WOULD NOT GO FULL OPEN. THE INSTRUMENT AIR TO THE VALVE WAS ISOLATED AND IT FAILED OPEN. FLOW WAS CONTROLLED BY THROTTLING THE MOTOR OPERATED ISOLATION VALVE. THE ROOT CAUSE OF THIS EVENT WAS A DEFECTIVE TRIP COIL FOR THE A PHASE OF BTCB 10-11. THE CAUSE OF THE LEVEL SPIKE ON THE 2C SG WAS A PRESSURE SPIKE FROM SUDDEN LOSS OF STEAM FLOW. THE CAUSE OF THE AF VALVE FAILURE WAS DEFECTIVE CONTROL CARD. THE CAUSE OF THE TRIP SIGNAL FROM TSS 177 WAS NOISE ON THE MICROWAVE CHANNELS. THE A PHASE TRIP COIL HAS BEEN REPAIRED. THE MICROWAVE UNIT AT TSS 177 WILL BE REPLACED. THERE WAS A PREVIOUS OCCURRENCE OF A LOSS OF A SWITCHYARD BUS DUE TO AN LBB INITIATION. PREVIOUS CORRECTIVE ACTIONS WERE NOT APPLICABLE TO THIS EVENT.
457 | 4561989006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4561989006R00.pdf | 1989-07-18 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 2 | P | WE | PO | 84 | POWER LEVEL - 086%. AT 2020 AND 2026 ON 7/18/89 THE STATION EXPERIENCED LIGHTNING INDUCED VOLTAGE TRANSIENTS CAUSING MULTIPLE ROD DRIVE OVERVOLTAGE PROTECTION DEVICES TO ACTUATE ON UNIT 1 AND 2, RESPECTIVELY. ON UNIT 1 TEN OUT OF TEN OVERVOLTAGE PROTECTORS ACTUATED. ON UNIT 2 SEVEN OUT OF TEN OVERVOLTAGE PROTECTORS ACTUATED. THIS REMOVED POWER TO VARIOUS ROD DRIVE CONTROL CARDS AND ALLOWED NUMEROUS CONTROL RODS TO DROP. BOTH REACTORS TRIPPED DUE TO NEGATIVE RATE TRIP ON THE POWER RANGE. IMMEDIATE CORRECTIVE ACTIONS WERE TO STABILIZE THE PLANT, RESET THE OVERVOLTAGE PROTECTORS, AND VERIFY ROD CONTROL OPERABILITY. THE EXACT LOCATION OF THE LIGHTNING STRIKES ARE UNKNOWN. THE ROOT CAUSE IS INADEQUATE PROTECTION AND ISOLATION OF THE ROD CONTROL SYSTEM FROM LIGHTNING INDUCED TRANSIENTS. THE IMMEDIATE CORRECTIVE ACTIONS WERE TO RESET THE OVERVOLTAGE PROTECTORS. NO DAMAGE OCCURRED TO THE ROD CONTROL SYSTEM. THERE HAS BEEN ONE PREVIOUS OCCURRENCE OF A LIGHTNING INDUCED VOLTAGE TRANSIENT RESULTING IN A REACTOR TRIP. CORRECTIVE ACTIONS WERE IMPLEMENTED ADDRESSING BOTH ROOT AND CONTRIBUTING CAUSES FOR THE ABOVE EVENT. THE PREVIOUS CORRECTIVE ACTIONS ARE NOT APPLICABLE TO THIS EVENT.
457 | 4571989004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571989004R00.pdf | 1989-09-07 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 2 | P | WE | PO | 90 | POWER LEVEL - 090%. AT APPROXIMATELY 2000 HOURS, 9/7/89 A SEVERE THUNDERSTORM WAS IN THE AREA OF BRAIDWOOD STATION. A VIDEO RECORDER HAD BEEN SET UP TO MONITOR THE EFFECTS OF ATMOSPHERIC EVENTS. FROM 2029 TO 2036 SIXTY-THREE LIGHTNING FLASHES WERE RECORDED BY THE CAMERA. FOUR OF THESE LIGHTNING STRIKES HIT STATION STRUCTURES. THE UNIT 2 AUX. BLDG. VENT STACK WAS STRUCK TWICE. THE BRAIDWOOD STATION SWITCHYARD WAS STRUCK. AT 2031:44 THE UNIT 2 CONTAINMENT WAS STRUCK. AT 2032 ALL TEN ROD CONTROL SYSTEM (RD) POWER CABINET OVERVOLTAGE PROTECTION DEVICES ACTUATED. THIS CAUSED THE STATIONARY GRIPPER COILS OF THE CONTROL RODS TO DEENERGIZE AND THE RODS DROPPED INTO THE CORE. THE RAPID FLUX DECREASE WAS SENSED BY THE NUCLEAR INSTRUMENTATION WHICH GENERATED A POWER RANGE FLUXRATE HIGH REACTOR TRIP. THE REACTOR TRIP BREAKERS OPENED, THE TURBINE TRIPPED, AND FEEDWATER ISOLATION OCCURRED. THE SHRINK EFFECT ON STEAM GENERATOR LEVEL INSTRUMENTATION RESULTED IN AN AUTO START OF THE AUXILIARY FEEDWATER PUMPS ON LOW WATER LEVEL. THE CAUSE OF THIS EVENT WAS A LIGHTNING INDUCED VOLTAGE TRANSIENT. THE RD OVERVOLTAGE PROTECTION DEVICES WERE RESET. THE RD SYSTEM WAS TESTED. A TIME DELAY HAS BEEN ADDED TO THE OVERVOLTAGE PROTECTION DEVICES. RECOMMENDATIONS ON ADDITIONAL CORRECTIVE MEASURES ARE BEING EVALUATED. THERE HAVE BEEN TWO PREVIOUS OCCURRENCES. PREVIOUS CORRECTIVE ACTIONS WERE NOT APPLICABLE.
457 | 4571990010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571990010R00.pdf | 1990-06-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 15 | A unit start up was in progress. Feedwater (FW) flow was being controlled in automatic by the Bypass FW Regulating valves (BFRV). Steamline Header Pressure was being controlled in automatic by the Steam DLWs. At 0030 on June 9, 1990 a Reactor Operator (RO), who was monitoring the FW panel, observed that indicated level on the 20 Steam Generator (SG) had decreased to 35%. This was below the set point of 50%. The RO placed the controller in manual and increased the output to raise SG level. 2B SG level continued to decrease from the 'shrink' effect of the cold FW. The Supervisor (SRO) directed the RO who was monitoring Reactor Control Panel, to withdraw control rods to increase temperature and "Swell" the level. SG level increased from an initial value of 20% to 24%. At 0039 the effects of the increased heat input caused steamline pressure to increase which caused the Steam Dump Valves to cycle. This created a level perturbation which caused the level in the 2B SG to decrease below the Reactor Trip Set point of 17% and a Reactor Trip occurred. The cause of the event was a malfunctioning BFRV which would stick during operation in the lower third of valve travel. The valve packing was loosened and valve travel was smooth and acceptable, Operator training will be provided. Previous corrective actions are not applicable.
457 | 4571991003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571991003R00.pdf | 1991-08-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 2 | P | WE | PO | 88 | Unit 2 was operating at 88% reactor power in a coast down mode at the end of core life. On August 1, 1991 at 2354 the unit operator attempted to move the control rods in Bank D to control Reactor Coolant System temperature. A Rod Drive (RD) System failure released numerous control rods and allowed them to fall into the core. A reactor trip signal was generated because the Nuclear Instrumentation (NR) System detected a rapid power decrease. Control Room personnel immediately recognized and responded to the reactor trip. The unit was stabilized with normal post-trip response conditions. During RD troubleshooting, the logic cabinet was analyzed to determine the amount of electric current being supplied to the stationary and movable grippers. The 2BD slave cycler was intermittently giving erratic current demand orders. The rods dropped because the stationary gripper was unable to hold the rods before the moving gripper unlatched. The cause of the 2BD slave cycler failure was a defective binary counter. The counter is required to properly sequence the energization/de-energization of the movable and stationary grippers during rod notion. The 2BD slave cycler binary counter circuit card was replaced. The logic cabinet slave cycler circuits were tested and analyzed for proper operation. A complete functional check of the RD system identified no further deficiencys. To improve RD system performance, a long-term corrective action plan was developed. An evaluation of the effects of high temperatures on the RD system is in progress.
457 | 4571991006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571991006R00.pdf | 1991-12-01 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 50 | At 1738 on December 1, 1991 a Generator Neutral Ground Overcurrent backup protective relay actuated and tripped the Unit 2 Main Generator. A turbine and reactor trip followed as designed. Operators performed applicable steps of the reactor trip response procedures and stablized the plant. The generator trip was caused by the neutral ground backup relay. The design purpose of this relay is to actuate when an unbalanced voltage condition exists between the three phases of the generator. An oscillograph, used to record voltage applied across the neutral resistor, indicated that no fault had existed on the generator. Additionally, a megger reading of the generator confirmed that no internal fault existed. With no generator fault, the cause of the trip was in the potential transformer circuitry. Upon completion of troubleshooting, the cause could not be determined. Precautionary measures were taken to prevent an intermittent potential fuse failure from causing another generator trip. <br /><br /> The potential transformer fuses were replaced and the suspect circuitry will be monitored.
457 | 4571992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571992001R00.pdf | 1992-02-25 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 98 | On February 25, 1992 Unit 2 had been placed on Economic Generation Control (EGC). At 1233, a Contact Closure Interlock (CCI) alarm was received on the turbine-generator control panel. Operational Analysis Department (OAD) determined that the CCI alarm was from EGC. The unit Nuclear Station Operator (NSO) placed turbine control to the "Manual" mode. The CCI alarm was then reset and the NSO noticed that both lenses of the Transfer Throttle Valve/Governor Valve (TV/GV) lite were illuminated. OAD then reset the computer used to operate the turbine. At 1446, turbine control was returned to "Auto." The governor valves immediately started opening. Simultaneously, the throttle valves began to close. When all 4 throttle valves reached the closed position, a turbine trip signal was generated. Since reactor power was above the P-8 setpoint (30%), a reactor trip also occurred. The cause was a defective circuit in the turbine control system. Failure of this circuit caused the "Auto" control section of the computer to reset the valve control from governor valve control to throttle valve control. The defective circuit board was replaced. The system was tested and returned to service.
457 | 4571992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571992002R00.pdf | 1992-03-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 98 | On March 15, 1992 a Nuclear Station Operator (NSO) (licensed) was taking Valve 2MS004G Out-of-Service (OOS). The OOS required eLectrical isolation. The NSO exited the ControL Room with 6 OOS cards to remove 6 fuses. There were two fuses that required removal in control cabinet panel 2PA28J. OOS card #10 was for fuse FU-51 in 2PA28J, and OOS card #11 was for fuse FU-52 in 2PA28J. While looking at card #10 and #11, the NSO thought the fuses to be removed were fuses 10 and 11. The NSO first removed fuse 10 arid de-energized the water hammer prevention reLays for Low 28 Steam Generator (S/G) leveL. Shortly thereafter, the NSO removed fuse 11 and de-energized the water hammer prevention protection relays for Low 2C S/G pressure. The removal of these fuses caused a feedwater isolation for the 2B and 2C S/G's. After realizing that feedwater would not be reestablished, operators in the Control Room decided to manually trip the reactor. As the Unit 2 NSO was proceeding to the manual reactor trip control switch, an automatic reactor trip occurred at 0620 because 2C S/G level was at the low-low level setpoint of 17%. The cause of the event was personnel error by the NSO. The NSO transposed the OOS card number for the fuse number and removed the wrong fuses.
457 | 4571992006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571992006R00.pdf | 1992-09-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 99 | On September 10, 1992 at 2126 hours CDST, Braidwood Unit 2 Control Room received a Feed Pump Turbine Exhaust Vacuum Low annunciator. Three Control Room Operators all noted dual indication on valve 2ES095A, which is the Turbine Driven Feedwater Pump Exhaust Valve. Within approximately twenty seconds, the 2B Turbine Driven Feedwater Pump tripped. The U-2 NSO responded immediately and manually initiated an automatic turbine runback. Approximately one minute later, due to the decreasing secondary side level on the steam generators, the reactor tripped on Low-Low Steam Generator Level on the 2A Steam Generator. All reactor protection systems responded as designed and all control rods fully inserted into the core. Both Auxiliary Feedwater pumps started as expected and restored all Steam Generator levels to the proper level. Normal Feedwater was reestablished utilizing the Startup Feedwater Pump at 2206 hours.<br /><br /> The event was caused by a personnel error by a contractor, who manipulated the valve on the operating unit instead of the outage unit that he was working on. There have been no previous occurrences of this type at Braidwood Station.
457 | 4571992007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571992007R00.pdf | 1992-11-14 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On November 14, 1991 Unit 2 was in Mode 1 at 100% power. At 18:52 an oscillograph operation alarm came in followed by a main generator neutral ground back-up relay trip which subsequently tripped the turbine resulting in a reactor trip. The unit trip was the result of a failed potential transformer secondary fuse. The failed fuse was analyzed. The analysis indicated mechanical failure of the fuse. The potential transformer secondary fuses were replaced with fuses less susceptible to damage. Engineering approval was also received for the fuse replacement. As a conservative measure, all primary potential transformer fuses were replaced to address the possibility of intermittent fuse actuation. A megger was also performed on the generator and the values were found to be acceptable. Additionally, the fuse contacts on the potential transformers were cleaned and adjusted. There has been a previous similar occurrence.
457 | 4571993007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571993007R00.pdf | 1993-10-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 100 | Prior to the event, a Nozzle Flow High/Low alarm occurred on the 2D S/G, all conditions appeared normal. Approximately 30 seconds later the Nozzle Flow High/Low alarmed again, followed immediately by a Steam/Feed Flow Mismatch alarm. It was then noted that turbine load had increased by approximately 50 MWe. Digital Electro-Hydraulic Control was taken to manual in an attempt to stabilize the plant. At 0138 on 10/03/93, the Unit tripped due to LO-2 level in the 2D S/G. The cause of this event was a combination of Equipment Failure and Management/Quality Assurance Deficiency. The O-rings in the valve positioner hardened due to normal aging in a moderate heat environment. The corrective actions are: all four positioners on the Unit 2 FWRVs were replaced, A Preventative Maintenance program will be established for the Unit 2 FWRV positioner internal components every refueling outage. A routine elastomer changeout on valve positioners will be investigated. A routine instrument air filter cleaning/changeout program will also be investigated. The valve positioners on the 2FW046A through D valves will be inspected during the next Unit 2 refuel outage. There has been a reportable event involving a FWRV at Braidwood. A different valve and failure mode was involved, therefore there is no adverse trend.
457 | 4571994003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571994003R00.pdf | 1994-04-05 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | At 1539 on April 5,1994 a Reactor Trip was received. The 2E Main Power Transformer (MPT) had a sudden pressure and a differential current trip which caused a turbine trip and a subsequent reactor trip. The cause of this reactor trip was Equipment Failure. A review of the oscillograph traces indicated a high side B phase fault on the 2E Main Power Transformer. The fault was initiated at the transformer and damage was extensive to the 2E MPT. A detailed investigation for collateral damage was performed which covered the following items: A generator crawlthru inspection; the 2W MPT and both UAT'S were electrically tested; and oil samples on the 2W MPT and both UAT'S were taken. The results of all of these activities indicated that there was no additional damage to any equipment beyond the 2E MPT. The 2E MPT will be replaced with a spare transformer. Additionally, instrumentation associated with the transformer will be calibrated prior to operation. Finally, a Company task force has been developed to investigate this recent failure. There have been previous similar occurrences where electrical system problems have resulted in a reactor trip. The root cause(s) and corrective actions of the previous similar occurrences do not apply to this event. There is no adverse trend.
457 | 4571994005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571994005R00.pdf | 1994-08-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 100 | Braidwood Unit 2 tripped due to a low low level in the 2A Steam Generator. The cause of this event was Equipment Failure; an o-ring in the Feedwater Regulating Valve positioner failed. The entire positioner was replaced, tested, and placed into service.
457 | 4571998001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571998001R00.pdf | 1998-01-26 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | At 21:53 on 1/26/98, the Unit 2 Reactor tripped as a result of a 2A Steam Generator Low Low Level. Operations personnel stabilized the Unit in Mode 3 in accordance with approved Emergency Operating Procedures and initiated a plant cooldown. All Engineered Safety Features (ESF) functioned properly and there were no safety consequences as a result of this event.The Reactor Trip was caused by a misconfigured electronic circuit card in the Unit 2 Turbine Digital Electro-Hydraulic Control (DEHC) system. This card was installed during maintenance work in progress at the time of the trip. The misconfigured card caused an inappropriate DEHC Overspeed Protection Circuit (OPC) actuation signal that closed the turbine governor and intercept valves resulting in the Steam Generator Low Low Level and the Reactor trip. The Root Cause Investigation Team concluded that there was an inadequate process to adapt the generic replacement DEHC card and to ensure that it had the correct configuration prior to installation. Contributing causes included inadequate work processes used in the DEHC maintenance activities, limited available DEHC design information, and the failure to characterize the work as a high risk evolution. Corrective actions include process changes in the control of work for the affected department, development of methodologies to configure and test DEHC cards, and planned improvements in the quality and control of the DEHC design information.This event is being reported pursuant to 10CFR50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF).
457 | 4571999001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571999001R00.pdf | 1999-04-14 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 87 | On 4/14/99 at 0433, the Braidwood Station Unit 2 reactor tripped due to a main generator and turbine trip. The generator trip was due to a spurious Generator Stator Ground Relay, GIX-104 relay, actuation. There was no identified personnel error or inappropriate action. The Digital Fault Recorder (DFR) records showed no evidence of a generator ground. The DFR showed a higher than normal third harmonic voltage before and after the reactor trip. The Sequence of Events Recorder (SER) showed two alarms, GIX-104 relay and voltage regulator, prior to the generator trip. A failed Minimum Excitation Limiter (MEL) card on the voltage regulator caused the card output to fail high raising the excitation of the generator. The plant equipment responded as designed, with the opening of the generator output breakers, tripping of the turbine, tripping of the reactor, and initiation of Auxiliary Feedwater.On 4/15/99 during startup following these repairs, a Rod Control Urgent Failure alarm was received. This resulted in the Control Rod Drive System being incapable of control rod movement. The control rods remained trippable. During the repair efforts control banks C and D became misaligned such that the overlap limits were not met. Actions of Limiting Conditions of Operation (LCO) 3.1.6, "Control Bank Insertion Limits" , were entered due to the failure to meet the required overlap specified in the Core Operating Limits Report. Actions of LCO 3.1.6 requires verification of shutdown margin within 1 hour and that the overlap limits be met otherwise the unit must be placed in mode 2 with Keff< 1.0 within the next 6 hours. A Unit 2 shutdown was initiated to complete repairs due to the Control Rod Drive Systems, inability to move control rods. The shutdown was accomplished by opening the reactor trip breakers. The cause of the Control Rod Drive System failure is attributed to several card failures, which were subsequently identified and replaced. Following repairs to the Control Rod Drive System, the unit was returned to operation.This event is being reported pursuant to 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(iv).
457 | 4571999003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4571999003R01.pdf | 1999-05-19 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 2 | P | WE | SU | 3 | At 1917 on 05/19/99, spurious spiking of indication on the Intermediate Range Neutron Flux Channel N36 resulted in a Unit 2 reactor trip. The unit was in reactor startup following a refueling outage when the Reactor Coolant System (RCS) was being diluted to increase reactor power. At approximately 3% reactor power, as indicated by the four Power Range Nuclear Instruments, erratic behavior was noted on the startup rate meter for Intermediate Range Neutron Flux Channel N36. The Main Control Room (MCR) personnel were investigating the erratic behavior when the reactor trip signal occurred. The MCR personnel stabilized the reactor in a shutdown condition using appropriate emergency procedures. All systems functioned as designed. All appropriate notifications were made.
457 | 4572000002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572000002R00.pdf | 2000-04-15 | QR3 | Reactivity Control Imbalance | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On 4/15/2000 at 1714 hours, Unit 2 was operating at 99.9 percent power when it experienced a trip on Power Range Neutron Flux High Negative Rate. Following the trip, a low Steam Generator (SG) level Engineered Safety Features (ESF) actuation signal started Auxiliary Feedwater and a high SG level ESF actuation P-14 signal was processed. The rapid power decrease was traced to the failed Stationary Gripper fuse and blown fuse indicator (telltale) for Control Rod P10 causing the rod drop. Troubleshooting verified that circuits were not shorted and had not caused an overcurrent condition. The blown fuse and telltale were removed for analysis and replacements installed. Unit start-up commenced on 4/16/2000 at 0414 hours, but was aborted due to Digital Rod Position Indication problems. The cause of the trip was the opening of fuse FU15 and telltale which led to the rod drop and subsequent high neutron flux negative rate. The fuse was blown due to an indeterminate overcurrent condition believed to be an isolated failure. Analysis revealed that the fuse had apparently failed prior to the trip and that the telltale had been carrying the load current. Thermography scans will be performed as predictive maintenance to look for "hot" telltales indicative of such fuse failures and the circuits will be reviewed to verify the adequacy of design. Because the negative rate trip may not be necessary, possible elimination of this trip will be reviewed. This event is being reported pursuant to 10 CFR 50.73 (a) (2)(iv).
457 | 4572001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572001001R00.pdf | 2001-05-19 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Braidwood 2 | P | WE | PO | 100 | At 0406 on 05/19/01, Braidwood Unit 2 tripped due to a loss of loop 2C reactor coolant flow while operating at 100 percent power. The 2C reactor coolant pump tripped when a nonlicensed operator opened the incorrect system auxiliary transformer (SAT) feed potential transformer fuse door on 6.9kV Bus 258 during preparations for a Unit 2 SAT outage. The loss of the 2C reactor coolant pump resulted in an automatic reactor trip due to low flow in the 2C loop.Due to the existing electrical lineup in support of the SAT outage, power to the 6.9kV buses and non-ESF 4kV buses was lost when the turbine/generator tripped offline. This resulted in a loss of all reactor coolant pumps, circulating water pumps, the main feedwater pumps and the condensate/condensate booster pumps. The reactor coolant system was maintained on natural circulation cooling with the secondary heat sink supplied by the steam generator power operated relief valves and auxiliary feedwater supplying the steam generators.The root causes for the event were failure to perform concurrent verification to identify the correct SAT primary potential transformer fuse door and improper command and control to ensure critical tasks were performed correctly. The corrective actions are counseling and discipline of the responsible individuals and development and implementation of a policy to strengthen command and control standards for execution of critical activities in the plant.
457 | 4572003004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572003004R00.pdf | 2003-12-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 100 | At 0336 on 12/03/03, the Unit 2 reactor tripped on 2D Steam Generator low-low water level due to the cascading trip of the 2C and 2B turbine driven feedwater pumps during 2C feedwater pump testing. While testing the 2C feedwater pump stop valves, the high pressure stop valve did not reopen as expected during the test due to a piece of age degraded tie wrap lodged in the relay contacts. The 2C feedwater pump subsequently tripped. The suspected reason for the trip of the 2C feedwater pump is believed to be a simultaneous closed signal from the low pressure and high pressure stop valves. During the start of the 2A motor driven feedwater pump, the 2B feedwater pump tripped on overspeed due to high flow demand when the 2C feedwater pump tripped and failure of the 2B feedwater pump speed feedback control circuit to limit the pump speed below the mechanical overspeed trip setpoint. The 2A motor driven feedwater pump could not provide sufficient flow to maintain the Unit 2 Steam Generator water levels above the automatic reactor trip setpoint.This event is the result of equipment failures and not due to human performance error. The significance of this event is an automatic Reactor Protection System actuation when the reactor tripped on low-low Steam Generator water level and subsequent Engineered Safety Feature actuation when the auxiliary feedwater pumps started.This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A).
457 | 4572004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572004002R00.pdf | 2004-12-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Braidwood 2 | P | WE | PO | 100 | Braidwood Unit 2 experienced a reactor trip on December 22, 2004 at 1308 due to a low-low level in the 2C Steam Generator (SG). The reactor trip was initiated by the failure of a circuit card in the 2C steam flow instrumentation loop. The steam flow signal from this card feeds into the 2C SG level control loop. The loss of the steam flow signal to the 2C SG level control loop resulted in two automatic actions; closure of the 2C SG feedwater regulating valve in response to a steam flow-feedwater flow mismatch, and a speed reduction of the two turbine-driven feedwater pumps to reduce feedwater header pressure in accordance with a programmed feedwater header pressure versus total steam flow control response. Operator actions were unable to recover SG level prior to the automatic reactor trip. The root cause was determined to be inadequate understanding and incomplete evaluation of changes made to the Unit 2 feedwater system control settings for the feedwater regulating valves and the feedwater pump speed controller. The corrective actions to prevent recurrence include determining and setting the proper values for the feedwater regulating valve controller settings and main feed pump speed controller response for optimum plant response, and providing licensed operators the response characteristics of both Braidwood Units to feedwater type transients initiated by circuit card failures.There were no safety consequences impacting plant or public safety as a result of this event. The reactor trip system responded as designed to the low SG level condition and shut down the reactor at the required setpoint for steam generator low-low level. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
457 | 4572005002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572005002R00.pdf | 2005-03-28 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On March 28, 2005, at 1246, the Unit 2 main generator tripped as a result of a fault on the main generator "C" phase (T-3) bushing, followed by a turbine trip and reactor trip. Operator response to the trip was proper and all safety equipment operated as expected, with minor exceptions. The root cause of the Unit 2 trip was determined to be the lack of technical rigor applied during the redesign of the bushing in the 2000 time period. Contributing to this event was the unavailability of spare parts and lack of Original Equipment Manufacturer expertise due to the sale of the bushing product line. Corrective actions include implementation of a Technical Human Performance Program, evaluating the addition of the demography windows to allow online monitoring of the bushings, and formalizing of the corporate high voltage bushing strategy. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
457 | 4572007001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572007001R00.pdf | 2007-08-23 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On August 23, 2007, at 1530 hours, Braidwood Unit 2 reactor manually tripped from 100% power following the automatic trips of the 2A and 2B circulating water pumps due to sudden spiking of the inlet traveling screen water level differential. Operator response to the trip was appropriate and all safety related systems, structures and components operated normally during this event. The root cause of the Unit 2 trip was that the traveling screen instrumentation experienced a sudden and false high differential level indication brought on by a momentary plugging of the upstream bubbler tube. This momentary plugging was caused by agitated debris during a period of high winds. The corrective action to prevent recurrence will be to install a time delay to preclude trips of the circulating water pumps due to sudden and false high differential level indication. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System (Reactor Trip) and the Auxiliary Feedwater System.
457 | 4572008002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572008002R00.pdf | 2008-12-27 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On December 27, 2008, at 14:18 hours, Braidwood Unit 2 Unit Aux Transformer 241-1 sudden pressure relay actuated causing a Unit 2 main generator trip, which resulted in a Unit 2 main turbine trip and subsequent Unit 2 reactor trip. Concurrent with the reactor trip, the 2C heater drain pump (HD) tripped on phase "A" and "C" phase over current.Operator response to the trip was proper and all safety related systems, structures and components operated normally during this event. The auxiliary feedwater system actuated, as expected, to maintain steam generator levels.The investigation of this event determined the initiating event to the reactor trip was a phase-to-phase motor fault at the 2C HD pump motor terminal housing box, which caused a trip of the 2C HD pump on phase over current. Inspection of the motor lead box found the motor lead from one phase ("A" phase) in contact with the bus bar for another phase ("C" phase) due to excessive motor lead length. The root cause of the HD pump trip was determined to be that the procedure guidance for trimming the motor leads was deficient in that a lack of adequate information was provided for the desired motor lead length. The corrective action to prevent recurrence is to revise the existing procedure to provide clear direction on the desired length of power cables.There were no actual safety consequences impacting plant or public safety as a result of this event.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
457 | 4572009001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572009001R00.pdf | 2009-04-24 | QR8 | Spurious Reactor Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On April 24, 2009, a Technical Specification calibration of the 2B pressurizer pressure loop was being performed. Insupport of this surveillance, the 2B over temperature delta temperature (OTDT) bistable was placed in the trippedcondition.At 1141 hours, while the 2B pressurizer pressure channel calibration was in progress, a momentary/spurious signal spikeoccurred on the 2D OTDT channel. With the 2B OTDT bistable already placed in the tripped condition, the spike on the2D OTDT channel satisfied the 2 of 4 trip coincidence, and initiated an automatic reactor trip.The investigation for this event found no issues with human performance, equipment failure, or plant activities that couldhave caused the signal spike. The root cause of the Unit 2 reactor trip is determined to be the design of the Reactor TripSystem and Engineered Safety Features Actuation System, which places a loop in a tripped condition for testing,increases vulnerability during testing conditions.The corrective action to prevent recurrence is to pursue a modification which bypasses a tested channel rather thanplacing it in the tripped state during surveillances.There were no actual safety consequences impacting plant or public safety as a result of this event.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system(reactor trip) and the auxiliary feedwater system.
457 | 4572009002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572009002R00.pdf | 2009-07-30 | QR2 | Loss of Primary Flow (RPS Trip) PWR |  | X | [13 empty] | X | [29 empty] | Braidwood 2 | P | WE | PO | 100 | On July 30, 2009 at 20:59 hours, Unit 2 experienced an automatic reactor trip from full power. The 2C reactor coolant pump (RCP) tripped on overcurrent following the initial loss of system auxiliary transformer (SAT) 242-1 on a sudden pressure relay actuation and subsequent bus 258 transfer. This resulted in an automatic reactor trip from full power due to less than four RCPs in operation above 30% power.The root causes of the Unit 2 reactor trip were determined to be: 1) the 2C RCP breaker tripped inappropriately due to a combination of an overcurrent trip setpoint time delay shorter than minimum acceptable, and an overcurrent drop out reset value too low; and 2) the procedure for the calibration of overcurrent protective relays does not contain guidance to take an as-found reading / calibration and functional check of the overcurrent drop out reset value.The corrective actions include: 1) perform a functional check, and calibration of the overcurrent protective relays for the 2C RCP, and on pumps with the same overcurrent protective relay; and 2) revise the procedure for the calibration of overcurrent protective relays to include procedure steps for functional check and calibration, as required, for the high drop out instantaneous values associated with overcurrent time delay relays.There were no actual safety consequences impacting plant or public safety as a result of this event.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B) including any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical, actuation of the emergency AC electrical power system, and actuation of the PWR auxiliary feedwater system.
457 | 4572010003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4572010003R00.pdf | 2010-08-16 | QR5 | Turbine Trip | [45 empty] | Braidwood 2 | P | WE | PO | 100 | On August 16, 2010 at 0206, Unit 2 main generator received generator lockout relay trips, which caused the Unit 2 reactor to trip on a turbine trip above 30 percent power. Following the reactor trip, the auxiliary feedwater pumps automatically started on low-low steam generator water levels.The root cause of the Unit 2 reactor trip was determined to be an inadequate damper inspection acceptance criteria and preventive maintenance (PM) frequency that did not account for the more turbulent flow characteristics that the crossover damper is subjected to. Corrective actions to prevent recurrence include revising the PM schedules to ensure the crossover damper assembly is inspected and/or replaced prior to failure, and revising the maintenance procedure for isophase bus duct PM to include additional inspection criteria for the crossover damper assembly. There were no actual safety consequences impacting plant or public safety as a result of the event.This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
458 | 4581987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581987002R00.pdf | 1987-01-12 | QG9 | Primary System Leak | [45 empty] | River Bend | B | GE | PO | 17 | POWER LEVEL - 017%. AT 1532 ON 1/12/87 WITH THE UNIT AT FULL POWER, A REACTOR SHUTDOWN WAS INITIATED AS REQUIRED BY TECHNICAL SPECIFICATION 3.4.3.2.B ACTION STATEMENT FOR UNIDENTIFIED DRYWELL LEAKAGE EXCEEDING 5 GPM. THE UNIDENTIFIED LEAKAGE BEGAN INCREASING AT APPROXIMATELY 0000 ON 1/12/87. AT 0308 AN 'UNUSUAL EVENT' WAS DECLARED, AND OPERATIONS BEGAN REACTOR SHUTDOWN PROCEDURES AT 0347 IN COMPLIANCE WITH TECHNICAL SPECIFICATION 3.4.3.2.B. THEREAFTER, THE LEAKAGE REMAINED IN THE 8.0 TO 10.5 GPM RANGE. POWER WAS REDUCED TO 17 PERCENT PRIOR TO INITIATING A MANUAL SCRAM PER APPROVED SHUTDOWN PROCEDURES TO COMPLY WITH THE TECHNICAL SPECIFICATION ACTION STATEMENT. THE UNIDENTIFIED DRYWELL LEAK RATE INCREASING TO GREATER THAN 5 GPM WAS CAUSED BY PACKING LEAKS ON SEVERAL VALVES WITH THE 'B' RESIDUAL HEAT REMOVAL (RHR) TESTABLE INJECTION CHECK VALVE (1E12*AOVF041B) BEING THE PRIMARY CONTRIBUTOR. PACKING ON ALL VALVES RESPONSIBLE FOR CONTRIBUTING TO THE EXCESSIVE LEAKAGE WAS SUBSEQUENTLY REPLACED OR SEALED WITH AN APPROVED SEALING COMPOUND. THE VALVES WERE THEN INSPECTED FOR LEAKAGE WHEN THE PLANT WAS RETURNED TO RATED PRESSURE. LITTLE OR NO LEAKAGE WAS OBSERVED. THE PLANT HAS CONTINUED TO OPERATE TO THIS DATE WITH THE UNIDENTIFIED DRYWELL LEAKAGE REMAINING WELL BELOW THE LIMIT ALLOWED BY THE TECHNICAL SPECIFICATION. AT NO TIME WAS THE HEALTH AND SAFETY OF THE PUBLIC AFFECTED AS A RESULT OF THIS EVENT.
458 | 4581987003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581987003R00.pdf | 1987-01-16 | QP5 | Excessive Feedwater Flow | [45 empty] | River Bend | B | GE | PO | 14 | POWER LEVEL - 014%. AT 1602 ON 1/16/87 WITH THE UNIT AT 14% POWER, A REACTOR SCRAM OCCURRED DUE TO HIGH REACTOR WATER LEVEL (LEVEL 8) CAUSED BY A FEEDWATER LEVEL TRANSIENT WHILE PLACING THE 'A' FEEDWATER REGULATING VALVE INTO SERVICE. THE CAUSE OF THE FEEDWATER LEVEL TRANSIENT WAS DUE TO THE OPERATOR FAILING TO REALIZE THE REGULATING VALVE CONTROL SIGNAL WAS 'LOCKED UP' WITH THE VALVE AT APPROXIMATELY 47% OPEN. WHEN THE FEEDWATER REGULATING VALVE WAS UNISOLATED, REACTOR WATER LEVEL INCREASED RAPIDLY TO THE LEVEL 8 REACTOR SCRAM SETPOINT. LEVEL WAS RETURNED TO NORMAL AFTER THE SCRAM WITHOUT THE USE OF SAFETY SYSTEMS AND FEEDWATER WAS REESTABLISHED TO MAINTAIN LEVEL. AND SAFETY OF THE PUBLIC WERE NOT AFFECTED AS A RESULT OF THIS EVENT. THE HIGH VESSEL WATER LEVEL CAUSED A REACTOR SCRAM WHICH PLACED THE REACTOR IN A SHUTDOWN CONDITION.
458 | 4581987012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581987012R01.pdf | 1987-06-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | River Bend | B | GE | PO | 70 | POWER LEVEL - 070%. ON 6/18/87 AT 0322, WITH THE UNIT AT APPROXIMATELY 70 PERCENT POWER, A REACTOR TRIP OCCURRED. INITIATION OF THE REACTOR PROTECTION SIGNAL WAS CAUSED BY A REACTOR VESSEL WATER LEVEL - HIGH LEVEL 8 (51 INCHES) CONDITION. A LOSS OF CONTROL POWER TO PANEL 1VBN-PNL01B1 OCCURRED INADVERTENTLY DURING THE TROUBLE SHOOTING OF BATTERY INVERTER 1BYS-INV01BB *INVT*. LOSS OF CONTROL POWER TO THE FEEDWATER REGULATING VALVES CAUSED THEM TO LOCKUP IN A POSITION CONSISTENT WITH 70 PERCENT REACTOR POWER. ALSO, AS A RESULT OF THE LOSS OF THE INVERTER, THE RECIRCULATION SYSTEM FLOW CONTROL VALVES RAN BACK. SIMULTANEOUSLY, THE RECIRCULATION PUMPS RECEIVED A SIGNAL TO TRANSFER TO THE LOW FREQUENCY MOTOR GENERATORS. THIS CAUSED SUFFICIENT FEEDWATER FLOW/STEAM FLOW MISMATCH TO INCREASE THE VESSEL LEVEL TO HIGH LEVEL 8. OPERATIONS PERSONNEL RESPONDED BY SATISFACTORILY IMPLEMENTING THE IMMEDIATE AND SUBSEQUENT ACTIONS REQUIRED BY 'REACTOR SCRAM' PROCEDURES. PROCEDURAL REVISIONS HAVE BEEN COMPLETED THAT WILL PRECLUDE RECURRENCE BY REQUIRING THE PLACEMENT OF THE BATTERY INVERTER IN MANUAL BYPASS MODE PRIOR TO TROUBLE SHOOTING. THERE WAS NO ADVERSE IMPACT ON THE SAFE OPERATION OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC AS A RESULT OF THIS EVENT. THE PLANT'S RESPONSE WAS IN A CONSERVATIVE DIRECTION WITH NO IMPACT ON SAFETY SYSTEMS. PLANT STAFF'S RESPONSE WAS IN ACCORDANCE WITH APPROVED PROCEDURES.
458 | 4581988002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581988002R00.pdf | 1988-01-10 | QR8 | Spurious Reactor Trip | [45 empty] | River Bend | B | GE | PO | 95 | POWER LEVEL - 095%. ON 1/10/88 AT APPROXIMATELY 0933 HOURS, WITH THE UNIT IN POWER OPERATION AT APPROXIMATELY 95 PERCENT POWER, INSTRUMENT AND CONTROLS (I&C) TECHNICIANS INADVERTENTLY INITIATED A FULL SCRAM VIA THE ALTERNATE ROD INSERTION (ARI) TRIP SYSTEM, WHILE PERFORMING SURVEILLANCE TEST PROCEDURE (STP)-051-4269, 'ATWS RECIRC PUMP TRIP REACTOR VESSEL PRESSURE HIGH MONTHLY CHANNEL FUNCTIONAL, 18 MONTH CHANNEL CAL, 18 MONTH LSFT.' INVESTIGATION REVEALED THAT THE CHANNEL CAL, 18 MONTH LSFT.' INVESTIGATION REVEALED THAT THE TECHNICIANS LIFTED LEADS FROM THE WRONG TERMINAL BLOCK, WHICH CAUSED TWO ARI TRIP UNITS TO LOSE THEIR SIGNAL AND CAUSED AN ARI/ANTICIPATED TRANSIENT WITHOUT SCRAM (ATWS) SYSTEM INITIATION. THE STP WAS MISLEADING IN THE LOCATION OF THE TERMINAL BLOCK AND IMPROPERLY LED THE TECHNICIANS TO TERMINAL BLOCK 2B6 INSTEAD OF THE CORRECT TERMINAL BLOCK, TB0006. THE STP WAS REVISED, AND THE PROCEDURE WAS RERUN WITH NO PROBLEM. I&C TECHNICIANS WERE TRAINED ON THIS INCIDENT THROUGH SHOP TRAINING. AFTW STPS WERE REVIEWED, EVALUATED, AND REWORDED TO CLEARLY DEFINE THE CORRECTED TERMINAL BOARD LOCATION. THE INITIATION OF ARI CAUSED ALL CONTROL RODS TO BE INSERTED SHUTTING DOWN THE REACTOR. ALL PLANT RESPONSES OCCURRED AS DESIGNED. THERE WAS NO IMPACT ON THE SAFE OPERATION OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC.
458 | 4581988003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581988003R00.pdf | 1988-01-28 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | POWER LEVEL - 100%. AT 1612 ON 1/28/88 WITH THE UNIT IN POWER OPERATION (MODE 1) AT 100% POWER, VIBRATION INDUCED FAILURE OF A TEMPERATURE CONTROLLER IN THE MAIN GENERATOR STATOR COOLING SYSTEM CAUSED A MAIN TURBINE RUNBACK. THE TURBINE SHED ITS LOAD FASTER THAN REACTOR POWER COULD BE DECREASED CAUSING AN INCREASE IN REACTOR PRESSURE. ALL SYSTEMS RESPONDED PROPERLY DURING THE TRANSIENT WITH THE EXCEPTION OF THE 'B' REACTOR RECIRC PUMP WHICH TRIPPED OFF FROM HIGH SPEED INSTEAD OF SHIFTING TO LOW SPEED. THE STATOR TEMPERATURE CONTROLLER WAS REPAIRED AND RELOCATED TO A BUILDING STRUCTURAL MEMBER TO PROTECT IT FROM VIBRATION. THERE WAS NO ADVERSE IMPACT ON THE HEALTH AND SAFETY OF THE PUBLIC AS A RESULT OF THIS EVENT.
458 | 4581988007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581988007R00.pdf | 1988-02-21 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 4 | POWER LEVEL - 004%. ON 2/21/88 AT APPROXIMATELY 2226, WITH THE UNIT IN STARTUP (MODE 2 - APPROXIMATELY 4 PERCENT POWER), AN AUTOMATIC REACTOR SCRAM WAS INITIATED DUE TO TURBINE STOP CLOSURE COINCIDENT WITH GREATER THAN 40 PERCENT POWER AS SENSED BY FIRST STAGE TURBINE PRESSURE. OPERATORS FAILED TO MAINTAIN TURBINE FIRST STAGE PRESSURE WITHIN REQUIRED LIMITS DURING THE TURBINE SHELL WARMUP PROCEDURE ALLOWING THE FIRST STAGE TO INCREASE TO A PRESSURE INDICATIVE OF 40 PERCENT RATE POWER. THE OPERATOR HAD NEGLECTED TO MAINTAIN THE CORRECT TURBINE FIRST STAGE PRESSURE, RELYING ON STEAM PILOT VALVE POSITION AND TURBINE SHELL TEMPERATURE FOR INDICATION RATHER THAN PRESSURE INDICATORS AS REQUIRED BY PROCEDURE. OPERATORS HAVE BEEN PROVIDED TRAINING N THIS SPECIFIC EVENT. STATION OPERATING PROCEDURE (SOP)-0080, 'TURBINE GENERATOR OPERATION,' HAS BEEN REVISED VIA TEMPORARY CHANGE NOTICE ADDING A CAUTION STATEMENT WARNING OF THE POSSIBILITY OF A REACTOR SCRAM. THE TRIP SIGNAL CAUSING THIS REACTOR SCRAM IS NORMALLY BYPASSED AT LESS THAN 40 PERCENT RATED THERMAL POWER. SINCE POWER WAS APPROXIMATELY 4 PERCENT, THE PLANT WAS WELL BELOW POWER VALUES REQUIRING THE ACTUAL SAFETY RELATED FUNCTION OF THE TRIP SIGNAL. THEREFORE, THERE WAS NO ADVERSE IMPACT ON THE SAFE OPERATION OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC.
458 | 4581988018 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581988018R04.pdf | 1988-08-25 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | POWER LEVEL - 100%. AT 1232 ON 8/25/88 WITH THE UNIT AT 100% POWER (OPERATIONAL CONDITION 1), THE REACTOR AUTOMATICALLY SCRAMMED DUE TO A TURBINE CONTROL VALVE FAST CLOSURE CAUSED BY A LOSS OF MAIN GENERATOR FIELD EXCITATION RESULTING IN AUTOMATIC MAIN GENERATOR AND TURBINE TRIPS. IMMEDIATELY FOLLOWING THE SCRAM, REACTOR PRESSURE SPIKED TO A PEAK BETWEEN 1100 AND 1117 PSIG CAUSING THE 5 LOW-LOW SET SAFETY RELIEF VALVES TO CYCLE PER DESIGN. THE TURBINE BYPASS VALVES OPENED AS REQUIRED AND THE REACTOR RECIRCULATION PUMPS TRANSFERRED TO SLOW SPEED PER DESIGN. REACTOR WATER LEVEL INITIALLY DECREASED TO +4 INCHES AS INDICATED BY THE WIDE RANGE INSTRUMENTS DUE TO THE REACTOR PRESSURE SPIKE. THE HIGH PRESSURE CORE SPRAY (HPCS) AND REACTOR CORE ISOLATION COOLING (RCIC) SYSTEMS INJECTED AS A RESULT OF A SPURIOUS LOW REACTOR WATER LEVEL 2 SIGNAL CAUSED BY A HYDRAULIC PERTURBATION IN THE REACTOR WATER LEVEL INSTRUMENT REFERENCE LINES. AS A RESULT OF THE FEEDWATER FLOW CONTINUING. (DUE TO THE 'A' FEEDWATER CONTROL VALVE BEING IN THE MANUAL MODE AT 50% OPEN) IN CONJUNCTION WITH THE HPCS AND RCIC INJECTIONS, REACTOR WATER LEVEL RAPIDLY INCREASED TO LEVEL 8 CAUSING THE HPCS INJECTION VALVE AND THE RCIC STEAM SUPPLY VALVE TO CLOSE AND THE REACTOR FEEDWATER PUMPS TO TRIP PER DESIGN. THERE WAS NO SIGNIFICANT ADVERSE IMPACT ON THE SAFE OPERATION OF THE PLANT.
458 | 4581988021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581988021R01.pdf | 1988-09-06 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | POWER LEVEL - 100%. ON 9/6/88 AT 0606 HOURS, WITH THE UNIT IN OPERATIONAL CONDITION 1 AT 100 PERCENT POWER, THE GENERATOR/TURBINE TRIPPED RESULTING IN A REACTOR SCRAM. THE GENERATOR TRIPPED DUE TO A FAULT ON THE NEUTRAL GROUNDING TRANSFORMER FOR 1STX-XGN1A (NORMAL 13.8 KV STATION SERVICE TRANSFORMER). THE FAULT WAS CAUSED BY A STRAY CAT SHORTING OUT THE HIGH SIDE (13.8KV) OF THE GROUNDING TRANSFORMER. THE HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM AND REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM WERE INADVERTENTLY INITIATED ON SPURIOUS LEVEL 2 DIFFERENTIAL PRESSURE SIGNALS. HOURS BASED ON EMERGENCY CORE COOLING SYSTEM INJECTION INTO THE REACTOR VESSEL. GULF STATES UTILITIES COMPANY (GSU) IS INVESTIGATING METHODS OF PROTECTING THE EXPOSED TRANSFORMER TERMINATIONS FROM STRAY ANIMALS AND MODIFICATIONS TO THE HPCS AND RCIC SYSTEMS LOW REACTOR WATER LEVEL CIRCUITS TO PREVENT SPURIOUS ACTUATIONS FROM SIMILAR PRESSURE TRANSIENTS. THERE WAS NO IMPACT ON THE SAFE OPERATION OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC AS A RESULT OF THIS EVENT. THE REACTOR SCRAM PLACED THE UNIT IN THE SAFE SHUTDOWN CONDITION.
458 | 4581989007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581989007R00.pdf | 1989-02-20 | QP5 | Excessive Feedwater Flow | [45 empty] | River Bend | B | GE | SU | 2 | POWER LEVEL - 002%. AT 0153 ON 2/20/89 WITH THE UNIT IN OPERATIONAL CONDITION 2 WITH REACTOR POWER IN THE IRM RANGE AND DURING A REACTOR STARTUP FROM A CONTROLLED SHUTDOWN, A REACTOR SCRAM OCCURRED DUE TO AN INTERMEDIATE RANGE MONITOR (IRM) UPSCALE TRIP. THE IRM UPSCALE WAS CAUSED BY EXCESSIVE FEEDWATER WHICH DECREASED THE MODERATOR TEMPERATURE AND INDUCED POSITIVE REACTIVITY. CONTRIBUTING TO THIS EVENT WAS THE PLACING OF STEAM DRAINS IN SERVICE BY OPERATIONS. AS EACH DRAIN WAS PLACED IN SERVICE, OPERATIONS WAS ALLOWING REACTOR PRESSURE AND LEVEL TO STABILIZE. AFTER OPENING THE FOURTH DRAIN IN A SERIES OF FOUR, A FEEDWATER TRANSIENT OCCURRED CAUSING THE REACTOR SCRAM. UPON INVESTIGATION IT WAS DISCOVERED THAT DURING THIS TIME FRAME THE STARTUP FEED WATER REGULATOR VALVE WAS NOT RESPONDING PROPERLY DUE TO NUMEROUS AIR LEAKS IN THE VALVE OPERATOR. THE AIR LEAKS CAUSED THE VALVE TO HAVE A SLUGGISH RESPONSE. REACTOR STARTUP OPERATING PROCEDURE GOP-001 HAS BEEN CHANGED TO NOW REQUIRE A STEAM BYPASS VALVE TO BE OPEN APPROXIMATELY 50% PRIOR TO PLACING STEAM DRAINS IN SERVICE. THIS WILL ALLOW ADDITIONAL MARGIN TO COMPENSATE FOR THE DECREASE IN REACTOR PRESSURE IF A RAPID INCREASE IN FEEDWATER FLOW OCCURS. THERE WAS NO IMPACT ON THE SAFE OPERATIONS OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC.
458 | 4581989008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581989008R00.pdf | 1989-02-25 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 78 | POWER LEVEL - 078%. AT 0041 ON 2/25/89 WITH THE UNIT AT 78% POWER (OPERATIONAL CONDITION 1), THE REACTOR AUTOMATICALLY SCRAMMED WHILE PERFORMING A ROUTINE UPPER THRUST BEARING WEAR DETECTOR TEST IN ACCORDANCE WITH OPERATIONS SECTION PROCEDURE (OSP)-0101. THE SCRAM OCCURRED AS A RESULT OF A TURBINE TRIP CAUSED BY A DEFECTIVE BYPASS RELAY. THE RELAY FAILED TO OPEN THE 'TRIP BUS' CIRCUIT AS DESIGNED TO PREVENT A TURBINE TRIP WHILE TESTING THE THRUST BEARING WEAR DETECTOR. IMMEDIATELY FOLLOWING THE TURBINE TRIP, THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM INJECTED DUE TO A SPURIOUS LOW REACTOR WATER LEVEL 2 SIGNAL. THE SPURIOUS SIGNAL RESULTED FROM A PRESSURE PERTURBATION, CAUSED BY THE FAST CLOSURE OF THE TURBINE CONTROL VALVES, BEING SENSED BY THE REACTOR WATER LEVEL INSTRUMENTATION. REACTOR WATER LEVEL INCREASED TO LEVEL 8 AND THE RCIC STEAM SUPPLY VALVE CLOSED PER DESIGN. AS CORRECTIVE ACTION, A TURBINE TRIP BYPASS SWITCH WILL BE INSTALLED TO BE UTILIZED DURING THE WEEKLY TURBINE TESTING TO TEMPORARILY BYPASS TURBINE TRIPS WHICH MAY BE INADVERTENTLY CAUSED BY SPURIOUS RELAY ACTUATIONS WITHIN THE MAIN TURBINE ELECTRO-HYDRAULIC CONTROL PANEL. ADDITIONAL CORRECTIVE ACTION IS BEING IMPLEMENTED DURING THE SECOND REFUELING OUTAGE TO PREVENT SPURIOUS RCIC INITIATIONS.
458 | 4581989035 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581989035R00.pdf | 1989-09-30 | QR8 | Spurious Reactor Trip | [45 empty] | River Bend | B | GE | PO | 78 | POWER LEVEL - 078%. AT 0340 ON 9/30/89 WITH THE UNIT AT 78% POWER(OPERATIONAL 1), THE REACTOR AUTOMATICALLY SCRAMMED DURING THE PERFORMANCE OF A ROUTINE REACTOR PROTECTION SYSTEM (RPS) - MAIN STEAM LINE ISOLATION VALVE CLOSURE MONTHLY SURVEILLANCE TEST. THE CAUSE OF THE SCRAM WAS DETERMINED TO BE A DEFECTIVE TEST SWITCH IN THE REACTOR PROTECTION SYSTEM. THE DEFECTIVE GENERAL ELECTRIC SWITCH (MODEL CR 2940) HAD INADVERTENTLY PLACED THE SYSTEM IN A CONSERVATIVE STATE ALLOWING A SCRAM TO OCCUR AFTER A HALF SCRAM SIGNAL WAS INITIATED AS REQUIRED BY THE SURVEILLANCE TEST. THE TEST SWITCH WAS REPLACED VIA A PROMPT MAINTENANCE WORK ORDER. PRIOR TO SUCCESSFULLY COMPLETING THE SURVEILLANCE TEST, THE PROCEDURE WAS REVISED TO REQUIRE VERIFICATION OF PROPER SWITCH POSITION PRIOR TO PERFORMING THE SURVEILLANCE AND UPON RESTORATION. THE RPS SYSTEM WAS RETURNED TO SERVICE. THE RPS SYSTEM ACTUATED PER DESIGN IN RESPONSE TO THE DEFECTIVE TEST SWITCH CONDITION AND THE REACTOR SCRAM PLACED THE UNIT IN A SAFE SHUTDOWN CONDITION. THERE WAS NO ADVERSE IMPACT ON THE SAFE OPERATION OF THE PLANT NOR TO THE HEALTH AND SAFETY OF THE PUBLIC AS A RESULT OF THIS EVENT.
458 | 4581989042 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581989042R00.pdf | 1989-12-01 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 97 | POWER LEVEL - 097%. AT 0628 ON 12/1/89 WITH THE UNIT AT 97 PERCENT POWER (OPERATIONAL CONDITION 1), THE MAIN TURBINE GENERATOR TRIPPED, RESULTING IN A REACTOR SCRAM. THE GENERATOR TRIPPED DUE TO THE MAIN GENERATOR PROTECTION BREAKERS TRIPPING AS A RESULT OF SENSING A FAULT ON AN OFFSITE 230KV LINE. THE FAULT FAILED TO CLEAR AT THE 230KV SWITCHYARD DUE TO A FAILED RELAY AND SLOW BREAKER RESPONSE TIME FOLLOWING THE SIGNAL FROM A BACKUP RELAY. IMMEDIATELY FOLLOWING THE GENERATOR TRIP, THE STATION 4.16KV NORMAL SWITCHGEAR (1NNS-SWG1A) FAILED TO SUCCESSFULLY TRANSFER TO OFFSITE POWER. THIS CAUSED AN UNDERVOLTAGE CONDITION WHICH INITIATED AN AUTOMATIC START OF THE DIVISION III HIGH PRESSURE CORE SPRAY (HPCS) EMERGENCY DIESEL GENERATOR. INITIATION OF THE DIVISION III STANDBY SERVICE WATER PUMP 1SWP*P2C ALSO OCCURRED DUE TO A MOMENTARY LOSS OF POWER TO THE INITIATING TRIP UNITS. THE DIVISION III EMERGENCY DIESEL GENERATOR RESTORED POWER TO THE BUS PER DESIGN. THE REACTOR SCRAM PLACED THE UNIT IN THE SAFE SHUTDOWN CONDITION. SINCE ALL SAFETY SYSTEMS FUNCTIONED AS DESIGNED, THERE WAS NO IMPACT ON THE SAFE OPERATION OF THE PLANT OR TO THE HEALTH AND SAFETY OF THE PUBLIC AS A RESULT OF THIS EVENT.
458 | 4581990008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581990008R00.pdf | 1990-03-15 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 42 | At 2140 hours on 3/15/90 with the unit at 42 percent power (Operational Condition 1) the main turbine generator tripped, resulting in a reactor scram. The generator was tripped by protective relay operation due to a loss of field. This resulted in trip signals being sent to main generator protection breakers at the 230 KV switchyard. <br /><br /> GSU's investigation revealed a malfunction of the zone 1 loss of field relay (40G KLF). This relay was reworked and returned to service. Procedures have been upgraded to include state of the art three-phase testing methods and to clearly identify those conditions that initiate a generator trip. The reactor scram placed the unit in a safe shutdown condition. Since all safety systems functioned as designed, there was no impact on the safe operation of the plant or to the health and safety of the public as a result of this event.
458 | 4581990014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581990014R00.pdf | 1990-04-07 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 79 | At 0154 on 04/07/90 with the reactor at 79 percent power (Operational Condition 1), a reactor scram occurred while testing the main turbine combined intermediate valves (CIVs) (*V*). The scram occurred on low turbine electrohydraulic control (EHC) system pressure. This low pressure appears to have been due to multiple CIVs stroking when the #4 CIV was being tested. However, repeated testing failed to bring about a repetition of the event which caused the scram.<br /><br /> Corrective action included replacement of two solenoid valves, five relays, and the electrical trip valve. A modification has been installed to provide additional relay contacts between the CIVs and the test circuit. In addition, the valve testing procedure has been revised to require increased monitoring of valve position.<br /><br /> This event resulted in the actuation of the reactOr protection system (RPS). Therefore, this report is submitted pursuant to 10CFR50.73(a) (2)(iv). This event caused no adverse impact on the health and safety of the public.
458 | 4581990047 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581990047R00.pdf | 1990-12-12 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 80 | At 0032 hours on 12/12/9, while performing turbine overspeed protection weekly operability testing (STP-110-0101), a reactor scram occurred as a result of a turbine control valve (TCV) fast closure signal. At the time of the scram, the reactor was at a reduced power of 80 percent to perform the subject testing. The cause of the turbine control valve fast closure signal was due to a low electro-hydraulic trip system (ETS) pressure transient that occurred during scheduled surveillance testing of the combined intercept valves (CIVs). <br /><br /> Corrective actions included the installation of orifices on all ETS supply ports to the TCVs, turbine stop valves (TSVs), and CIVs. In addition, a transmitter was installed on the turbine front standard to verify ETS pressure.<br /><br /> All systems responded to the reactor scram per design. The RPS responded correctly to the TCV fast closure in anticipation of the loss of the turbine generator. Reactor water level at no time reached a level requiring the use of alternate sources of water injection to make up for lost inventory. Therefore, the reactor was not placed in a condition which threatened the health and safety of the public.
458 | 4581992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581992001R01.pdf | 1992-02-15 | QR8 | Spurious Reactor Trip | [45 empty] | River Bend | B | GE | PO | 100 | At 2328 on 02/15/92 with the unit at 100% power (Operational Condition 1) a loss of power to average power average monitors (APRMS) 'C' and 'G' resulted in a trip of the Division I reactor protection system (RPS) and a reactor scram. The Division II RPS had been previously placed in the tripped condition due to the failure of a surveillance test on the scram discharge volume (SDV) water level instrumentation. Following the reactor scram, normal switchgear NPS-SWG1A failed to fast transfer to the preferred station service transformer, 1RTX-XSR1A. However, an automatic slow transfer to the preferred station service transformer was successfully completed. This report is submitted pursuant to 10CFR50.73(a)(2)(iv), as an RPS actuation. <br /><br /> The reactor scram placed the unit in a safe shutdown condition and all safety systems functioned as designed. The failure of normal switchgear NPS-SWG1A to fast transfer to the preferred station service transformer, 1RTX-XSR1A, resulted in the loss of loads supplied by the normal switchgear, none of which are safety-related. All standby service water pumps functioned as designed and automatically started on low service water header pressure.
458 | 4581992005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581992005R00.pdf | 1992-03-05 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | At 02:03 on March 5, 1992 with the unit operating at 100 % power, (Operational Condition 1), a reactor scram occurred due to TCV fast closure. This was caused by a generator trip due to a C phase-to-ground fault of approximately 5 cycles on the 230KV transmission line from the main generator step up transformers to the Fancy Point switchyard. This ground occurred as a result of high winds which blew sheet metal siding loose from the southeast corner of the Turbine Building causing it to land on the energized components and damage the No. 2 main generator step up transformer high side disconnect switch.<br /><br /> Upon receiving a report of the extent of the damage, the Shift Supervisor declared a Notification of Unusual Event (NOUE) at 03:50. The NOUE was terminated at 04:23. All safety-related systems functioned as designed in response to the transient. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document the reactor scram. <br /><br /> The root cause of this event was high winds during a thunderstorm causing damage to the plant turbine building resulting in a phase-to-ground fault. This led to a generator trip and subsequent reactor scram, per design. The reactor scram occurred as designed. All safety systems functioned per design to place the plant in a safe shutdown condition. In addition, GSU has concluded that the radiological implications of insulation being blown out of the building walls are bounded by 10CFR20 Appendix C limits.
458 | 4581992026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581992026R00.pdf | 1992-11-24 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | River Bend | B | GE | PO | 96 | On 11-24-92, at 00:54:49.9, the reactor scrammed from 96 percent power due to problems with the steam bypass and pressure regulator system. As a result of a mismatch between the 'A' and 'B' regulator outputs, the main turbine control valves changed position from approximately 35 percent open to 23 percent open. The resulting pressure increase caused a corresponding increase in reactor power. The plant then scrammed on high neutron flux. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document the reactor scram. <br /><br /> The root cause of the scram consisted of failures in the 'A' pressure amplifier card, and the 'B' pressure transmitter. These components have been replaced. <br /><br /> Failure of the pressure regulator is bounded by USAR chapter 15.2 'Increase In Reactor Pressure'. The high neutron flux scram setpoint Units the peak fuel surface temperature and ensures that the minimum critical power ratio (MCPR) was still within the safety limit for this transient. All plant systems responded as expected and the reactor was placed in a safe shutdown condition.
458 | 4581993017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581993017R00.pdf | 1993-08-10 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 75 | On August 10, 1993, at approximately 2149 with the plant at 75% power (Operational Condition 1), a personnel error, during "trouble shooting" the operation of the steam bypass & pressure regulating system, initiated a main steam isolation valve (MSIV) closure and subsequently a reactor scram. Investigation into the cause of this transient revealed that an instrumentation and control (I&C) technician was disconnecting a piece of test equipment from a circuit card in the Channel B steam bypass control circuitry. While disconnecting the test equipment, the technician shorted a signal common to +22vdc resulting in the partial loss of power for the steam bypass system. The root cause for this event was that the management policies and expectations were not effectively communicated to the workers, planners and line management. The persons performing the test should have implemented measures to isolate the surrounding work area once they had identified the confined working conditions. <br /><br /> Consistent with strengthening the program for GSU's management policies and expectations, I & C personnel have been instructed that they are responsible for screening the work area for possible unanticipated effects on the plant. Precautions/prerequisites that match the current plant conditions shall be specifically included in MWO test packages. A review of the plant response to this transient indicates that all plant systems reacted as designed. An analysis of the key plant parameters important to plant safety indicates that these parameters remained well within all safety limits. .
458 | 4581993024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581993024R02.pdf | 1993-10-14 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 95 | On October 14, 1993, at 0842, with the plant at 95 percent power (Operational Condition 1) for the performance of routine turbine testing, a turbine trip and reactor scram occurred due to the failure of relay contacts to open per design. This report is submitted pursuant to 10CFR50.73(a)(2)(iv), as an automatic actuation of an engineered safety feature (ESF).<br /><br /> Entergy has concluded that this event was caused by the failure of the K15-1 relay contacts to open. During troubleshooting, the failure of the K15 relay could not be recreated. Following troubleshooting, the K15 relay was replaced and successfully tested. The plant was safely brought to the Hot Shutdown condition. The relay was subsequently tested in the relay shop and all test results were satisfactory. The failure mode could not be identified.
458 | 4581994023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581994023R01.pdf | 1994-09-08 | QR8 | Spurious Reactor Trip | [45 empty] | River Bend | B | GE | PO | 97 | On September 8, 1994 at 8:28 PM, with the reactor at 97 percent power, an automatic reactor scram occurred due to a false high reactor water level condition sensed on channels C and D of the reactor water level instrumentation. During this event, the RCIC turbine tripped due to binding of the turbine governor valve. The conditions leading to this failure have been determined to be reportable pursuant to 10CFR21. Since the HPCS system was manually operated during this event, this supplement also finalizes the Special Report required by Technical Specification 3.5.1 concerning emergency core cooling system (ECCS) injections. <br /><br /> The cause of this event is spurious signals from undamped Rosemount model 1153 transmitters in response to process noise. The model 1153 transmitters that were in service in the reactor water level instrumentation application have been replaced with Rosemount model 1152s. Extensive monitoring was conducted as a conservative measure during the startup from the forced outage and continuing into power operation for a limited period of time. <br /><br /> The investigation of transmitter performance revealed that the model 1153 susceptibility to process noise would not have prevented the transmitters from functioning properly in an actual event. Equipment and radiological issues, including reactor vessel cooldown and the Technical Specification surveillance time limit non-compliances for radiological and chemistry sampling were evaluated and determined not to be safety significant. Therefore, this event did not compromise the health and safety of the public.
458 | 4581994028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581994028R00.pdf | 1994-10-28 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 40 | On October 28, 1994, with the plant in Operational Condition 1 (Power Operation) and decreasing power for a planned shutdown, vibration levels on main turbine bearings 5 and 6 increased to the trip set point of 10 mils. The plant was manually scrammed and the turbine manually tripped to prevent potential turbine damage due to high vibration. <br /><br /> The root cause of the event is increased temperature sensitivity of the Low Pressure Turbine Rotor B following its recent replacement in conjunction with step changes in rotor temperature caused by throttling the reheating steam supply valves. Corrective actions include limiting the rate of rotor temperature change by expanding the limitations at which the MSRs can be placed into or removed from service during plant start-up or shutdown. During the event, turbine vibration remained within acceptable levels and the temperature change requirements for the MSR were never exceeded. An evaluation determined that safety systems functioned as designed and concluded the event was of no safety significance.
458 | 4581994030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581994030R00.pdf | 1994-12-04 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 100 | On December 4, 1994 with the plant in Operational Condition 1 (Power Operation), a reactor scram occurred when isolation logic was satisfied for a Main Steam Isolation Valve (MSIV) isolation. This isolation signal was the direct result of surveillance activities that were being performed prior to the event. <br /><br /> The root cause of the event was that a procedural step requiring removal of a half MSIV isolation signal was not performed as required. This action resulted in the failure to remove a half MSIV isolation signal on one test channel prior to proceeding to the next test channel where another half MSIV isolation signal was generated. Corrective actions consisted of reinforcing management expectations regarding personal accountability and procedure compliance. Also, the procedure revision process was modified to ensure that the appropriate verification requirements are considered during procedure revisions and reviews. The surveillance procedure was revised to incorporate the appropriate level of verification to ensure the MSIV isolation circuitry was restored before proceeding in the procedure. An evaluation determined that operator actions during the scram were appropriate and that safety systems functioned as designed.
458 | 4581995012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581995012R00.pdf | 1995-12-19 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 85 | On December 19, 1995 with the reactor at approximately 85 percent power, one recirculation pump tripped followed shortly by the downshift of the other pump. The resulting core flow appeared to place the plant in an unanalyzed power-to-flow condition. To avoid possible instabilities, the reactor was manually scrammed.<br /><br /> A Significant Event Response Team (SERT) was established to investigate this event. The investigation determined that both of the recirculation pumps functioned as designed in response to a cavitation interlock signal. The root cause of this event has been determined to be a spurious actuation of this cavitation interlock. was determined to be a loose connection in the trip instrumentation circuitry. Contributing conditions involved the reduction of the setpoint margin due to a planned reduction of reactor pressure, the end-of-cycle coastdown and the as-found instrument drift. <br /><br /> Immediate corrective action was taken to recalibrate the instruments. The loose connection found during RF6 has been repaired. On-line monitoring of this interlock is being established. In addition, an evaluation is being conducted to investigate the deletion or bypassing of this trip function. No evidence of a power oscillation or power level excursion was detected. The operators acted safely and conservatively by manually scramming the reactor. All safety systems functioned as designed and this event is not considered safety significant.
458 | 4581996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581996001R00.pdf | 1996-01-04 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 19 | On January 4, 1996, with the plant in Mode 1 (Power Operation) and reducing power for refueling outage 6 (RF-06), vibration levels on main turbine bearings 5 and 6 increased. vibration, the reactor was manually scrammed and the turbine was manually tripped.<br /><br /> The most probable cause of the event was determined to be the tight clearance between the rotor and the stationary parts of the Low Pressure (LP) Turbine 'B'. The tight clearance is intended to improve turbine efficiency, but has resulted in the turbine rotor being more sensitive to the temperature changes caused by plant power maneuvering and removal of the moisture separator reheaters (MSR) from operation. Contributing causes include some aspects of the MSR operation such as the inability of the high load/low load valves to provide the desired ramp control of MSR heating steam and sticking of one of the MSR level control valves. Corrective actions include modifying the high load/low load valves to provide better control of MSR heating steam and reworking the MSR level control valve. <br /><br /> During the event all safety systems functioned as designed and the turbine vibration remained within the acceptable limits. The event was, therefore, not safety significant.
458 | 4581996012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581996012R00.pdf | 1996-06-06 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 100 | On June 6, 1996, while the plant was in mode 1 at 100% power, turbine combined intercept valves and one turbine stop valve began to close unexpectedly causing a pressure rise which caused all four moisture separator reheater relief valves to lift. This caused a reduction in turbine load, followed by a reactor feed pump trip on low suction pressure. The control valves partially closed to control throttle pressure. When the moisture separator reheater relief valves reseated, reactor pressure vessel pressure began to increase and the average-power-range-monitor upscale alarm lights illuminated. A manual scram was then initiated. <br /><br /> The root cause was determined to be recently replaced electro-hydraulic control power supplies which were inadequate for their intended purpose. Even though the power supplies are configured such that a single failure should not affect the bus, a failed power supply caused bus voltage to degrade. not meeting their published design specifications and inadequate installation testing. Corrective actions included replacing the power supplies with ones that were acceptable. Various aspects of this event will be evaluated. Lessons learned training will be provided and an operating experience bulletin has been generated to alert the industry to the problems detected with the replacement power supplies. <br /><br /> The plant was safely and successfully shut down with all systems operating per design, resulting in no challenges to the primary fission product boundaries and no impact on nuclear safety.
458 | 4581997001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581997001R00.pdf | 1997-05-06 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 99 | On May 6, 1997, at 9:01 AM, with the plant in mode 1 (power operation) and the reactor at 99% power, contract insulators severed and shorted two wires inside a cable (*CBL*) while removing low density silicon elastomer (LDSE) from a floor penetration in the turbine building. This resulted in a trip of three electrical breakers de-energizing the 4.16kV safety-related bus "B", and the 4.16 kV and 13.8kV non-safety-related bus "B", resulting in a loss of two of three reactor feedwater pumps. The reactor operator initiated a manual scram at 9:02 AM on lowering water level in anticipation of an automatic scram at reactor vessel level 3. The loss of electrical busses also resulted in the loss of reactor protection system "B" and subsequent containment isolations. In addition, the inboard main steam isolation valves (MSIV) isolated on high temperatures in the turbine building and main steam tunnel. The primary causes of the cut cable event were determined to be: site standards, procedures, and formal guidance for breaching penetrations was less than adequate, and tools and techniques used for the work need improvement. The cause of the MSIV isolation was determined to be human engineering. Corrective actions include repairing the cut cable, developing expectations for breaching penetration seals, and evaluating measures to reduce vulnerability to isolations caused by ambient area temperatures. The reactor safely shut down and the main turbine trip occurred in accordance with plant design. Engineered safety feature (ESF) systems performed their safety function per design. These events are reportable pursuant 10CFR50.73 (a)(2)(iv) as a manual reactor protection system actuation and automatic ESF actuations.
458 | 4581997005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581997005R00.pdf | 1997-08-22 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 93 | On August 22, 1997, at 00:27, with the plant in mode 1 (power operation) and the reactor power at 92.9% power, a turbine stop and control valve closure occurred resulting in an automatic reactor scram. The turbine trip and monitor panel indicated the stop and control valve closure was due to low emergency trip system fluid pressure.The valve closure was due to a Turbine Emergency Trip System signal caused by a short circuit in a connector for the Main Turbine Electrical Trip Solenoid Valve. The short was due to the formation of a conductive bridge, containing elements of solder flux and solder spatter, between the connector conductors. The connector had been installed as part of a plant modification in June, 1994. The condition was discovered during troubleshooting performed subsequent to the August 22, 1997, scram.Immediate corrective action was to replace the connector prior to start-up. Additional corrective actions will be implemented to ensure maintenance personnel are knowledgeable and adequately trained on soldering skills, and to evaluate the installation of the new connector.An evaluation determined that operator actions during the scram were appropriate and that safety systems functioned as designed
458 | 4581999014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4581999014R00.pdf | 1999-10-29 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On October 29, 1999, with the plant in Mode 1 (Power Operation) at 100 percent power, an automatic reactor scram occurred following a trip of the main generator. Plant systems responded to the event as expected, with the exception of Reactor Recirculation Pump 'A.' (**ADIC2**). This pump tripped from fast speed to "off," failing to downshift to slow speed as expected for this event. The scram is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event that resulted in the automatic actuation of the reactor protection system.The cause of this event was the inadvertent initiation of a trip signal in the main generator breaker protective relay circuit (**EL/C38**) by inappropriate work activities in the substation relay house. Contributing to the inappropriate action was poor labeling of the pilot wire terminal boards at the substation. A warning sign identifying the pilot wire cables has been installed at the termination board. The reactor scram signal originated with the closure of the main turbine control valves (**JK/C18**). The event scenario is analyzed by the River Bend Updated Safety Analysis Report. This event was of no consequence to the health and safety of the public.
458 | 4582000012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582000012R00.pdf | 2000-08-21 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | River Bend | B | GE | PO | 81 | On August 21, 2000, at 1531 hours, with the plant operating at 81 percent power, the operating crew initiated a manual reactor scram in response to a decrease in main condenser vacuum. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a condition that resulted in the actuation of an engineered safety feature.Before the event, the plant was operating at 100 percent power. Troubleshooting activities were in progress on the main condenser offgas system in an effort to clear a low flow alarm. Instructions in the alarm response procedure directed the initiation of an air purge of the system. When the air purge was started, the air flow rate was apparently too high, causing excessive backpressure at the discharge of the main condenser air ejector. Condenser vacuum began to decrease, and operators began reducing power in accordance with procedure. Condenser vacuum could not be recovered prior to reaching the point at which a manual reactor scram is directed by operating procedures.Following the scram, the transient in reactor water level actuated the Level 3 setpoints, causing the actuation of an engineered safety feature in the suppression pool cooling (SPC) system. The SPC system was operating in the suppression pool cooling mode at the time. The containment isolation valves in the SPC system closed as designed. All plant responses to the scram were as expected. This event was of minimal potential consequence to the health and safety of the public.
458 | 4582001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582001001R00.pdf | 2001-04-21 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 58 | On April 21, 2001, at approximately 2:54pm, a reactor scram occurred during scheduled testing of the main turbine control valves. The plant was at approximately 58 percent rated power at the time of the scram. The scram was an automatic response to high reactor steam pressure resulting from an unanticipated closure of the main turbine control valves. Plant systems responded normally following the scram. Thirteen reactor safety-relief valves opened following the turbine trip, which is an anticipated response to this transient. Operators implemented the appropriate response procedures, and promptly stabilized the plant systems. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system.Subsequent troubleshooting and testing did not positively identify the root cause for the turbine trip. The most likely cause was determined to be a turbine speed signal error generated by rotor dynamics of the high pressure turbine during the testing of control valve no. 1.This event was of very low significance. A main turbine trip while at power is an analyzed event, and all plant systems responded normally.
458 | 4582002001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582002001R00.pdf | 2002-09-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On September 18, 2002, at 8:25 p.m., an automatic reactor scram occurred while the plant was operating at 100 percent power. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system and a manual actuation of the reactor core isolation cooling system.The sequence of events leading to the scram began with a voltage transient in the main turbine electro-hydraulic control system. This resulted in a "close" signal to the main turbine control valves, which caused reactor steam pressure to rise. The scram was initiated by a high neutron flux signal in the average power range monitors resulting from the rise in reactor steam pressure. Following the scram, a valve in the main condensate pump discharge header closed unexpectedly, shutting off flow to the reactor feedwater pumps. All three reactor feedwater pumps tripped in sequence due to low suction pressure, as designed. Operators initiated the reactor core isolation cooling system to provide makeup water to the reactor.This event is bounded by the analyses contained in the River Bend Updated Safety Analysis Report, and thus was of minimal significance with respect to the health and safety of the public.
458 | 4582003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582003001R01.pdf | 2003-02-22 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 90 | At approximately 1:23 a.m. CST on February 22, 2003, with the plant operating at 90 percent power in end-of-cycle coastdown, an unplanned manual reactor scram was initiated. During the scram recovery, the reactor core isolation cooling (RCIC) system was manually actuated to assist in reactor water level control. This event is being reported In accordance with 10CFR50.73(A)(2)(iv)(a) as a valid actuation of the reactor protection system and RCIC. The scram was necessitated by a fluid leak in the main turbine electrohydraulic control system that significantly depleted the system. Subsequent investigation determined that the leak occurred when a section of hydraulic tubing near the main turbine control valves developed a through-wall crack. An analysis of the failed tubing indicated that the likely cause was metal fatigue induced by system vibration. Additionally, pipe stress analysis verified that the tubing was overstressed due to deficiencies in design and configuration. Plant safety systems responded normally to the manual scram and the RCIC initiation. This event was of minimal significance to the health and safety of the public.
458 | 4582003008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582003008R00.pdf | 2003-09-22 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 78 | At 10:43 p.m. CDT on September 22, 2003, with the plant operating at approximately 78 percent power, an automatic reactor scram occurred during scheduled testing of the main turbine control valves. The scram signal originated from reactor steam pressure instruments following a malfunction of the main turbine control system which caused the control valves to move toward the closed position. A containment isolation signal initiated due to the expected reactor low water level alarm, which caused the isolation of the suppression pool cooling system, as designed. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a valid actuation of the reactor protection system and the containment isolation logic circuitry. Modifications are being considered to prevent recurrence of this condition. Turbine control valve testing has been suspended pending further corrective actions. This event was of very low safety significance, as the response of the plant to the scram signal was bounded by the safety analysis.
458 | 4582004001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582004001R00.pdf | 2004-08-15 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | X |  |  |  |  | River Bend | B | GE | PO | 100 | At 4:05 a.m. on August 15, 2004, with the plant operating at 100 percent power, an automatic reactor scram occurred as a result of a main turbine trip. A fault caused by failure of a 230kv transmission tower remote from the River Bend switchyard initiated a trip signal to an oil circuit breaker in the switchyard. Slow operation of some of the switchyard breakers caused a failure to clear the fault within the design time frame and the initiation of the breaker failure scheme. This resulted in a trip of one of the two main generator output breakers. Due to the slow clearing time, the ground fault protection system for the main generator step-up transformers also responded to the fault signal and tripped the remaining main generator output breaker. The resulting electrical transient also caused the loss of power to the Division 2 standby switchgear, which caused the automatic start of the Division 2 diesel generator. The reactor core isolation cooling system was initiated manually following the loss of the third main reactor feedwater pump. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(a) as an event that resulted in the initiation of the reactor protection system, the Division 2 diesel generator, the reactor core isolation cooling system. The breakers of the type that exhibited slow operation were inspected and lubricated, or left out of service for plant startup. This event was of low actual safety significance, as the plant response was within the bounds of the safety analysis. All safety systems responded as expected.
458 | 4582004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582004002R00.pdf | 2004-10-01 | QR5 | Turbine Trip | [10 empty] | X |  |  | X | [25 empty] | X | X |  |  |  | X | River Bend | B | GE | PO | 100 | On October 1, 2004, at 7:17 a.m., with the plant operating at 100% power, a loss of power to the Division 1 standby switchgear caused the automatic start of the Division 1 diesel generator. Some non-safety switchgear were also deenergized by this event. At 7:30 a.m., an automatic reactor scram was initiated by a main turbine trip. Both of these events were caused by the flashover of high-voltage insulator strings in the station transformer yard. During the event, all main reactor feedwater pumps shut down, main condenser vacuum was lost, and the standby service water system initiated. The reactor core isolation cooling (RCIC) turbine steam supply valve isolated during the pressure transient associated with the main turbine trip. Operators manually started the high pressure core spray (HPCS) system to provide water to the reactor. A momentary low reactor water level caused a primary containment isolation signal. This is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system, Division 1 diesel generator, and standby service water system; an automatic isolation of primary containment; and the manual actuation of the RCIC and HPCS systems. There were no safety systems out of service at the time of the first event. Mitigating safety systems responded as designed. This event is bounded by the River Bend safety analysis, and was thus of minimal safety significance.
458 | 4582004005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582004005R01.pdf | 2004-12-10 | QR3 | Reactivity Control Imbalance | [45 empty] | River Bend | B | GE | PO | 100 | On December 10, 2004, at 1:17 p .m. CST, an automatic reactor scram occurred while the plant was operating at 100 percent power. The scram was the indirect result of the failure of a 120 volt AC uninterruptible power supply (UPS) on a non-safety related instrument bus. The UPS failed due to a shorted capacitor on an internal circuit board. The loss of the instrument bus resulted in the downshift of the reactor recirculation pumps to slow speed and the lockup of the main feedwater regulating valves. The decrease in coolant flow caused a flow-biased simulated thermal power signal to be sensed in the average power range monitoring system, which actuated the reactor protection system (RPS). The reactor core isolation cooling (RCIC) system was manually started in response to the failure of the feedwater regulating system. RCIC subsequently shut down as designed due to a high reactor water level signal. While it was idle, an alarm actuated indicating the presence of water in the RCIC turbine exhaust drain trap. A conservative decision was made to leave RCIC out of service and to start the high pressure core spray (HPCS) system as needed for reactor water level control. The reactor scram occurred as designed, and reactor water level was maintained above the low-low alarm setpoint. This event is being reported in accordance with 10CFR50.73(a)(2)(IV)(A) as a condition that resulted in the actuation of the RPS, RCIC, and HPCS systems. This event was of minimal safety significance.
458 | 4582005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582005001R01.pdf | 2005-01-15 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 100 | On January 15, 2005, at 2:12 a.m. CST, while the plant was operating at 100 percent power, a manual reactor scram was initiated. This action was procedurally required in response to an alarm received at 2:10 a.m. which indicated a ground fault in the main generator. The plant shutdown proceeded normally, and safety systems responded as required. This event is being reported in accordance with 10CFR50.73(A)(2)(iv)(a) as a condition that required the manual actuation of the reactor protection system. Reactor water level was adequately controlled by the main feedwater system. No actuations of emergency core cooling systems, reactor safety relief valves, or standby diesel generators were required. The ground fault alarm relay was found to be overly sensitive to a low ground current, causing it to actuate early. Absent an intrusive internal examination of the generator, the most likely cause of the ground leakage current is deposition of copper oxide in the rectifier banks. These deposits resulted from an abnormally low dissolved oxygen concentration in the stator water cooling system due to a small hydrogen leak into the system. There were no safety systems out of service at the time of the event. This event was of minimal safety significance.
458 | 4582006004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582006004R00.pdf | 2006-04-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On April 15, 2006, at 4:15 p.m., an automatic reactor scram occurred while the plant was operating at 100% power. Prior to the scram, both reactor recirculation pumps shifted from high to slow speed due to a failed optical isolator card in the reactor protection system. With the reactor control rod pattern set for full power operation, the decrease in reactor recirculation flow caused the average power range monitors (APRM) to trip on a simulated high thermal power signal. The APRM trip signal caused the reactor scram approximately twelve seconds after the recirculation pumps downshifted. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a valid actuation of the reactor protection system. There were no safety-related systems out of service at the time of the event. Plant systems responded to the scram as designed, and reactor pressure and water level were promptly stabilized. Both optical isolator cards in the EOC-RPT circuitry were replaced during the forced outage. A downshift of both reactor recirculation pumps while operating at full power is an event analyzed in the River Bend Updated Safety Analysis Report. As such, this event was of minimal safety significance.
458 | 4582006007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582006007R00.pdf | 2006-10-19 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | River Bend | B | GE | PO | 100 | On October 19, 2006, at approximately 5:57 p.m. CDT, an automatic reactor scram occurred in response to a low water level signal (Level 3) in the reactor vessel. This condition was the result of the inadvertent closure of the motor-operated isolation valves in the main feedwater headers supplying the reactor. These valves closed when part of a chart recorder was accidentally dropped on their control switches. The high pressure core spray system automatically actuated as designed when its reactor water level (Level 2) initiation setpoint was reached. The reactor core isolation cooling system was out of service for planned maintenance. Reactor steam pressure began to decrease as expected, and when pressure reached 849 psig approximately three minutes after the scram, the main steam isolation valves (MSIVs) automatically closed. The MSIVs closed because the reactor mode switch was not promptly re-positioned as required by scram response procedures. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the reactor protection system and the high pressure core system (including the Division 3 diesel generator). Also, primary containment isolation signals actuated as a result of the Level 2 condition and the low reactor steam pressure signal to the MSIVs.
458 | 4582007002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582007002R00.pdf | 2007-05-04 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 67 | At 1256 CDT on May 4, 2007, an unplanned manual reactor scram was initiated following the loss of cooling on the No. 2 main transformer. Reactor power at the time of the scram was approximately 67 percent. Following the scram, reactor water level briefly decreased below Level 3 as expected, resulting in the automatic closure of two containment isolation valves in the suppression pool cleanup system. This isolation was confirmed to have occurred as designed. Control of reactor pressure and water level was promptly established. No emergency coolant injection system actuation was required.This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition that resulted in the unplanned manual actuation of the reactor protection system. The loss of cooling to the transformer resulted from an electrical fault in the cooling system control cabinet caused by rainwater intrusion. The cabinet was repaired and sealed, and preventative maintenance procedures are to be enhanced to prevent recurrence. The plant responded to the manual scram as expected, thus this event was of minimal safety significance.
458 | 4582007005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582007005R00.pdf | 2007-09-26 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On September 26, 2007, at 10:42 pm CDT, an unplanned automatic reactor scram occurred while the plant was operating at 100 percent power. At the time of the event, scheduled surveillance testing was in progress for a functional test of the average power range monitor (APRM) channel "A". Part of the test procedure involved the actuation of the Division 1 reactor protection system (RPS) trip circuitry. When this action was taken, 36 reactor control rods ("Group 2" rods) unexpectedly inserted into the core. As the reactor operator was taking actions to respond to this condition, an automatic reactor scram was generated by a low reactor water level (Level 3) signal. This event is being reported in accordance with10CFR50.73(a)(2)(iv) as an automatic actuation of the reactor protection system. The investigation found that a terminal block and wiring had been damaged by overheating due to a loose terminal screw, which had caused a loss of power to the scram valve pilot solenoids on the Group 2 rods. This loss of power was not apparent to the operators, as it occurred in a part of the circuit downstream of the power status lights. The damaged components were repaired, and similar circuits were inspected for loose terminals.
458 | 4582007006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582007006R00.pdf | 2007-11-07 | QP3 | Loss of Condensate Flow | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 75 | On November 7, 2007, at 3:06 a.m. CST, an unplanned manual reactor scram was initiated following the loss of the operating condensate pumps. The plant was operating at 75 percent power at the time. The main condensate pumps tripped when power was lost on the "A" non-safety 13.8kv bus, in addition to numerous 480v load centers supplied by that bus. The loss of that 13.8kv bus occurred when a rodent inside a transformer enclosure supplied by that bus caused arcing across phases and to ground. The slow action of the circuit breaker feeding the faulted transformer caused the main feeder breaker to the "A" 13.8kv bus to trip. Following the scram, reactor water level decreased below the actuation setpoint of the high pressure core spray (HPCS) system and the reactor core isolation cooling (RCIC) system, both of which started automatically as designed. Due to the loss of electrical power, the normal service water system was being supplied by only one 50 percent capacity pump, resulting in an abnormally low header pressure. The standby service water system was being placed into service to raise header pressure when the "C" standby service water pump started automatically due to the low pressure condition (this response was as designed, considering the configuration of the system at thetime). The Level 2 signal also caused actuation of the primary containment isolation valves in numeroussystems, which were confirmed to have responded as designed. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an unplanned manual actuation of the reactor protection system, as well as the automatic actuations of the HPCS, RCIC, standby service water, and primary containment isolation systems.
458 | 4582008002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582008002R00.pdf | 2008-03-05 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | River Bend | B | GE | PO | 60 | On March 5, 2008, at 2:43 p.m. CST, an automatic reactor scram occurred while the plant wasoperating at 60 percent power. The scram signal was initiated by high steam pressure in the reactor,and all control rods inserted as designed. The initial pressure transient caused the automatic actuationof nine main steam safety-relief valves. Reactor water level momentarily decreased to Level 3 immediately following the scram, resulting in the automatic closure of the containment isolation valvesin the suppression pool cleanup system. Reactor pressure and water level were promptly stabilizedfollowing the initial transient. A malfunction in the main turbine control system resulting from a loose,oil-contaminated electrical connector apparently produced an errant turbine speed error signal. Thissignal caused a closure of the turbine control valves, resulting in high reactor steam pressure. Theconnector was cleaned and reassembled. A preventative maintenance task will be developed to inspect this and similar connectors periodically. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an unplanned actuation of the reactor protection system and the primary containment isolation system.
458 | 4582009002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582009002R00.pdf | 2009-09-20 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 23 | On September 20, 2009, at 5:47 p.m. CDT, an unplanned manual reactor scram was initiated while reactor power was at approximately 23 percent of rated thermal power. A plant shutdown for a refueling outage was in progress at the time. At approximately 5:33 p.m., with reactor power at 37 percent, the operators had attempted to shift the reactor recirculation pumps from fast speed to slow in accordance with the plant shutdown procedure. RCS pump "A" shifted to slow speed, but approximately nine seconds later, it tripped off. RCS pump "B" did not complete the transfer to slow speed, but tripped off from high speed. Following the trip of the RCS pumps, the thermal-hydraulic conditions in the reactor remained within operational limits of plant Technical Specifications. The response procedures for the trip of both RCS pumps did not specify the actuation of the manual scram. The conservative decision was made to initiate the scram. After the scram signal was initiated, operators stabilized reactor pressure and temperature. All systems responded as designed. No safety systems were out of service at the onset of the event. A controlled reactor cooldown was commenced in preparation for the outage. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition that resulted in the unplanned manual actuation of the reactor protection system while the reactor was critical.
458 | 4582011003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582011003R00.pdf | 2011-12-23 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On December 23, 2011, at approximately 6:10 a.m. CST, the main turbine tripped unexpectedly, resulting in a reactor scram. The plant was stable at 100 percent power at the time of the event, and no safety-related systems were out of service. Operators implemented the appropriate response procedures, and began to stabilize reactor vessel pressure and water level. The closure of the turbine control valves resulted in the actuation of at least fifteen of sixteen main steam safety relief valves. A subsequent high reactor water level caused a trip of all three reactor feedwater pumps. As reactor water level lowered back through the normal operating range, operators attempted to restart a feedwater pump, but component malfunctions were encountered on "B" and "C" pumps. The reactor core isolation cooling (RCIC) system was manually actuated approximately nine minutes after the scram and injected water into the reactor for approximately two minutes. The "A" feedwater pump was restored to service approximately one minute after RCIC was initiated. The cause of the turbine trip was a spurious backup over-speed trip resulting from an electrical discharge from the turbine shaft in the vicinity of the EHC turbine speed pickup probe. The cause of the electrical discharge was due to a failure of the shaft grounding system. The plant responded as designed, and no emergency core cooling system actuation setpoints were exceeded. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of the reactor protection system (RPS).
458 | 4582012002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582012002R00.pdf | 2012-05-21 | QL7 | Degraded condenser vacuum | [45 empty] | River Bend | B | GE | PO | 100 | On May 21, 2012, at 2:52 p.m., while the plant was operating at 100% power, an automatic reactor scram occurred due to a partial loss of vacuum in the main condenser. This condition initially caused a trip of the main turbine, and the fast closure of the turbine control valves provided the actuation signal to the reactor protection system (RPS). Main condenser vacuum remained within the operating limits for use of the main turbine bypass valves, thus reactor pressure was automatically controlled following the initial transient. The reactor feedwater system remained inservice. The decrease in main condenser vacuum resulted from the loss of two of four circulating water pumps. This condition was caused by the failure of a splice in one of three 13.8kV cables providing power to half of the 4160V switchgear at the circulating water structure. The splice failure resulted in a small fire inside a manhole located outside the protected area. The plant fire brigade confirmed the fire was out within approximately 24 minutes of the onset of the event. Six reactor safety-relief valves actuated in response to the main turbine trip. The reactor core isolation cooling (RCIC) system steam supply valve automatically closed due to a false high-flow signal from the steam flow sensors. The system was restored to its standby configuration at 5:36 p.m. No plant parameters requiring the automatic actuation of the RCIC system were exceeded during the event. The failed splice was replaced, and the other cables in the circuit were tested for integrity, resulting in the replacement of one other splice. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an automatic actuation of the RPS system. There were no safety-related systems out of service at the time of the event.
458 | 4582012003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582012003R00.pdf | 2012-05-24 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 32 | On May 24, 2012, at 3:40 p.m. CDT, a manual reactor scram was initiated in response to the loss of the running reactor feedwater pump. The plant was operating at approximately 32% power. The reactor core isolation cooling system was manually started to provide high pressure makeup to the reactor. The high pressure core spray system was manually started during the recovery from the event, but was not aligned to the reactor vessel. An electrical transient caused by the failure of a lockout relay resulted in the main supply breaker to the "B" 13.8kv switchgear to trip. Reactor recirculation pump "B" tripped due to the loss of its power source; the "A" reactor recirculation pump continued to operate in slow speed. The electrical transient also caused a loss of power to all main condenser circulating water pumps and normal service water pumps, necessitating the manual closure of the main steam isolation valves. The standby service water system actuated as designed in response to low normal service water pressure. The operators manually operated selected SRVs for reactor pressure control and for reactor cooldown. Personnel in the turbine building reported the presence of smoke in the area of the feedwater pumps, but no actual fire was observed. There were no safety-related systems out of service at the time. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an actuation of the reactor protection system and the standby servicewater system. This event was of low safety significance to the health and safety of the public.
458 | 4582014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582014002RC0.pdf | 2014-10-17 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On January 16, 2014, a final review of industry operating experience determined that the station's practice of allowing reactor pressure vessel (RPV) pressure to become negative during plant startup constituted a violation of Technical Specifications (TS). The plant was operating at 100 percent power at the time of this determination. Negative RPV pressure is not bounded by TS 3.4.11, Reactor Coolant System Pressure and Temperature Limits. As such, this condition constitutes operations prohibited by TS, and is being reported in accordance 10CFR50.73(a)(2)(i)(B). This condition occurred due to a failure to recognize that a negative RPV pressure is not allowed by the TS. Consequently, the practice was incorporated into the plant startup procedure and operator training. Interim action was taken to modify the use of the plant startup procedure. Subsequently, a revision to the procedure was developed and instituted. An engineering determined that the RPV remained within the established material stress margins. The RPV also remained within established margins with regard to brittle fracture of the RPV ferritic materials. As such, this condition was of minimal significance to the health and safety of the public.
458 | 4582014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582014002RC0.pdf | 2014-10-17 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On October 17, 2014, at approximately 3:03 a.m. CDT, a reactor scram occurred in response to a high neutron flux signal from the average power range monitors (APRMs). The plant was operating at 100 percent power at the time. Immediately prior to that signal, an apparent malfunction in the main turbine electro-hydraulic control (EHC) system caused both the main turbine steam bypass valves to fully open, and also commanded all four main turbine control valves to close. The resulting increase in reactor steam pressure caused reactor power to immediately rise to the trip setpoint of the APRMs, at which point the actuation of the reactor protection system (RPS) occurred. After the scram occurred, an operator in the auxiliary control room erroneously removed all the main condensate system demineralizers from service, isolating condensate flow to the suction header of the main feedwater pumps. The running feedwater pump tripped on low suction pressure. The mis-operation of the demineralizer system was promptly corrected, and the main feedwater system was restored to service. The cause of the EHC malfunction has not been determined. Potential failure points were identified, and those circuitry parts were replaced. A human performance error review was conducted regarding the mis-operation of the condensate demineralizers, and appropriate procedure revisions have been made. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the RPS system.
458 | 4582014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582014002RC0.pdf | 2014-10-17 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On October 17, 2014, at approximately 3:03 a.m. CDT, a reactor scram occurred in response to a high neutron flux signal from the average power range monitors ( APRMs ). The plant was operating at 100 percent power at the time. Immediately prior to that signal, an apparent malfunction in the main turbine electro-hydraulic control (EHC) system caused both the main turbine steam bypass valves to fully open, and also commanded all four main turbine control valves to close. The resulting increase in reactor steam pressure caused reactor power to immediately rise to the trip setpoint of the APRMs, at which point the actuation of the reactor protection system (RPS) occurred. After the scram occurred, an operator in the auxiliary control room erroneously removed all the main condensate system demineralizers from service, isolating condensate flow to the suction header of the main feedwater pumps. The running feedwater pump tripped on low suction pressure. The mis-operation of the demineralizer system was promptly corrected, and the main feedwater system was restored to service. The cause of the EHC malfunction has not been determined. Potential failure points were identified, and those circuitry parts were replaced. A human performance error review was conducted regarding the mis-operation of the condensate deminerlizers, and appropriate procedure revisions have been made. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the RPS system, and in accordance with 10CFR50.73(a)(2)(v) as a condition that potentially caused the loss of safety function of the affected RPS instruments.
458 | 4582014006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582014006R00.pdf | 2014-12-25 | QR8 | Spurious Reactor Trip | [45 empty] | River Bend | B | GE | PO | 85 | On December 25, 2014, at 0836 CST, a reactor scram occurred while the plant was operating at approximately 85 percent power. This event resulted from the loss of power on the Division 2 reactor protection system (RPS) bus, in conjunction with a pre-existing halfscram on Division 1. The loss of Division 2 RPS power also resulted in a Division 2 containment isolation signal. Approximately four minutes after the scram, reactor water level increased to the Level 8 setpoint, causing the running main feedwater pump to trip. As reactor water level decreased back through the normal operating range, operators attempted to re-start main feedwater pump "C," but its supply breaker failed to close. Main feedwater pump "A" was subsequently returned to service. As reactor water level decreased to the point at which the startup feedwater regulating valve (FRV) should have opened to establish automatic control, the valve failed to open. Attempts to open it with a manual input signal were unsuccessful, and the "C" main FRV was put back into service. By that time, reactor water level had decreased slightly below the Level 3 RPS actuation setpoint, resulting in a second scram signal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of the RPS system and the primary containment isolation logic. No plant parameters required the actuation of any standby diesel generators or emergency core cooling systems. No reactor safety-relief valves actuated. This event was of minimal safety significance with respect to the health and safety of the public.
458 | 4582015005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582015005R00.pdf | 2015-06-01 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | River Bend | B | GE | PO | 90 | On June 1, 2015, at 9:09 p.m. CDT, with the plant operating at 90 percent power, an unplanned automatic reactor scram occurred due to low reactor water level. This event resulted from the loss of a non-safety related instrument power panel, apparently caused by an internal electrical transient in a 125-volt AC / DC inverter. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as the automatic actuation of the reactor protection system. All reactor control rods inserted normally, and control of reactor parameters was promptly established using the main turbine bypass valves and the main feedwater system. An expected general containment isolation signal occurred when reactor water level decreased to Level 3. The "A" reactor recirculation pump shifted to slow speed as designed, while the "B" pump tripped off. The runback feature of the reactor recirculation flow control valves failed to operate due the loss of instrument power. No plant parameters requiring the actuation of the emergency diesel generators, the main steam safety-relief valves, or the emergency core cooling systems were exceeded. This event was, thus, of minimal safety significance to the health and safety of the public.
458 | 4582015009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582015009R01.pdf | 2015-11-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On November 27, 2015, at 4:31 a.m. CST, with the plant operating at 100 percent power, an automatic reactor scram occurred following the loss of power to both divisions of the reactor protection system (RPS). This condition resulted from a single-phase fault in the local 230kV switchyard. The initial response of the protective relays for the switchyard caused the breakers connected to the north 230kV bus in the switchyard to trip. The fault caused a voltage transient on the in-plant switchgear sufficient to trip the scram relays in the Division 2 RPS, resulting in a half-scram. The action of the protective relays continued, eventually causing the de-energization of reserve station service line no. 1. This lead to the loss of Division 1 RPS and a full reactor scram. The Division 1 and 3 emergency diesel generators started as designed to restore power to their respective safety-related onsite electrical distribution subsystems. No safety-related systems were out of service at the time of the scram, and reactor pressure and water level were promptly stabilized. All reactor control rods inserted properly. Multiple actuations of the main steam safety-relief valves (SRVs) occurred during the event. The nuclear steam supply system vendor reported this action was likely due to a localized pressure transient in the SRV instrumentation lines. SRV tailpipe temperature recorders indicated that all valves re-seated correctly following the initial transient. The cause of the event was an animal-induced fault in the 230kV switchyard that resulted in the automatic trip of the north bus feeder breaker to the RSS No. 1. The fault also caused the south bus feeder breaker to trip, de-energizing RSS No. 1.
458 | 4582016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582016002R00.pdf | 2016-01-09 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | River Bend | B | GE | PO | 100 | On January 9, 2016, at approximately 2:37 a.m. CST, with the plant operating at 100 percent power, an automatic reactor scram occurred concurrent with the closure of all main steam isolation valves (MSIVs). That action was the result of an electrical transient caused by a phase-to-phase fault on a nearby 230kV transmission line. The transient caused a momentary decrease in the voltage on both reactor protection system busses, which also power the MSIV control solenoids. The Division 2 primary containment isolation logic was also actuated, causing the Division 2 valves in balance-of-plant systems to close. Both divisions of the standby gas treatment system automatically started due to the shutdown of the normal annulus pressure control system. Both reactor recirculation pumps downshifted to slow speed. The company's transmission department investigated the event. Although no definite source of the fault was found, it was concluded that a lightning strike likely caused the transient. The fault occurred on a 230kV transmission line approximately three miles from the station. The fault lasted for 5.4 cycles before it was isolated by automatic breaker action, and caused the voltage on the switchgear supplying the RPS busses to decrease to approximately 34 percent of normal. This transient was sufficient to trip the scram solenoids and the MSIV solenoids. No plant parameter limits requiring the automatic actuation of any of the emergency core cooling systems or the emergency diesel generators were exceeded. This event, thus, was of minimal significance to the health and safety of the public. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an actuation of the reactor protection system and the primary containment isolation logic.
458 | 4582017003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582017003R00.pdf | 2017-03-10 | QK4 | Steam or Feed Leakage | [45 empty] | River Bend | B | GE | PO | 15 | On March 10, 2017, at approximately 7:14 a.m. CST, the reactor operator manually actuated a reactor scram in response to an abnormal increase in steam pressure. Reactor power was approximately 15 percent at the time. The turbine generator had been synchronized to the grid at 5:13 a.m. on March 10, and was being closely monitored by engineers and operators since a major modification to the turbine electro-hydraulic control (EHC) system had been installed during the recent refueling outage. Approximately 45 minutes prior to the manual scram, a main control room alarm actuated indicating a problem with the EHC system. A few minutes later, it was reported from the turbine building that there was a steam leak in the area of the EHC steam pressure transmitters. Shortly thereafter, reactor pressure began to increase with no demand signal present, at which time the reactor operator initiated the scram. The main feedwater system remained in service, and reactor water level control performed normally as designed. No reactor safety-relief valves actuated. The main turbine bypass valves did not open following the shutdown, and engineering review determined this condition was consistent with the response to the abnormal configuration of the EHC system pressure transmitters created by efforts to isolate the leak locally. Approximately five minutes after the scram, the outboard main steam isolation valves were manually closed to limit the reactor cooldown rate. This event resulted from the incorrect installation of a new compression fitting in the steam pressure instrumentation tubing for the main turbine control system. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the reactor protection system.
458 | 4582017007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582017007R00.pdf | 2017-06-23 | QR5 | Turbine Trip | [45 empty] | River Bend | B | GE | PO | 100 | On June 23, 2017, at 10:18 PM CDT, an unanticipated reactor scram occurred during scheduled testing of the main turbine generator. The plant was operating at 100 percent power at the time, and no safety-related equipment was out of service. A reactor recirculation system flow control valve runback occurred as designed, and the recirculation pumps properly downshifted to slow speed. The main feedwater system responded properly to control reactor water level. The scram signal was initiated by the closure of the main turbine control valves, which was an automatic response to a trip of the main generator. The associated steam pressure increase following turbine valve closure resulted in the actuation of 12 main steam safety-relief valves. A reactor water level 3 signal was received, as expected, following the turbine trip and reactor scram and was promptly restored to the normal reactor water level band. The non-safety related turbine building chillers tripped as a result of the electrical transient caused by the generator trip. One area served by that cooling system is the reactor water cleanup (RWCU) system heat exchanger room. Approximately 20 minutes after the scram, the temperature in that room exceeded the trip setpoint of the area temperature monitors, resulting in the automatic closure of the primary containment isolation valves for the RWCU system.
458 | 4582017008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582017008R00.pdf | 2017-08-18 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On August 18, 2017, at 8:55 p.m. CDT, an automatic reactor scram occurred while the plant was operating at 100 percent power. The operators promptly established control of reactor water level and pressure, and a controlled plant cooldown was commenced. The initial scram signal was a flow-biased thermal power trip on the average power range monitors. This action closely followed a planned shift of the master feedwater controller from channel "B" to channel "A." Troubleshooting discovered that the feedwater level channel select relay had failed such that no signal was present on the "A" channel. When that channel was selected, the feedwater system erroneously sensed that reactor water level was low, and caused all three feedwater regulating valves to move fully open. At the same time, the false low water level signal was sensed in the control circuitry for the reactor recirculation system, resulting in an automatic shift of the recirculation pumps to slow speed. The resultant decrease in core flow caused the flow-biased thermal power trip in the average power range monitors, actuating the reactor scram. The failed feedwater system relay was replaced with an updated model with gold contacts. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event resulting in the automatic actuation of the reactor protection system.
458 | 4582018007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582018007R00.pdf | 2018-02-01 | QR6 | Manual Reactor Trip | [45 empty] | River Bend | B | GE | PO | 27 | On February 01, 2018 River Bend Station was performing a plant startup. At approximately 27% power, an attempt was made to shift Reactor Recirculation Pump 'B' from slow to fast speed. A failure in the pump motor transformer caused the pump to trip during the upshift, requiring entry into AOP-0024, Thermal Hydraulic Stability Controls and GOP-0004, Single Loop Operation. Both procedures require monitoring core flow using the Validated Core Flow Emergency Response and Information System computer data point (WTX). When operators observed the data point they noted that it was "Suspect" and magenta in color, persuading the control room team to question the validity of WTX. The control room team engaged Nuclear IT to help resolve the anomaly. The control room team attempted to use several alternate indications of core flow, but ultimately was unable to reconcile the anomaly with the quality and color of WTX. Although the reactor was in compliance with Technical Specifications, the decision was made to conservatively shutdown the reactor. Nuclear IT contacted the operating crew several minutes after the shutdown to inform them that the data provided by WTX was indeed valid. AOP-0024 and GOP-0004 were revised, the color of "Suspect" data points was changed, and an extent of condition review was performed to determine if other transformers with the same vulnerability exist.
458 | 4582018010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4582018010R00.pdf | 2018-11-10 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | River Bend | B | GE | PO | 100 | On November 10, 2018 at 00:46, with the reactor operating at 100% power, Turbine Control Valve number 3 (CV3) unexpectedly closed. Turbine Control Valve number 4 (CV4) did not respond as designed and the reactor automatically scrammed on a reactor vessel high pressure signal. Following the scram, all major systems responded as designed. The CV3 closure was due to failure of the valve's push rod spring housing coupling bolts. The CV4 failure to correctly respond to the CV3 closure transient was due to incorrect operating procedure guidance. This event was of minimal significance to the health and safety of the public.
461 | 4611987017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987017R00.pdf | 1987-03-22 | QR3 | Reactivity Control Imbalance | [45 empty] | Clinton 1 | B | GE | SU | 1 | POWER LEVEL - 001%. ON MARCH 22, 1987, AT 0415 HOURS, WITH THE PLANT IN MODE 2 (STARTUP), LESS THAN 1% REACTOR POWER, 450 PSIG, A MANUAL REACTOR SCRAM WAS INITIATED AFTER THE CONTROL ROOM OPERATOR OBSERVED THAT THE CONTROL RODS WERE BEGINNING TO DRIFT INTO THE REACTOR CORE. SUBSEQUENT TO THE SCRAM IT WAS DETERMINED THAT THE CONTROL RODS BEGAN DRIFTING INTO THE REACTOR CORE DUE TO LOSS OF INSTRUMENT AIR TO THE SCRAM PILOT VALVE AIR HEADER DURING PERFORMANCE OF SURVEILLANCE PROCEDURE 9030.O1C016, 'EMERGENCY CORE COOLING SYSTEM REACTOR WATER LEVEL 1B21-N691A(E,B,F) CHANNEL FUNCTIONAL CHECKLIST.' THE CAUSE OF THIS EVENT IS ATTRIBUTED TO UTILITY OPERATOR ERROR IN THAT THE SIMULATED TRIP SIGNAL HAD NOT BEEN FULLY RESET PRIOR TO RELANDING OF THE ELECTRICAL LEAD THAT HAD BEEN LIFTED TO PRECLUDE CLOSURE OF VALVES 1IA005 AND 1IA008 DURING THE SURVEILLANCE TEST. CORRECTIVE ACTION WILL INCLUDE A REVISION OF THE SURVEILLANCE PROCEDURE TO PROVIDE FORMAL VERIFICATION THAT THE IA VALVES REMAIN OPEN. THIS EVENT IS NOT SAFETY SIGNIFICANT FOR MODES 3, 4 AND 5, SINCE ALL CONTROL RODS ARE ALREADY FULLY INSERTED. THIS EVENT RESULTS IN A REACTOR SCRAM IN MODES 1 AND 2, DUE TO THE LOSS OF INSTRUMENT AIR TO THE SCRAM PILOT VALVE HEADER.
461 | 4611987025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987025R00.pdf | 1987-05-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 16 | POWER LEVEL - 016%. ON MAY 6, 1987, AT 0617 HOURS, WITH THE PLANT IN MODE 1 AT 16% POWER, 920 PSIG AND 524 DEGREES FAHRENHEIT, FEEDWATER CONTROL VALVE 1FW004 FAILED 'AS IS' IN THE OPEN POSITION, AND REACTOR WATER LEVEL BEGAN TO RISE AND APPROACH THE AUTOMATIC SCRAM SETPOINT AT LEVEL 8 (52 INCHES). THE REACTOR WAS MANUALLY SCRAMMED BY THE CONTROL ROOM OPERATORS AT LEVEL 6 (41 INCHES). THE CAUSE OF THIS EVENT WAS A RUPTURED PRESSURE SWITCH THAT ALLOWED HYDRAULIC CONTROL FLUID TO LEAK OUT OF THE 1FW004 VALVE OPERATOR. CORRECTIVE ACTION INCLUDED REPLACEMENT OF THE RUPTURED PRESSURE SWITCH AND CLEANING OF COMPONENTS EXPOSED TO THE HYDRAULIC FLUID. THIS EVENT WAS EVALUATED AND DETERMINED NOT TO BE SAFETY SIGNIFICANT. THE EFFECTS OF THIS TYPE OF EVENT HAVE BEEN ANALYZED IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT AND HAVE BEEN FOUND ACCEPTABLE. PROMPT AND CORRECT OPERATOR ACTION WAS TAKEN BY MANUALLY SCRAMMING THE REACTOR BEFORE REACHING THE AUTOMATIC SCRAM SETPOINT. THIS EVENT IS REPORTABLE IN ACCORDANCE WITH 10CFR50.73(A)(2)(IV) DUE TO A MANUAL ACTUATION OF THE REACTOR PROTECTION SYSTEM.
461 | 4611987029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987029R00.pdf | 1987-05-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 18 | POWER LEVEL - 018%. ON MAY 24, 1987, AT 1815 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION) AT 18% REACTOR POWER AND 940 PSIG PRESSURE, THE MOTOR DRIVEN REACTOR FEED PUMP FEEDWATER REGULATING VALVE 1FW004 MALFUNCTIONED CAUSING A HIGH WATER LEVEL TRANSIENT. ALTHOUGH AN ATTEMPT WAS MADE BY THE OPERATIONS PERSONNEL TO MANUALLY STABILIZE AND BALANCE FEEDWATER FLOW, THE FAILED FEEDWATER REGULATING VALVE RESULTED IN REACTOR VESSEL WATER LEVEL OSCILLATIONS WHICH CAUSED REACTOR POWER LEVEL TO RISE DUE TO THE INTRODUCTION OF COLD FEEDWATER. THE RESULTING POWER LEVEL RISE CAUSED AN AUTOMATIC SCRAM OF THE REACTOR ON A HIGH FLUX LEVEL TRIP SIGNAL AT 40% REACTOR POWER. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO FAILURE OF FEEDWATER REGULATING VALVE 1FW004. IMMEDIATE ACTIONS INCLUDED PLACING THE MODE SELECTOR SWITCH IN SHUTDOWN, MANUALLY TRIPPING THE TURBINE AND VERIFYING THAT ALL RODS WERE IN THE CORE. THIS EVENT WAS NOT SAFETY SIGNIFICANT FOR EXISTING PLANT CONDITIONS OR OTHER PLANT MODES. THE EFFECTS OF THIS TYPE OF EVENT HAVE BEEN ANALYZED IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT AND HAVE BEEN FOUND ACCEPTABLE. THIS EVENT IS REPORTABLE IN ACCORDANCE WITH 10CFR50.73(A)(2)(IV) DUE TO AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
461 | 4611987036 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987036R00.pdf | 1987-07-13 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Clinton 1 | B | GE | PO | 53 | POWER LEVEL - 053%. ON JULY 13, 1987, AT 0045 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION), 53% REACTOR POWER, AN AUTOMATIC REACTOR SCRAM OCCURRED DUE TO A HIGH FLUX (75%) TRIP SIGNAL ON THE AVERAGE POWER RANGE MONITORS. THE HIGH FLUX TRIP OCCURRED AS A RESULT OF THE 'A' REACTOR RECIRCULATION FLOW CONTROL VALVE RAMPING FROM 19% TO 31% OPEN IN APPROXIMATELY ONE SECOND. AT THE TIME OF THIS EVENT, THE REACTOR RECIRCULATION FLOW CONTROL VALVES WERE BEING CLOSED TO REDUCE REACTOR POWER. FOLLOWING THE SCRAM, OPERATIONS PERSONNEL IMPLEMENTED THE SCRAM PROCEDURE AND THE FLOW CONTROL VALVES WERE HYDRAULICALLY LOCKED OUT. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO EQUIPMENT/COMPONENT MALFUNCTION DUE TO A LOOSE VELOCITY TRANSDUCER ON THE 'A' REACTOR RECIRCULATION FLOW CONTROL VALVE. THE SAFETY SIGNIFICANCE ASSESSMENT OF THIS EVENT DETERMINED THAT INADVERTENT OPENING OF THE REACTOR RECIRCULATION VALVES HAS BEEN ANALYZED IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT AND THE RESULTS OF THIS ANALYSIS SHOW THAT THE RESULTING TRANSIENTS ARE WITHIN THE DESIGN LIMITS OF THE PLANT. THIS EVENT IS REPORTABLE UNDER THE PROVISIONS OF 10CFR50.73(A)(2)(IV) DUE TO AN AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
461 | 4611987043 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987043R00.pdf | 1987-07-24 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 60 | POWER LEVEL - 060%. ON JULY 24, 1987, AT 0603 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION), 60% REACTOR POWER, AND NORMAL OPERATING TEMPERATURE AND PRESSURE, A REACTOR SCRAM OCCURRED AS A RESULT OF A TURBINE CONTROL VALVE FAST CLOSURE. THE TURBINE TRIP WAS CAUSED BY A TURBINE HIGH VIBRATION SIGNAL. THE CAUSE OF THE TURBINE HIGH VIBRATION TRIP IS ATTRIBUTED TO LOOSE CONNECTORS IN THE TURBINE TRIP VIBRATION DETECTION CIRCUITRY WHICH CREATED SUFFICIENT CIRCUIT NOISE TO CAUSE A SPURIOUS TURBINE TRIP SIGNAL AND ACTUATION OF THE REACTOR PROTECTION SYSTEM. FOLLOWING THE REACTOR SCRAM, IMMEDIATE ACTION WAS TAKEN IN ACCORDANCE WITH THE CLINTON POWER STATION SCRAM PROCEDURE. INVESTIGATION OF THE TURBINE VIBRATION CIRCUITRY IDENTIFIED LOOSE CONNECTORS ON VIBRATION CIRCUITRY FOR BEARINGS 1, 3 AND 7. THE LOOSE CONNECTORS WERE CORRECTED UNDER THE SUPERVISION OF GENERAL ELECTRIC. AN ASSESSMENT OF THE SAFETY IMPLICATIONS OF THIS EVENT DETERMINED THAT THIS EVENT WAS NOT SIGNIFICANT TO THE SAFETY OF OPERATIONS OF THE CLINTON POWER STATION. SCRAMS RESULTING FROM TURBINE TRIPS (LOAD REJECTIONS) HAVE BEEN ANALYZED IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT AND THE RESULTING TRANSIENTS ARE WITHIN THE DESIGN LIMITS OF THE PLANT. THIS EVENT IS REPORTABLE UNDER THE PROVISIONS OF 10CFR50.73(A)(2)(IV) DUE TO AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
461 | 4611987042 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987042R00.pdf | 1987-08-12 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Clinton 1 | B | GE | PO | 71 | POWER LEVEL - 071%. ON AUGUST 12, 1987, AT 0001 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION), 71% REACTOR POWER, AND NORMAL OPERATING TEMPERATURE AND PRESSURE, TECHNICIANS WERE CALIBRATING THE FUNCTION GENERATOR FOR THE 'A' REACTOR RECIRCULATION FLOW CONTROL VALVE. A TRACE OF INPUT VERSES OUTPUT FOR THE 'A' FLOW CONTROL VALVE WAS OBTAINED. TECHNICIANS INVOLVED BELIEVED THAT BOTH HYDRAULIC POWER UNITS, WHICH POSITION THE FLOW CONTROL VALVES, WERE LOCKED OUT. WHEN THE FLOW CONTROL VALVE FUNCTION GENERATOR CARD WAS REMOVED, THE 'B' FLOW CONTROL VALVE WENT TO ITS MINIMUM POSITION. THE TECHNICIANS REINSERTED THE FUNCTION GENERATOR CARD. THIS CAUSED THE FLOW CONTROL VALVE 'B' TO OPEN, CAUSING AN INCREASE IN CORE FLOW, AND A CORRESPONDING INCREASE IN CORE NEUTRON FLUX. THE REACTOR SCRAMMED ON A HIGH FLUX SIGNAL. THIS TRANSIENT IS BOUNDED BY THE ANALYSIS IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT. 10CFR50.73(A)(2)(IV) DUE TO AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
461 | 4611987050 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987050R00.pdf | 1987-08-25 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Clinton 1 | B | GE | PO | 60 | POWER LEVEL - 060%. ON AUGUST 25, 1987 AT 0736 HOURS WITH THE PLANT IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 60% REACTOR POWER AND NORMAL OPERATING TEMPERATURE AND PRESSURE, THE TURBINE GENERATOR TRIPPED ON LOW CONDENSER VACUUM RESULTING IN A REACTOR SCRAM. OPERATIONS PERSONNEL WERE IN THE PROCESS OF SHIFTING FROM THE 'B' TRAIN STEAM JET AIR EJECTORS (SJAE) TO THE 'A' TRAIN SJAE. THIS WAS THE FIRST ATTEMPT TO CHANGE TRAINS DURING OPERATION. WITH BOTH TRAINS IN PARALLEL SERVICE, THE OPERATORS CLOSED THE 'B' SJAE SUCTION VALVE AND WERE SECURING DRIVING STEAM WHEN CONDENSER VACUUM BEGAN DECREASING. A POSSIBLE BACKFLOW PATH WAS BELIEVED TO BE CAUSING THE VACUUM LOSS. THE 'B' TRAIN RECOMBINER MANUAL OUTLET VALVE WAS THEN CLOSED BUT VACUUM CONTINUED TO DECREASE. THE DECISION WAS MADE TO RESTORE THE 'B' SJAE TO SERVICE; HOWEVER, THE TURBINE GENERATOR TRIPPED. REACTOR SCRAM PROCEDURES WERE IMPLEMENTED. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO UTILITY NON-LICENSED OPERATOR ERROR RESULTING FROM A DEFICIENT VALVE LINEUP PROCEDURE. THE SAFETY IMPLICATION AND SIGNIFICANCE DETERMINED THAT THE EVENT WAS NOT SIGNIFICANT TO THE SAFETY OF OPERATIONS OF THE CLINTON POWER STATION.
461 | 4611987055 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987055R00.pdf | 1987-09-21 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 98 | POWER LEVEL - 098%. ON SEPTEMBER 21, 1987 AT 1245 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 98% REACTOR POWER, THE REACTOR PROTECTION SYSTEM (RPS) AUTOMATICALLY ACTUATED. THE ACTUATION OCCURRED DURING REACTOR FEEDWATER CONTROL SYSTEM RESPONSE TESTING FOR THE POWER ASCENSION TEST PROGRAM. THE TEST PROCEDURE CALLED FOR A -20% STEP CHANGE TO BE INSERTED INTO THE 'A' REACTOR FEED PUMP (RFP), FOLLOWED BY A +20% STEP CHANGE. WHEN THE +20% STEP CHANGE WAS INSERTED, THE STANDBY CONDENSATE/CONDENSATE BOOSTER PUMPS BOTH AUTOMATICALLY STARTED CAUSING AN INCREASED FLOW OF WATER INTO THE REACTOR. REACTOR WATER LEVEL BEGAN INCREASING. AT 48 INCHES, THE OPERATOR ATTEMPTED TO BRING THE FLOW UNDER CONTROL BY SHIFTING THE 'A' RFP INTO MANUAL CONTROL AND BY REDUCING SPAED BY TWO POTENTIOMETER TURNS. THE REACTOR TRIPPED DUE TO HIGH WATER LEVEL AT 52 INCHES. THE CAUSE WAS DETERMINED TO BE A FAULTY 'B' RFP NET POSITIVE SUCTION HEAD FUNCTION GEN@RATOR CARD. THE FUNCTION GENERATOR CARD HAS BEEN REPLACED. THE EVENT WAS NOT SAFETY SIGNIFICANT FOR EXISTING PLANT CONDITIONS OR OTHER PLANT MODES. THE EFFECTS OF A SIMILAR INCREASE IN REACTOR WATER LEVEL HAVE BEEN ANALYZED FOR A MORE SEVERE TRANSIENT IN CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT AND HAVE BEEN FOUND ACCEPTABLE. THIS EVENT IS REPORTABLE UNDER THE PROVISIONS OF 10CFR50.73(A)(2)(IV) DUE TO AN AUTOMATIC ACTUATION OF THE RPS.
461 | 4611987060 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611987060R00.pdf | 1987-10-02 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 90 | POWER LEVEL - 090%. ON OCTOBER 2, 1987 AT 1238 HOURS, WITH THE PLANT IN MODE 1 (POWER OPERATION) AT 90% REACTOR POWER, A NON-CLASS 1E 125 VOLTS DIRECT CURRENT (VDC) BREAKER MISOPERATION BY A UTILITY NON-LICENSED OPERATOR INITIATED A TRANSIENT RESULTING IN AN AUTOMATIC REACTOR TRIP. THE OPERATOR WAS ALIGNING BREAKERS TO SUPPORT MAINTENANCE OF THE NON-CLASS 1E BATTERIES. THE OPERATOR INCORRECTLY OPENED A CROSS TIE BREAKER BETWEEN THE TWO NON-CLASS 1E 125 VDC DISTRIBUTION PANELS, DEENERGIZING ONE OF THE PANELS RESULTING IN A REACTOR HIGH WATER LEVEL TRIP. THE CAUSE OF THE EVENT HAS BEEN ATTRIBUTED TO UTILITY NON-LICENSED OPERATOR FAILURE TO CORRECTLY ALIGN THE CIRCUIT BREAKERS. THE OPERATOR WAS NOT CERTAIN THAT HE HAD FOUND THE CORRECT BREAKER PRIOR TO THE MISOPERATION. THE OPERATOR HAS BEEN COUNSELLED FOR THE FAILURE TO RESOLVE THE BREAKER QUESTION WITH HIS SUPERVISOR. THE NON-CLASS 1E 125 VDC BUS POWER FEEDS ARE BEING REVIEWED AND WILL BE RELABELED AS NECESSARY. AS AN INTERIM MEASURE, A ONE-LINE DIAGRAM HAS BEEN INSTALLED ON THE NON-CLASS LE DIRECT CURRENT BREAKER PANELS IDENTIFYING THE LOCATION OF BREAKERS. THE EVENT WAS ASSESSED AS NOT SAFETY SIGNIFICANT; THE TRANSIENT IS BOUNDED BY CHAPTER 15 OF THE FINAL SAFETY ANALYSIS REPORT.
461 | 4611988017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611988017R01.pdf | 1988-06-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 60 | POWER LEVEL - 060%. ON 6/24/88, AN AGASTAT GP RELAY FAILED WHILE A CONTROL ROOM OPERATOR (CRO) WAS SHIFTING THE FEEDWATER SYSTEM FROM TWO TURBINE-DRIVEN REACTOR FEEDWATER PUMPS (TDRFP) ON THE MASTER CONTROLLER TO THE 'A' TDRFP IN MANUAL AND THE 'B' TDRFP ON THE STARTUP LEVEL CONTROLLER (SULC). AS A RESULT, A 'CONTROL SIGNAL FAILURE' ALARM ANNUNCIATED AND THE SULC WOULD NOT STAY IN AUTOMATIC. THE 'B'' TDRFP FLOW DECREASED. THE CRO ATTEMPTED TO GAIN CONTROL OF REACTOR WATER LEVEL BUT WAS UNSUCCESSFUL. AS A RESULT, WHEN REACTOR WATER LEVEL DECREASED TO THE LEVEL 3 SCRAM SETPOINT, AN AUTOMATIC REACTOR SCRAM OCCURRED. THE ROOT CAUSE OF THIS EVENT IS ATTRIBUTED TO A DESIGN ERROR BY GENERAL ELECTRIC. THE AGASTAT RELAY WAS INAPPROPRIATE FOR THE LOW CURRENT APPLICATION IN THE FEEDWATER CONTROL SYSTEM LOGIC CIRCUITRY. BECAUSE OF THIS MISAPPLICATION, A BUILDUP OF OXIDE OCCURRED ON THE RELAY CONTACTS RESULTING IN THE INTERRUPTION OF THE CIRCUIT AND A LOSS OF THE CONTROL SIGNAL. CORRECTIVE ACTIONS INCLUDE DETERMINING OTHER SUSCEPTIBLE RELAY APPLICATIONS, CLEANING AND TESTING OR REPLACING AND TESTING ALL SUSCEPTIBLE RELAY CONTACTS, AND PERIODICALLY TESTING THE CONTACT RESISTANCE. THIS REPORT INCLUDES INFORMATION REQUIRED UNDER THE PROVISIONS OF 1OCFR21 RELATING TO SIMILAR RELAY DEFECTS IN THE LEAK DETECTION SYSTEM.
461 | 4611988019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611988019R00.pdf | 1988-07-12 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Clinton 1 | B | GE | PO | 100 | POWER LEVEL - 100%. ON 7/12/88, WITH THE PLANT AT 100% REACTOR POWER, ALL THREE CIRCULATING WATER (CW) PUMPS AUTOMATICALLY SHUT DOWN CAUSING A RAPID LOSS OF CONDENSER VACUUM. OPERATORS ATTEMPTED TO RESTART TWO OF THE PUMPS BUT WERE UNSUCCESSFUL. A MANUAL SCRAM WAS INITIATED AND THE MAIN TURBINE WAS MANUALLY TRIPPED. A GROUP 1 CONTAINMENT ISOLATION OCCURRED BECAUSE OF LOW CONDENSER VACUUM. GROUPS 2, 3 AND 20 CONTAINMENT ISOLATIONS OCCURRED BECAUSE OF LOW REACTOR WATER LEVEL. THE SAFETY RELIEF VALVE (SRV) MONITORING TROUBLE ALARM DID NOT ANNUNCIATE WHEN ONE SRV WAS OPEN. THE ROOT CAUSE OF THIS EVENT IS ATTRIBUTED TO THE RANDOM FAILURE OF A CONDENSER PIT HIGH WATER LEVEL SWITCH. INVESTIGATION IDENTIFIED THAT THIS SWITCH TRIPPED WHEN ITS INTERNAL SWITCH ARM FAILED. ANOTHER CONDENSER PIT HIGH WATER LEVEL SWITCH WAS ALREADY IN A TRIPPED CONDITION BECAUSE OF A BENT PLUNGER. THE COMBINATION OF THE TWO TRIPPED SWITCHES RESULTED IN THE SHUTDOWN OF THE CW PUMPS. STRESS FRACTURES RESULTING FROM CORROSION CAUSED THE INTERNAL SWITCH ARM OF THE SWITCH TO FAIL TO THE TRIPPED CONDITION. CORRECTIVE ACTION INCLUDED REPLACING THE SWITCH THAT HAD BROKEN INTERNALS AND STRAIGHTENING THE BENT PLUNGER. ILLINOIS POWER IS EVALUATING OTHER RECOMMENDATIONS THAT MAY REDUCE OR ELIMINATE THE RECURRENCE OF A SIMILAR CW PUMP SHUTDOWN.
461 | 4611988028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611988028R00.pdf | 1988-11-11 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 86 | POWER LEVEL - 086%. ON NOVEMBER 11, 1988, WITH THE PLANT IN MODE 1 (POWER OPERATION), THE 'C' PHASE MAIN POWER TRANSFORMER (MPT 'C') FAILED CAUSING A GENERATOR-TO-TRANSFORMER DIFFERENTIAL RELAY TRIP OF THE MAIN GENERATOR. THE TRIP OF THE MAIN GENERATOR RESULTED IN A TURBINE TRIP AND AN AUTOMATIC REACTOR SCRAM BECAUSE OF THE TURBINE CONTROL VALVE FAST CLOSURE SIGNAL. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO AN INTERNAL FAULT ON THE HIGH VOLTAGE SIDE OF THE TRANSFORMER. THE MPT 'C' WAS REPLACED WITH A SPARE TRANSFORMER OF THE SAME TYPE AND MANUFACTURER. ELECTRICAL TESTS AND OIL SAMPLES OF THE MPT 'A', 'B' AND THE SPARE TRANSFORMER INDICATED ACCEPTABLE INSULATION LEVELS AND DISSOLVED GAS CONTENTS. THE RESULTS FROM THE TESTS AND SAMPLES INDICATE THAT THE THREE MAIN POWER TRANSFORMERS ARE IN SATISFACTORY CONDITION. ILLINOIS POWER WILL PERFORM A VISUAL INSPECTION OF THE MPT 'C' AND PERFORM TESTS TO DETERMINE THE EXTENT OF THE FAULT AND THE SCOPE OF THE NECESSARY REPAIRS. THE EXISTING PREVENTIVE MAINTENANCE REQUIREMENTS FOR THE MAIN POWER TRANSFORMERS WILL BE EVALUATED TO DETERMINE IF CHANGES ARE WARRANTED.
461 | 4611989022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611989022R00.pdf | 1989-05-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 19 | POWER LEVEL - 019%. THIS REPORT DOCUMENTS THE INSERTION OF A MANUAL SCRAM SIGNAL ON MAY 26, 1989 AND AGAIN ON JUNE 1, 1989. ON MAY 26, 1989, REACTOR WATER LEVEL BEGAN DROPPING. THE MOTOR DRIVEN REACTOR FEEDWATER PUMP (MDRFP) REGULATING VALVE IFW004 DID NOT OPEN IN RESPONSE TO THE DECREASING LEVEL. WHEN INDICATED REACTOR WATER LEVEL DROPPED TO APPROXIMATLY TEN INCHES, A MANUAL SCRAM SIGNAL WAS INSERTED. THE FAILURE OF VALVE IFW004 WAS DETERMINED TO BE CAUSED BY A FAULTY SERVO-AMPLIFIER BOARD. THE BOARD WAS REPLACED. THE PLANT ENTERED MODE 2 (STARTUP) IN MAY 27, 1989. ON JUNE 1, 1989, POWER WAS BEING REDUCED IN ORDER TO SHUT THE REACTOR DOWN TO REPAIR THE SEAL ON REACTOR RECIRCULATION PUMP B. AFTER SWITCHING FEEDWATER CONTROL FROM THE TURBINE DRIVEN REACTOR FEEDWATER PUMP TO TH MDRFP, VALVE IFW004 FAILED TO SHUT IN RESPONSE TO ITS CONTROL SIGNAL. REACTOR WATER LEVEL BEGAN IN RAISING. WHEN INDICATED REACTOR WATER LEVEL REACHED FORTY-FIVE INCHES, A MANUAL SCRAM SIGNAL WAS INSERTED. THE CAUSE OF THESE EVENTS WAS THE FAILURE OF VALVE IFW004 TO RESPOND TO ITS CONTROL SIGNAL. TROUBLESHOOTING IDENTIFIED TWO PROBABLE CAUSES: VIBRATIONS CAUSED LOOSE ELECTRICAL CONNECTIONS ON THE SERVO-AMPLIFIER BOARD; SILICON-CONTROLLED RECTIFIERS ON THE BOARD HAD FAILED. THE BOARD HAS BEEN REPLACED AND RELOCATED.
461 | 4611989022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611989022R00.pdf | 1989-06-01 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | SU | 2 | POWER LEVEL - 019%. THIS REPORT DOCUMENTS THE INSERTION OF A MANUAL SCRAM SIGNAL ON MAY 26, 1989 AND AGAIN ON JUNE 1, 1989. ON MAY 26, 1989, REACTOR WATER LEVEL BEGAN DROPPING. THE MOTOR DRIVEN REACTOR FEEDWATER PUMP (MDRFP) REGULATING VALVE IFW004 DID NOT OPEN IN RESPONSE TO THE DECREASING LEVEL. WHEN INDICATED REACTOR WATER LEVEL DROPPED TO APPROXIMATLY TEN INCHES, A MANUAL SCRAM SIGNAL WAS INSERTED. THE FAILURE OF VALVE IFW004 WAS DETERMINED TO BE CAUSED BY A FAULTY SERVO-AMPLIFIER BOARD. THE BOARD WAS REPLACED. THE PLANT ENTERED MODE 2 (STARTUP) IN MAY 27, 1989. ON JUNE 1, 1989, POWER WAS BEING REDUCED IN ORDER TO SHUT THE REACTOR DOWN TO REPAIR THE SEAL ON REACTOR RECIRCULATION PUMP B. AFTER SWITCHING FEEDWATER CONTROL FROM THE TURBINE DRIVEN REACTOR FEEDWATER PUMP TO TH MDRFP, VALVE IFW004 FAILED TO SHUT IN RESPONSE TO ITS CONTROL SIGNAL. REACTOR WATER LEVEL BEGAN IN RAISING. WHEN INDICATED REACTOR WATER LEVEL REACHED FORTY-FIVE INCHES, A MANUAL SCRAM SIGNAL WAS INSERTED. THE CAUSE OF THESE EVENTS WAS THE FAILURE OF VALVE IFW004 TO RESPOND TO ITS CONTROL SIGNAL. TROUBLESHOOTING IDENTIFIED TWO PROBABLE CAUSES: VIBRATIONS CAUSED LOOSE ELECTRICAL CONNECTIONS ON THE SERVO-AMPLIFIER BOARD; SILICON-CONTROLLED RECTIFIERS ON THE BOARD HAD FAILED. THE BOARD HAS BEEN REPLACED AND RELOCATED.
461 | 4611989028 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611989028R00.pdf | 1989-06-28 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 100 | POWER LEVEL - 100%. ON JUNE 28, 1989, WITH THE PLANT IN MODE 1 (POWER OPERATION), THE 'C' PHASE MAIN POWER TRANSFORMER (MPT) SUDDEN PRESSURE SENSOR RELAY MALFUNCTIONED CAUSING A TRIP OF THE MAIN GENERATOR. THE TRIP OF THE MAIN GENERATOR RESULTED IN A TURBINE TRIP AND AN AUTOMATIC REACTOR SCRAM BECAUSE OF THE TURBINE CONTROL VALVE FAST CLOSURE SIGNAL. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO A SPURIOUS SIGNAL FROM THE MALFUNCTIONING SUDDEN PRESSURE SENSOR RELAY. THE SUDDEN PRESSURE SENSOR RELAY MALFUNCTIONED BECAUSE OF INTERNAL CORROSION RESULTING FROM WATER INTRUSION INTO THE RELAY. THE SUDDEN PRESSURE SENSOR RELAY WAS REPLACED WITH A SENSOR RELAY WHICH HAS AN AIR VENT TO PREVENT MOISTURE BUILDUP INSIDE THE RELAY. THE SUDDEN PRESSURE SENSOR RELAYS WERE REPLACED IN THE OTHER TWO MAIN POWER TRANSFORMERS AND ALSO IN THE RESERVE AUXILIARY TRANSFORMER AND THE EMERGENCY RESERVE AUXILIARY TRANSFORMER.
461 | 4611989029 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611989029R00.pdf | 1989-07-14 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Clinton 1 | B | GE | PO | 39 | POWER LEVEL - 039%. ON JULY 14, 1989, WITH THE PLANT AT THIRTY-NINE PERCENT REACTOR POWER, A MANUAL REACTOR SCRAM WAS INITIATED IN ANTICIPATION OF AN AUTOMATIC SCRAM THAT WAS IMMINENT BECAUSE MAIN CONDENSER VACUUM WAS DECREASING. (A LOSS OF MAIN CONDENSER VACUUM CAUSES A TURBINE TRIP AND RESULTS IN AN AUTOMATIC REACTOR SCRAM.) THE REACTOR HAD BEEN OPERATING AT 100 PERCENT REACTOR POWER WHEN CONDENSER VACUUM BEGAN DECREASING. AFTER THE REACTOR SCRAM, GROUPS 2, 3 AND 20 AUTOMATIC CONTAINMENT ISOLATIONS OCCURRED BECAUSE OF LOW REACTOR VESSEL WATER LEVEL. GROUP 1 CONTAINMENT ISOLATION VALVES WERE MANUALLY CLOSED IN ANTICIPATION OF THE AUTOMATIC ISOLATION THAT WOULD OCCUR BECAUSE OF LOW CONDENSER VACUUM. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO A MECHANICAL FAILURE OF THE RUBBER EXPANSION JOINT LOCATED BETWEEN THE 'A' LOW PRESSURE TURBINE AND THE MAIN CONDENSER. THE EXPANSION JOINT FAILED BECAUSE OF AGE, OVERTORQUING OF THE ATTACHMENT NUTS OF THE EXPANSION JOINT CLAMP ASSEMBLY, AND STEAM EXPOSURE THAT RESULTED FROM A DETACHED PROTECTIVE COVER. CORRECTIVE ACTION FOR THIS EVENT INCLUDED REPLACING THE RUBBER EXPANSION JOINTS BETWEEN BOTH THE 'A' AND 'B' LOW PRESSURE TURBINES AND THE MAIN CONDENSER, TORQUING THE ATTACHMENT NUTS OF THE CLAMP ASSEMBLY TO VENDOR RECOMMENDED VALUES, AND REINFORCING THE WELDS OF THE PROTECTIVE COVER.
461 | 4611989032 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611989032R00.pdf | 1989-07-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 25 | POWER LEVEL - 025%. ON JULY 31, 1989, WITH THE PLANT AT APPROXIMATELY 25 PERCENT POWER, OPERATORS INITIATED A MANUAL SCRAM OF THE REACTOR. PRIOR TO THE SCRAMS THE PLANT HAD BEEN OPERATING AT 100 PERCENT POWER WHEN DIFFICULTIES WERE EXPERIENCED WITH THE MOISTURE SEPARATOR REHEATER (MSR) AND THE HIGH PRESSURE FEEDWATER HEATER SYSTEMS AND THEIR VENT AND DRAIN SYSTEM. IN RESPONSE TO THESE DIFFICULTIES, OPERATORS BEGAN REDUCING POWER TO REMOVE THE MSRS FROM SERVICE. AT THIS POINT OPERATORS NOTED AN INCREASE IN WATER LEVEL IN THE REHEATER DRAIN TANK, AN INCREASE IN OFF-GAS SYSTEM FLOW, AND A DECREASE IN THE MAIN CONDENSER VACUUM. REACTOR POWER. AT APPROXIMATELY TWENTY-FIVE PERCENT REACTOR POWER, WHILE REMOVING ONE OF THE TURBINE DRIVEN REACTOR FEEDWATER PUMPS FROM SERVICE, AN OPERATOR FAILED TO MATCH THE MANUAL FEEDWATER CONTROL TO THE AUTOMATIC FEEDWATER CONTROL PRIOR TO TRANSFERRING THE PUMP TO MANUAL. THIS CAUSED REACTOR WATER LEVEL TO INCREASE AND APPROACH THE HIGH WATER LEVEL SCRAM SETPOINT THEREFORE. OPERATORS INITIATED A MANUAL SCRAM. THE CAUSE OF THIS EVENT IS ATTRIBUTED TO OPERATOR ERROR DURING THE TRANSFER OF FEEDWATER PUMP CONTROL. BECAUSE THE OPERATOR RECOGNIZED HIS ERROR AND IDENTIFIED IT TO HIS SUPERVISION, NO CORRECTIVE ACTION IS REQUIRED.
461 | 4611990012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611990012R00.pdf | 1990-05-17 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 43 | On May 17, 1990, with the plant in POWER OPERATION at 43 percent reactor power, and both reactor recirculation (RR) pumps in fast speed, reactor feedwater system (FW) flow channel "B" failed and caused instrumentation to incorrectly sense total FW flow as low. As a result of this, the logic initiated an automatic transfer of the "A" and "B" RR pumps to slow speed. In response to the RR pump transfers, the control room operator initiated a manual reactor scram in accordance with the off-normal procedure. Additionally, groups 2, 3 and 20 containment isolation valves actuated as a reactor vessel water low-level trip occurred. Troubleshooting determined that a power converter for the FW control system failed due to normal end of life and caused the "B" FW flow channel to fail. The cause of this event is attributed to the normal end-of-life failure of the power converter. Corrective actions included: replacing the specific power converter and replacing another power converter of the same model; initiating a Preventive Maintenance (PM) task to periodically replace the power converter and another converter of the same model; and determining if other FW control system power supplies/converters may need PM tasks for periodic replacement.
461 | 4611990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611990013R00.pdf | 1990-07-09 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 91 | On July 9, 1990, with the plant in POWER OPERATION at 91 percent reactor power, main generator overvoltage/hertz protection relay 59/81-1 actuated. After a designed 45-second time delay, the main turbine generator tripped via turbine control valve fast closure which caused an automatic reactor scram. Additionally, Groups 2, 3, and 20 containment isolation valves actuated as a reactor vessel water low-level trip occurred. Investigation determined that relay 59/81-1 had actuated prior to exceeding its design setpoint because it was out of calibration. The cause of the relay being out of calibration cannot be determined. Probable causes are personnel error in reading the test instrument during calibration and/or test instrument error during calibration caused by a fluctuating voltage source. Corrective actions include: recalibrating two relays and verifying setpoints of a sample of other relays calibrated during the same period; issuing detailed procedures for calibrating - protective voltage relays; investigating qualifying a Clinton Power Station technician to perform relay testing; recently purchasing new digital test equipment; and briefing each operations crew on generator limitations and abnormal voltages.
461 | 4611991006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611991006R00.pdf | 1991-11-16 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Clinton 1 | B | GE | PO | 27 | On November 16, 1991, with the plant in Power Operation, a rapid plant shutdown with a manual SCRAM was initiated due to decreasing condenser vacuum. The decreasing vacuum occurred during a plant down-power to repair leaking condenser tubes. At 0358 hours, with reactor power decreased to 65 percent, the 'A' waterbox was isolated. Immediately, condenser vacuum decreased and condensate temperature increased, as expected. Condenser suction isolation valve 1CA001A was left open while the waterbox was draining. Condenser vacuum and condensate temperature failed to stabilize. Reactor power was decreased in an effort to maintain vacuum. At 0645 hours, with the reactor at 34 percent reactor power and with condenser vacuum decreasing below 25 inches mercury vacuum, a rapid plant shutdown was initiated followed by a manual SCRAM. The cause of this event was attributed to a combined effect of degraded condenser performance and valve 1CA001A positioning which resulted in a failure to isolate the air removal pathway ultimately causing a loss of the intercondenser loop seal. Corrective actions for the event include a revision to plant procedures to clarify reactor power limitations prior to isolating a condenser waterbox and to clarify positioning of valve 1CA001A/B prior to draining a waterbox. The main condenser will be mechanically cleaned during the third refueling outage.
461 | 4611991008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611991008R00.pdf | 1991-12-22 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 63 | On December 22, 1991, with the plant in POWER OPERATION, a manual SCRAM was initiated due to operation in the restricted zone of the thermal power versus core flow map of Technical Specification 3.4.1.3. While the control room operators conducted a scheduled power reduction, the "B" Reactor Recirculation (RR) flow control valve (FCV) started to operate erratically. Control room operators, attempting to stop the erratic operation, hydraulically locked out the "B" RR FCV. The "B" RR FCV continued to operate erratically and then suddenly closed enough to cause core flow to drop into the restricted zone. The control room operator immediately initiated a reactor SCRAM in accordance with plant procedure 3005.01, "Unit Power Changes". No reactor power oscillations were observed. The causes of this event are attributed to the failure of the "B" RR FCV position feedback loop and to internal leakage of the hydraulic valves on the hydraulic power unit. Corrective actions for this event include replacing the RR FCV position and velocity transducers, replacing the leaking hydraulic valves, examining and testing the feedback sensor and associated lead, and determining if any long-term corrective actions are appropriate.
461 | 4611992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611992001R00.pdf | 1992-01-04 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 99 | On January 4, 1992, with the plant in POWER OPERATION at 99 percent reactor power, the "B" phase main power transformer (MPT 1B) failed due to an internal fault. The transformer failure resulted in a turbine generator trip and an automatic reactor SCRAM. The automatic reactor scram occurred due to the turbine control valve fast closure. Within seconds of the SCRAM, the turbine driven reactor feed pump (TDRFP) 1B tripped. Additionally, after the reactor SCRAM was reset, a SCRAM discharge volume (SDV) drain valve failed to reopen and a SDV vent valve only opened to an intermediate position. The cause of the SCRAM was an internal fault in MPT 1B. The cause of the TDRFP 1B trip was attributed to a worn thrust bearing, and the cause of the SDV vent and drain valves failing to reopen was attributed to air leakage past the seat of a three- way solenoid valve. Corrective actions for this event include replacing the failed MPT with a spare MPT, restoring the TDRFP 1B thrust bearing clearance to original manufacturer specifications, and rebuilding the three-way solenoid valve.
461 | 4611992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611992002R01.pdf | 1992-02-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 72 | With the plant at 72 percent reactor power, an automatic reactor scram occurred due to low reactor water level when the 'B' Turbine Driven Reactor Feed Pump (TDRFP) control valve (CV) failed to properly control TDRFP speed and, consequently, feedwater flow. During a transfer of reactor feedwater level control from the 'A' channel to the 'B' channel, the 'B' TDRFP controller signaled the 'B' TDRFP CV to open. The TDRFP CV locked up causing the 'B' TDRFP to pick up more of the controller demand to the vessel than the 'A' TDRFP. After the TDRFP CV locked up, the controller demand went to a minimum, giving the TDRFP CV a full-close signal. While reducing reactor power and attempting to manually remove the 'B' TDRFP from service, the TDRFP CV closed causing the TDRFP speed to decrease and creating a low reactor water level condition which resulted in an automatic reactor scram. The cause of this event is attributed to manufacturing deficiencies compounded by inadequate procedural guidance for maintaining the TDRFP turbine actuating linkages. <br /><br /> Corrective actions include replacing worn or damaged components; revising procedures to include more detailed instructions; initiating a preventive maintenance task to periodically inspect the linkages; training maintenance personnel on lessons learned; and monitoring TDRFP performance.
461 | 4611992010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611992010R00.pdf | 1992-11-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 75 | With the plant at 75 percent reactor power, in accordance with plant procedures, a manual reactor SCRAM was initiated due to operation within the restricted operating region of the thermal power versus core flow operating map. Entry into the restricted region was due to an automatic fast closure (runback) of both reactor recirculation (RR) flow control valves (FCVs). The fast closure was initiated by the presence of a trip signal for the 'A' Turbine Driven Reactor Feed Pump (TDRFP) and a decrease in reactor vessel water level to the low level alarm trip setpoint (Level 4). The 'A' TDRFP was out of service for preplanned testing and inspection. Vessel water level began to decrease when the 'B' TDRFP minimum flow valve failed open due to a broken instrument air supply line. The rigid copper tubing instrument air supply line failed due to stress caused by long term exposure to normal system vibration. Corrective actions included replacing the rigid copper tubing air supply line on both the 'B' and 'A' TDRFP minimum flow valves with flexible stainless steel hoses.
461 | 4611993006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611993006R00.pdf | 1993-12-06 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | SU | 5 | With the plant in STARTUP at about five percent reactor power, one turbine-driven reactor feed pump (TDRFP) uncoupled for an overspeed test and the motor-driven reactor feed pump (MDRFP) out of service to repair an oil leak, the only operating TDRFP tripped. Attempts to reset and restart the TDRFP were unsuccessful. Reactor water level dropped, and operators initiated a manual reactor SCRAM prior to the low reactor water level trip. Three groups of containment isolation valves received signals to close when water level dropped to the low reactor water level trip. Water level dropped to minus 19 inches on the wide-range level instrument before being restored. The most probable cause of the TDRFP trips were momentary rotor thrusts that activated the turbine thrust bearing wear detection trip system. Contributing to the cause of this event were operating the TDRFP at a continuous low-power/low-flow condition using high pressure steam, and continuing the plant startup after taking the MDRFP out of service. Corrective actions include: a review of the event to identify possible improvements to the reliability of the thrust wear detection trip system; continued evaluation of the event and incorporation of the lessons learned into the appropriate procedures to provide guidance on operating the plant at low-power/low-flow conditions; and operator review of the event.
461 | 4611993007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611993007R00.pdf | 1993-12-20 | QL7 | Degraded condenser vacuum | [45 empty] | Clinton 1 | B | GE | PO | 60 | With the plant at 100 percent reactor power, operators were attempting to place a second Steam Jet Air Ejector (SJAE) in service so its new steam flow pressure controller could be tuned. When the main steam inlet isolation valve was opened, a high steam flow rate saturated the offgas system desiccant dryer with moisture and iced up the charcoal adsorber gas cooler, causing a loss of the capability to remove non-combustibles from the condenser. This led to the loss of condenser vacuum and a manual reactor scram at sixty percent reactor power. In preparing to put the SJAE in service, the operator verified the steam flow pressure controller setpoint dial was set at the zero position as directed by the procedure. The steam flow control valve was believed to be fully closed, which would have prevented the high steam flow when the isolation valve was opened. The cause of this event is a lack of operators' full understanding of the steam flow pressure controller design and how it relates to operating the control valve. Corrective action for the event includes revising the system operating procedure to identify the proper operation of the controller and training operators on that operation.
461 | 4611995001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611995001R00.pdf | 1995-01-05 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 79 | With the plant at 100 percent reactor Power, operators decided to reduce power to 53 percent of rated t power (RTP) and isolate the B low pressure (LP) feedwater heater string to correct degradation related to suspected tube leaks, in the 5B LP heater. With reactor power at 70 percent RTP and extraction steam to the B heater string secured, operators began to slowly open the (LP) heater string bypass valve. While opening the valve, water levels in the 6A high pressure heater and the A side reheater drain tank began to oscillate to off-scale high causing the 6A heater to isolate from extraction steam. Feedwater temperature decreased 50 degrees and reactor power increased to 79 percent RTP. In response to these conditions, the shift supervisor ordered the initiation of a manual scram. The cause of this event is attributed to insufficient understanding of heater train operation in an abnormal condition. Personnel did not fully understand the impact that opening the bypass valve would have on the 6A heater operation. Corrective action for this event includes plugging 5B feedwater heater tubes, revising the system operating procedure to incorporate additional guidance for removing a heater string from service and restoring it, and inspecting tubes in the next refueling outage.
461 | 4611995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611995005R00.pdf | 1995-05-15 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 100 | On May 15, 1995, the plant was in POWER OPERATION at about 100% reactor power. Operators were adjusting reactor core flow using the 'B' reactor recirculation flow control valve when the hydraulic power unit locked up, which hydraulically locks the flow control valve, and both reactor recirculation pumps tripped from fast to slow speed. The reduction in core flow caused the plant to enter the restricted zone of the thermal power versus core flow operating map. Plant procedures required the operators to initiate a manual SCRAM when the restricted zone was entered. The cause of the hydraulic power unit locking up and the pump trip from fast to slow speed was a fault in one of the reactor recirculation control panel +/- 15 volt Direct Current (DC) field bus bars. This fault created a false indication of low differential temperature between the steam dome and reactor recirculation pump suction which causes the pumps to trip from fast to slow speed following a time delay. The fault was due to a protrusion or 'spur' on the +/- 15 volt DC bus bar. The 'spur' was created during the manufacturing process and propagated through the insulating paper from the - 15 volt DC portion of the field bus and shorted with the + 15 volt DC portion of the bus bar. The nest assembly, which contained the faulty field bus bar, was replaced with a spare nest assembly.
461 | 4611996004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611996004R00.pdf | 1996-04-09 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Clinton 1 | B | GE | PO | 100 | On April 9, 1996, utility electrical maintenance personnel, with the support of a representative of the equipment vendor, were performing a preventive maintenance task on gas circuit breaker GCB 4522 in the Clinton Power Station (CPS) switchyard. The plant was operating at about 100 percent reactor power when the reserve auxiliary transformer (RAT) lost power due to the work being performed in the switchyard. The loss of power to the RAT caused a momentary loss of power to the turbine building main steam tunnel high temperature instruments. This caused the main steam line isolation valves to close which resulted in an automatic reactor scram. The cause of this event was attributed to inadequate job preparation brought on by a false sense of security on the part of the individuals involved with preventive maintenance task PEMSYM004. Plant procedures will be revised to more clearly define when a system impact matrix and work plan is required. Also, a briefing of applicable personnel will be conducted to reinforce what situations require a system impact matrix.
461 | 4611996008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611996008R01.pdf | 1996-06-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Clinton 1 | B | GE | PO | 100 | On June 13, 1996, the plant was in Mode 1 at about 100% reactor power. Control and instrumentation technicians were performing a calibration of the feedwater flow measurement instrument loop as part of a preventive maintenance task. The control and instrumentation technician was required by the preventive maintenance task to determine the voltage on a termination on a trip unit. When the technician attempted to take the voltage the two wire leads connected to the terminal separated, interrupting power to two trip units, which caused the reactor recirculation pumps to shift from fast to Blow speed. The resulting reduction in core flow caused the plant to enter the restricted zone of the reactor thermal power versus core flow operating map. The exact cause of the loose wire could not be determined. Contributing to this event was the fact that it was difficult to attach the electrical meter to the point where it was required to take the voltage reading. Corrective actions for this event were to revise the preventive maintenance work document to use a common point as reference when verifying the change of state of the contacts, and a briefing was held with electrical and control and instrumentation technicians on this event.
461 | 4611996010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611996010R01.pdf | 1996-09-06 | G1 | Very Small LOCA or Leak | [6 empty] | X | [18 empty] | X | [19 empty] | Clinton 1 | B | GE | PO | 58 | The plant was in POWER OPERATION and operators were preparing to shut down the "B" reactor recirculation (RR) pump, isolate the "B" RR loop, and operate the plant with a single RR loop to reduce unidentified reactor coolant system (RCS) leakage. A degrading RR pump seal was suspected to be the source of an increasing unidentified RCS leakage rate into the drywell floor drain sump. In the process of isolating the loop, the leakage rate increased above the Technical Specification (TS) limit and the seal experienced a rapid failure. operators attempted to control the resulting increased leakage rate to continue plant operation but the leakage rate could not be reduced to the TS limits within the Action completion time. A plant shutdown was completed per the TS Action. The event was initiated by the failure of the "B" RR pump seal. Corrective action for this event included revising procedures to require plant shutdown in response to high or low seal pressures, and valid alarms for high seal leakage and high or low seal staging flow; replacing the seal that failed; and replacing the existing seal design with an improved design.
461 | 4611999008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4611999008R00.pdf | 1999-05-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Clinton 1 | B | GE | SU | 4 | On May 14, 1999, the reactor was in Mode 2 operation with feedwater being supplied to the reactor vessel by the Motor Driven Reactor Feed Pump (MDRFP). At approximately 0723 hours the MDRFP flow control valve, 1FW004, failed causing a reactor vessel level transient. Control room operators took manual control of feedwater flow but were unable to maintain reactor vessel level. Reactor vessel level increased to the level 8 trip setpoint and the MDRFP tripped on high vessel water level. A manual scram was initiated and all control rods fully inserted. The cause for this event was failure of the 1FW004 valve's hydraulic control system. This failure was due to inadequate written guidance used when performing maintenance on the valve earlier in the year. The corrective actions include: fixing the discrepancies that caused the 1FW004 valve to fail; replacing the hydraulic system fluid with new, filtered fluid; and developing a maintenance procedure for performing maintenance on the valve which will include the lessons learned from this investigation.
461 | 4612000001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612000001R00.pdf | 2000-05-17 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [7 empty] | X |  |  | X |  |  | X | [22 empty] | X | X |  |  |  | X | Clinton 1 | B | GE | PO | 100 | On May 17, 2000, the plant was in Mode 1, at approximately 100 percent power. Functional testing of over current relays for the reserve feeder breaker to the 4160 Volt (V) 1B Bus (non-safety) was in progress. While inputting a simulated over current condition to test the over current relays on the reserve feeder breaker, the main feeder breaker to the 4160 V 1B Bus tripped unexpectedly resulting in a loss of power to the 4160 V 1B Bus. The resulting loss of power caused a loss of feedwater flow and reactor vessel level transient. In response to the level transient, a manual reactor scram was initiated and the reactor shut down. The cause of this event was incorrect labeling of a test switch on the 4160 V 1B Bus. The corrective actions for this event include performing walkdowns of other electrical busses to identify labeling problems, briefing maintenance personnel on this event, and incorporating a Labeling Validation Form in Electrical Maintenance work packages.
461 | 4612000007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612000007R00.pdf | 2000-12-18 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Clinton 1 | B | GE | PO | 100 | A Containment Main Steam Line isolation (Group 1) and subsequent reactor scram from 100 percent reactor power occurred during a Division (Div) 2 Main Steam Line tunnel ambient temperature channel functional test. The logic for the isolation was completed when a Div 2 channel functional test signal combined with a pre-existing Div 1 trip signal. The Div 1 trip signal was a result of a circuit card failure and was unknown at the time of the test. The isolation initiated a Reactor Scram. During recovery from the event, an additional scram occurred on low reactor water level. While reestablishing the main condenser as a heat sink, a deficient procedure lacked provisions for opening both the inboard and outboard main steam isolation valves and an at risk revision of the procedure was initiated. During the revision process, poor command and control allowed reactor pressure to increase and water level to decrease to the scram setpoint. The cause of the Group 1 and scram was inadequate indication/annunciation for the technician to detect a pre-existing fault in an alternate channel. The cause of the additional scram was poor command and control. Corrective action for this event includes changing circuit design, revising procedures, counseling the main control room crew, providing remedial training, and developing a comprehensive corrective action plan to address the operator performance issues.
461 | 4612001002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612001002R00.pdf | 2001-02-04 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 96 | On February 4, 2001, Clinton Power Station (CPS) was in Mode 1 at approximately 96 percent power. During performance of turbine valve surveillance testing of the #3 Combined Intermediate Valve, an emergency trip system (ETS) low fluid pressure transient occurred as sensed by the control fast closure pressure switches resulting in an automatic scram. The cause for the event was determined to be an inadequate process for the review and approval of the CPS response to General Electric Technical Information Letter (TIL) 1212-2. This TIL contains a recommendation that a flow restricting orifice be installed in the P-Port of the fast acting solenoid valves in the turbine electrohydraulic control system for main turbine stop valves, control valves, and combined intermediate valves. Installation of the orifice prevents random reactor scrams on low ETS pressure during valve testing. The review of this TIL did not identify that the recommended orifice was not installed in the P-Port of the FASV for the #3 CIV. The corrective actions for this event include installation of the recommended orifices, revising the Operating Experience program procedure, providing training, and reviewing the responses to other operating experience documents.
461 | 4612001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612001003R00.pdf | 2001-07-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 100 | Instrument Maintenance (IM) technicians were performing a quarterly channel functional test on the B Reactor Feedwater level channel with the A reactor feedwater level channel in service. During the surveillance test, the technicians incorrectly performed a step in the procedure and lifted the Channel B-Device GT leads. Per procedure, the step for lifting the leads is only performed if a high reactor water level condition exists, and no such condition existed. Lifting the leads caused a loss of the reactor vessel level input signal for feedwater control, resulting in an immediate demand by the Master Level Controller. A feedwater transient began that resulted in reactor water level rising above the High Level 8 trip initiating an automatic reactor scram. The cause of this event was human error. The technicians involved did not follow the procedure and performed a step not applicable to current plant conditions. Corrective actions for this event include personnel actions for the technicians involved in the event, revising the surveillance procedure and reviewing other IM procedures, issuing a risk review and screening procedure, training on various topics, and increasing management oversight on backshifts.
461 | 4612002002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612002002R00.pdf | 2002-05-13 | QP5 | Excessive Feedwater Flow | [45 empty] | Clinton 1 | B | GE | PO | 86 | Extended Power Uprate testing was in progress with the 'A' Turbine-Driven Reactor Feed Pump (TDRFP) in manual on its flow controller and the 'B' TDRFP in automatic on the Startup Level Controller (SLC). When a planned reactor pressure vessel (RPV) water level increase from 32 to 38 inches was performed for startup testing using the SLC, water level increased but the Feedwater Level Control System (FLCS) did not adjust to stabilize water level. The operator took manual control of the SLC and lowered the demand signal to the 'B' TDRFP, but level continued to rise and an automatic reactor scram occurred on high RPV water level before insertion of a manual scram. The 'B' TDRFP did not respond to the lowered demand signal due to a lock-up of the TDRFP from mechanical binding. The cause of this event is an inadequate preventive maintenance program for the Feedwater System that did not identify the TDRFP limit switch guide as a critical component and establish appropriate preventive maintenance to prevent its failure. Corrective action includes developing a preventive maintenance task to inspect, clean and lubricate the limit switch guide mechanism periodically; replacing the 'B' TDRFP horizontal linkage rod, and reviewing the preventive maintenance program for the Feedwater System to assure critical components have adequate preventive maintenance tasks assigned.
461 | 4612002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612002003R00.pdf | 2002-07-04 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 95 | On July 4 the sudden pressure alarm for the `B' Main Power Transformer (MPT) actuated in the Main Control Room and at the same time the reactor automatically scrammed from 95 percent reactor power. The sudden pressure alarm was initiated by a malfunction of the sudden pressure relay (SPR). The SPR initiated a Generator trip and lockout. The Generator trip caused a Main Turbine trip and Turbine Control Valve fast closure, resulting in the reactor scram. The SPR trip also initiated the `B' MPT deluge system, and the fire pumps automatically started as expected. Operators entered Emergency Operating Procedures due to an expected low reactor water level transient. The root cause for the reactor scram was a latent defect in the bimetal of the SPR control orifice that likely occurred during the manufacturing process and resulted in a false actuation of the SPR. Corrective action for this event includes replacing the deficient `B' MPT relay, testing the MPT SPRs for proper operation, and implementing a design change to modify the SPR trip logic.
461 | 4612003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612003002R00.pdf | 2003-04-11 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 33 | On April 11, 2003, with the plant in Mode 1 (Power Operation) while lowering reactor power in preparation for maintenance outage C1M13, the reactor was manually scrammed from 33 percent power in response to vibration levels on the Main Turbine approaching the automatic trip setpoint. The Low Pressure Turbine vibrations were caused by development of a minor rub between the rotating and stationary components as a result of the temperature change induced on the Low Pressure Turbine when the Moisture Separator Reheaters (MSRs) were removed from service. The root cause of the event-was that operating procedures were deficient in providing sufficient operating restrictions of the new monoblock turbine rotor due to inadequate vendor guidance. Corrective actions to prevent recurrence include revisions to plant procedures and the turbine vendor manual to incorporate more restrictive heat up and cool down ramp rates. Additional corrective actions identified include providing expectations in the design modification process to require independent operating experience reviews during the design phase.
461 | 4612003003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612003003R01.pdf | 2003-12-02 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Clinton 1 | B | GE | PO | 88 | On December 2, 2003, at approximately 1700 hours, the reactor was manually scrammed from 88 percent power in response to low feedwater pump suction pressure and reactor pressure vessel (RPV) water level trending downward toward the RPV Low Water Level - Level 3 automatic scram setpoint. Initiating the event was a loss of power to the 480 Volt Unit Substation 1I (1AP19E) causing the 'B' turbine driven reactor feed pump (TDRFP) minimum flow valve to fail open. This resulted in a low pump suction pressure and a trip of both TDRFPs. The motor-driven reactor feed pump (MDRFP) automatically started to control water level and pressure. The cause of the 480 Volt Unit Substation 1I to trip was a lack of overload circuit protection (i.e., fuse protection) for a branch circuit due to a design error.A second event occurred on December 2, 2003 at approximately 1937 hours when a RPV Low Water Level - Level 3 Reactor Protection System (RPS) actuation occurred during the transfer of reactor coolant makeup from the MDRFP to the condensate/condensate booster pumps. The RPS actuation'(scram) was caused by the RPV water level dropping at a faster rate than anticipated by the operating crew. The MDRFP was restarted and water level was quickly recovered. This event was caused by less than adequate operating crew response in shutting down the MDRFP to reduce reactor pressure.The deficient circuit will remain removed from service until an engineering change to modify the circuit for over load protection is installed. For the second event, operations crews will be trained on the event in simulator training to emphasize the crew's response to challenges, including reactor water level responses to pressure reduction without high pressure feed injection available.
461 | 4612004001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612004001R01.pdf | 2004-03-22 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 33 | On March 22, 2004, at about 1931 hours, an automatic reactor scram occurred with the plant at 93 percent power. Operators received a trouble alarm in the Main Control Room for the Hydrogen and Stator Cooling Cabinet followed by a Main Generator neutral over-voltage trip and Generator Trip System 2 Lockout. The Generator trip caused a Main Turbine trip and Turbine Control Valve fast closure, resulting in an automatic reactor scram. All control rods fully inserted. Following the reactor scram, reactor water level dropped, as expected, to the Low Level 3 trip setpoint, initiating the Reactor Protection System. Operators entered Emergency Operating Procedures due to the low reactor water level transient. The root cause investigation determined that a failed Partial Discharge Analysis (PDA) system cable and/or a piece of aluminum laminate from a degraded bus conductor expansion joint contacted the grounded bus duct causing a ground fault and subsequent generator neutral over-voltage trip. The failures of the PDA cable and the aluminum laminate were both due to mechanical fatigue caused by an increase in design air flow rate in the bus duct implemented during the Spring 2004 refueling outage. Corrective actions include implementing a design change for the bus duct expansion joint that is not susceptible to fatigue failure.
461 | 4612004003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612004003R00.pdf | 2004-07-13 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 95 | A suspected lightning strike to the A Phase of the 345 Kilovolt (kV) line 4.5miles from the station resulted in a generator trip and automatic reactor scram. The Main Generator Trip System 2 received an instantaneous neutral phase over-current trip on the station ITH Relay. The ITH relay monitors the difference between the current in the Main Power Transformer (MPT) neutral legs and the sum of the 345kV Main Power Output breakers phase currents; the purpose of this scheme is to provide protection for the high voltage leads for a ground fault. All control rods fully inserted. The cause of the event was a legacy design vulnerability that was unknown to the Station. The design of the protective relaying system and breaker trip logic for the MPTs had some weaknesses since current transformers in the circuit had potential saturation issues. The potential for current transformer saturation along with the speed of the ITH relay made the circuit vulnerable to false tripping. The magnitude of the fault, grid conditions (load and reactance) at the time of the fault, and the timing of the fault allowed the vulnerabilities to result in an unexpected reactor trip. The corrective action was a design change to replace the ITH relay with a relay that has a time delay in the tripping circuit to permit proper sequencing of the protective relaying during transmission line faults.
461 | 4612006001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612006001R00.pdf | 2006-03-20 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 96 | On 3/20/06, at about 0450 hours with the plant at about 96 percent power, an open circuit in the C Phase neutral Current Transformer (CT) of the Main Generator output caused the Generator Differential Overcurrent 87-G1 relay to trip due to a sensed current imbalance. Actuation of the 87-G1 relay resulted in a Generator Trip / Lockout and an automatic Turbine Electro Hydraulic Control (EHC) trip. The Turbine EHC trip caused a Turbine Control Valve fast closure and a Reactor Protection System signal for the automatic scram. A loose terminal screw on the CT lead wire caused the open circuit, resulting in high resistance and overheating that melted the wire. The cause of this event was inadequate workmanship that occurred during Generator High-Potential testing, as a result of a process weakness. The inadequate workmanship most likely occurred during the eighth refueling outage. Terminal screws at the C phase CT were most likely loosened to install test leads and not adequately retightened following removal of the test leads, resulting in a failure of the wire termination. Corrective action includes adding process controls to ensure that lifted and landed leads will be adequately tightened in the future.
461 | 4612006003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612006003R00.pdf | 2006-08-27 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Clinton 1 | B | GE | PO | 97 | On 8/27/06, the station experienced a momentary loss of safety-related Division 4 Nuclear System Protection System (NSPS) inverter resulting in an automatic reactor scram on high reactor water level. The event cycled the safety-related 120 Volts Alternating Current (VAC) NSPS bus causing the Division 3 emergency diesel generator, the Division 3 shutdown service water system, and the High Pressure Core Spray System (HPCS) to automatically start, and HPCS to inject water into the reactor vessel. The loss of inverter also caused the "A" Reactor Recirculation (RR) pump to trip. The loss of the RR pump combined with the HPCS injection caused reactor vessel water level to increase to the high reactor water level trip. The cause of the momentary loss of the inverter was an intermittent failure of an inadequate solder joint in the Division 4 NSPS inverter. The solder joint is located on the backplane circuit board, and is a common node for both inverter and bypass transformer sources of power. Failure of the connection resulted in a loss of power to the safety-related 120 VAC bus. Corrective action includes replacement of the circuit board in the Division 4 inverter and the same board in the Division 3 inverter, and revising the purchasing description for the backplane circuit boards to disallow boards of this vintage. This event is reportable under 10CFR 21.
461 | 4612008001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612008001R02.pdf | 2008-02-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Clinton 1 | B | GE | PO | 95 | On 2/10/08 the 'B' Reactor Recirculation (RR) Pump unexpectedly tripped from fast speed to off. Reactor Pressure Vessel (RPV) water level increased to the automatic scram setpoint. Operators placed the Reactor Mode Switch in Shutdown but the automatic scram on high RPV water level occurred approximately one second prior. The operator reported reactor power at zero percent and control rods status, but had difficulty verifying four control rods due to anomalous indication on the full core display. When RPV water level decreased below the low RPV water level setpoint, operators entered Emergency Operating Procedure (EOP) 1, RPV Level Control, and then transitioned to EOP 1A, ATWS RPV Level Control, in response to the anomalous position indication of four control rods. During control rod position verification by other crewmembers, all control rods were verified to have fully inserted on the initial scram. The causes of this event are low risk perception in investigating and resolving an unexplained source of voltage in a circuit, and insufficient technical rigor in not specifying tuning of feedwater level control system (FWLCS) following a previous scram. Corrective action includes conducting briefings on the root cause of this event emphasizing risk, consequences and application of appropriate human performance fundamentals, tuning the FWLCS, and revising procedures.
461 | 4612009005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612009005R01.pdf | 2009-10-15 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 96 | On 10/15/09 the 'B' Reactor Recirculation (RR) Pump unexpectedly tripped from fast speed to off. Reactor Pressure Vessel (RPV) water level increased and operators placed the Reactor Mode Switch in Shutdown at a predetermined level prior to the high reactor vessel water level automatic scram setpoint. All control rods fully inserted. When RPV water level decreased below the low RPV water level setpoint, operators entered Emergency Operating Procedure (EOP) 1, RPV Level Control. The cause of this event is attributed to failure of the 'B' RR pump motor. Vendor failure analysis concluded that the failure in the RR pump motor was a B-Phase turn-to-turn fault located at a connection end coil knuckle. The failure was limited to a single coil end turn knuckle of the winding and was located in a position that is not susceptible to air flow or foreign material. The apparent cause of the failure was a random insulation breakdown of the original winding that resulted in a turn-to-turn failure. The pump motor that failed has been replaced by a spare pump motor and the motor that failed was shipped to a vendor for failure analysis and repair.
461 | 4612011004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612011004R00.pdf | 2011-11-29 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Clinton 1 | B | GE | PO | 16 | On November 29, 2011, with the reactor at 16.1 percent thermal power, Operators were reducing generator load to 50 Megawatts in order to trip the Main Turbine to start refueling outage C1R13. Turbine Bypass Valve (BPV) #1 had begun opening and was approximately 8 percent open when it ramped closed contrary to system demand. A Steam Bypass Control Pressure Regulator error alarm was received in the Main Control Room. Due to the loss of the steam flow path through the bypass valve to the Main Condenser, Reactor Pressure Vessel (RPV) pressure began to increase and subsequently reached the high reactor pressure scram setpoint resulting in an automatic reactor scram. Reactor pressure control was established manually utilizing the Steam Bypass Valve opening jack. Troubleshooting determined that BPV #1 closed due to failure of a Bypass Valve Demand (BVD) card in the Steam Bypass and Pressure Control (SBPC) System causing RPV pressure to increase. The cause of this event is attributed to the failure to replace or refurbish the BVD card prior to it failing. Corrective actions include replacement of both the A and B BVD cards, establishment of periodic preventive maintenance for the cards, and performing an extent of condition review for other cards in the SBPC system.
461 | 4612013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612013002R00.pdf | 2013-03-07 | QR5 | Turbine Trip | [45 empty] | Clinton 1 | B | GE | PO | 97 | On 3/7/13, at 0756 hours, the main generator tripped followed by a main turbine trip and an automatic reactor SCRAM at 0758 hours. A troubleshooting team was immediately dispatched to investigate the cause of the event and found that a fuse was blown/open on the C phase of the main generator's voltage regulating potential transformer (PT). This fuse is designed to fast blow. A voltage balance relay is installed to sense a fast blow failure and prevent a generator trip. Investigation found that the fuse did not fast blow and instead degraded gradually and did not allow the voltage balance relay to detect a problem, thus the relay did not prevent the main generator trip and subsequent SCRAM. A failure analysis of the fuse identified that the cause of the C phase potential transformer fuse failure was a manufacturing defect in a solder connection in the fuse. The poor solder connection was caused by deficiencies in the manufacturing process. Corrective actions include replacing the fuse that failed with a fuse that was not manufactured at the affected facility. An evaluation is being performed to determine when to inspect and replace the population of other potentially affected fuses.
461 | 4612013003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612013003R00.pdf | 2013-04-26 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 97 | On 4/26/13, with the plant at 97 percent power, the Main Control Room received a Main Electro-Hydraulic Control (EHC) pressure alarm due to lowering level in the EHC Oil Reservoir. An operator reported Main EHC Oil Reservoir level was at minus 4.25 inches and rapidly lowering. In response, Operators initiated a manual reactor SCRAM. All control rods fully inserted and the plant responded as expected to the SCRAM. The EHC oil leak was caused by a broken socket head cap screw used to attach a hydraulic shutoff valve to a Main Steam Turbine Control Valve and three remaining cap screws were loose, with one slightly bent. The faulty shutoff valve was replaced, properly torqued, and the EHC system was pressurized to verify it was free of leaks. The bolting torque was verified to be proper for all hydraulic shutoff valves for control valves, stop valves, and intermediate valves. The most probable cause for this event is inadequate work instructions that led to failure to install appropriate lock washers on the shutoff valve connection, resulting in cap screws becoming loose and ultimately failing due to fatigue. Corrective action includes correcting work instructions, initiating work orders to install lock washers on hydraulic shutoff valves, and ensuring the bill of materials in model work orders specifies the appropriate lock washers for the application.
461 | 4612013008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612013008R01.pdf | 2013-12-08 | QR6 | Manual Reactor Trip |  |  |  | X | [15 empty] | X | [25 empty] | Clinton 1 | B | GE | PO | 97 | On 12/8/13 at 2026 hours with the plant in Mode 1 at 97.3 percent reactor power, operators received multiple alarms due to the trip of 4160 volt 1A1 breaker which resulted in a loss of power to two Division 1 480 volt unit substations. Operators were immediately dispatched and found a 4160/480 volt stepdown transformer failed. Many Division I components lost power. The loss of power caused an instrument air (IA) containment isolation. The loss of IA affected various containment loads, including the scram pilot air header, the main steam isolation valves and the reactor water cleanup system. At 2036 hours, the scram pilot air header low pressure alarm was received, and in response to an anticipated automatic reactor scram, operators immediately initiated a manual reactor scram. All control rods fully inserted into the core. Reactor pressure vessel water level dropped to the low reactor water level 3 setpoint (normal result of a scram from high power) and operators entered the Reactor Pressure Vessel Control Emergency Operating Procedure. The most probable cause of the transformer failure was a tum to turn failure of the high side windings due to insulation breakdown over time, prior to its expected end of life. An installed spare was connected to replace the failed Division 1 transformer.
461 | 4612013009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612013009R00.pdf | 2013-12-13 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 18 | On 12/13/13 the plant was in Mode 1 at 18 percent reactor power with power ascension in progress. Operators were transitioning from the Motor Driven Reactor Feed Pump (MDRFP) to the 'A' Turbine Driven Reactor Feed Pump (TDRFP). Operators opened the 'A' TDRFP Discharge Valve and placed the 'A' TDRFP Recirculation Valve in Automatic, which positioned the recirculation valve to 25% open. When the `A' TDRFP began to feed, the MDRFP began to reduce flow as designed. Over the next few minutes, flow from the two feed pumps began to fluctuate, and reactor water level began to oscillate outside the normal control band. Operators recognized the level swings were growing in amplitude and took manual control of the MDRFP flow control valve (FCV). At this time, the speed of the 'A' TDRFP increased causing an increase in Reactor Water Level. As reactor water level approached the high Level 8 trip set point, operators placed the Reactor Mode Switch into the Shutdown position, initiating a manual scram. The cause for this event is errors in the recently installed digital feedwater control system software. The installed digital feedwater programming will be revised to correct the identified software errors. Interim actions were taken to revise operating procedures.
461 | 4612014002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612014002R00.pdf | 2014-03-25 | QL7 | Degraded condenser vacuum | [45 empty] | Clinton 1 | B | GE | PO | 46 | On 3/25/14 the plant was in Mode 1, steady state at 85 percent reactor power. Operators in the Main Control Room (MCR) observed Offgas (OG) flow rate lowering, condenser vacuum lowering, and condensate water temperature rising. The 13' Steam Jet Air Ejector (SJAE) was in service at the time. As condenser vacuum lowered from 29 inches Mercury (Hg) to 27.4 inches Hg, Operators entered the Loss of Vacuum off-normal procedure and commenced a rapid power reduction. While reducing power, the MCR team began preparations to place the 'A' SJAE in service. At 1942 hours with Reactor power at 46 percent and vacuum at 24 inches Hg and lowering, Operators placed the Mode Switch in shutdown. All control rods were fully inserted. The plant responded as expected with no complications. No safety systems actuations occurred nor were required to place the plant in a safe and stable condition. The cause for this event is unstable pressure control of B SJAE due to a system resonance or instability. The root cause of the system resonance is indeterminate at this time pending additional testing. Corrective action for this event includes replacing the SJAE pressure controller and developing a comprehensive test plan that will dampen or eliminate the system resonance.
461 | 4612017005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612017005R01.pdf | 2017-05-30 | QR3 | Reactivity Control Imbalance | [45 empty] | Clinton 1 | B | GE | PO | 28 | On May 30, 2017 at 2038 CDT, with the reactor at approximately 28% thermal power Clinton Power Station (CPS) experienced an automatic reactor scram while conducting scram time testing (STT). Plant systems responded as expected and functioned properly following the automatic scram. The automatic scram signal was generated by the Oscillation Power Range Monitor (OPRM) Growth Rate Algorithm (GRA). An evaluation confirmed that the reactor was operating in a very stable core condition and that the event did not occur due to an actual core thermal hydraulic instability. The cause of the event was that the OPRM GRA trip function design is unable to distinguish between plant response to system perturbations and onset of thermal-hydraulic instabilities. Interim actions were implemented to increase operating margin to trip setpoints to support reactor startup and completion of STT. They included a revision to a plant procedure to establish an operating strategy when performing STT in the OPRM enabled region, implementing a monitoring strategy to assess the effectiveness of the operating strategy and monitoring for expected plant response, and raising OPRM Amplitude and GRA set points. Planned corrective actions include working with the industry, as needed, to develop and implement an industry solution for the design of the OPRM GRA to prevent false, spurious trip signals. The automatic scram is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
461 | 4612017007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612017007R02.pdf | 2017-06-10 | QR6 | Manual Reactor Trip | [45 empty] | Clinton 1 | B | GE | PO | 93 | On June 10, 2017, at 2256 CDT, Clinton Power Station (CPS) experienced a complete loss of the 'A' feedwater (FW) heater string. The operators received numerous FW trouble alarms on FW string 'A' and low pressure heater 1A/1B bypass opened (1CB004). The operators entered procedure CPS 4005.01, "Loss of FW Heating," which directs the operators to restore and maintain power at or below the original power level. The operators lowered core flow and inserted all CRAM rods, and then observed that FW temperature had dropped greater than 100°F. As directed by CPS 4005.01, at 2306 hours the reactor mode switch was placed into the shutdown position and Procedure 4100.01, "Reactor Scram," was entered. All systems operated as expected following the scram. At 0100 EDT on June 11, 2017, Event Notification 52800 was made. The loss of FW heating transient was caused by a loss of power to Moore trip units caused by a shorted condition on the Moore trip unit associated with the Hi-Hi level in the 4A FW heater. The root cause is that the design of the FW heater level control trip circuitry was not adequate to prevent scrams due to an unevaluated single point vulnerability. Prior to startup, CPS modified the circuit card locations and thereby diversified the power supplies so that the trip units have less dependency on common fuses. Additional corrective actions include performing an engineering evaluation to determine if there are additional single component failures, operator errors, or events for the FW heating system that could result in a drop in FW temperature of greater than 100°F.
461 | 4612017010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612017010R02.pdf | 2017-12-09 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Clinton 1 | B | GE | PO | 97 | On December 9, 2017 at 1347 CDT the Main Control Room received annunciators that indicated a trip of a 4160V 1A1 Breaker (1AP07EJ), 480V transformer 1A and A1 feed breaker. The loss of Division 1 480V power caused the Instrument Air (IA) containment isolation valves to fail close as designed. The loss of IA affected various containment loads, including the scram pilot air header and containment isolation valves. Another consequence of this event was that secondary containment (SC) vacuum was not maintained within Technical Specification (TS) limits due to Fuel Building ventilation dampers failing closed by design due to the loss of power. In addition, this event resulted in the inoperability of the Low Pressure Core Spray System (a single train safety system) and inoperability of primary containment due to primary to secondary containment differential pressure being outside TS limits. Operations entered Emergency Operating Procedure (EOP) -08, Secondary Containment Control. Division 2 Standby Gas Treatment System was activated at 1350 and restored SC vacuum within allowable TS values at 1351 and the EOP was exited. Due to the loss of IA, a manual reactor scram was inserted at 1353 when two control rods began drifting in as expected. A phase to ground fault was identified on 480V transformer 1A (1AP11E). On December 14, 2017, the 480V transformer was replaced and the plant returned to Mode 1 operations on December 15, 2017. The condition described in this report was determined to be reportable under 10 CFR50.73(a)(2)(iv)(A), 10 CFR 50.73(a)(2)(v)(C), 10 CFR 50.73 (a)(2)(ii)(B) and 10 CFR 50.73 (a)(2)(v)(D). Based on analyses performed at vendor test facilities following the event, the cause of the transformer failure was determined to be excessive layer to layer design stress within the 4160V winding. The identification of a pre-existing design defect during the cause analysis also resulted in the issuance a 10 CFR Part 21 notification to the NRC. This event is classified as an unplanned scram with complications due to the loss of Div. 1 480 power.
461 | 4612018005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4612018005R02.pdf | 2018-10-28 | QR3 | Reactivity Control Imbalance | [45 empty] | Clinton 1 | B | GE | HD | 0 | On October 28, 2018, at 0445 CDT at approximately 0.5% power while performing a soft shutdown in support of a planned maintenance outage (C1M23), the plant experienced an unplanned Reactor Protection System (RPS) actuation due to Intermediate Range Monitors (IRMs) High Flux. At the time of the event Main Steam Line (MSL) drains were being closed to control the reactor cooldown rate. When MSL drain isolation valve 1B21-F016 was full closed, pressure reduction (cooldown) stopped resulting in a small reactor water level change and the Feedwater system responded by injecting a small amount of cold water. This combination of conditions resulted in a positive reactivity change which resulted in the reactor scram. A review of the Feedwater system response determined that the system responded as designed and no equipment failure initiated the conditions leading to the scram. The cause of the event was pressure control guidance was not adequate to address the cooldown rate conditions during a soft shutdown. Corrective actions include implementing best practices for pressure control strategies, abort criteria based on reactor pressure, actions to minimize time in the region of vulnerability, and associated operator training. This event is reportable under the provisions of 10 CFR 50.73(a)(2)(iv)(A) as an "event or condition that resulted in the manual or automatic actuation of the Reactor Protection System."
482 | 4821987002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987002R00.pdf | 1987-01-08 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1818 ON 1-8-87, WITH THE UNIT OPERATING AT ABOUT 100% POWER, A LOW STEAMLINE PRESSURE SIGNAL OCCURRED DURING CALIBRATION TESTING AND INITIATED A SI SIGNAL AND MAIN STEAMLINE ISOLATION. THIS RESULTED IN A REACTOR TRIP, MFW ISOLATION, CONTAINMENT ISOLATION PHASE A, CONTAINMENT PURGE ISOLATION SIGNAL, CONTROL ROOM VENTILATION ISOLATION, EMERGENCY DG START, AFW ACTUATION, ESSENTIAL SERVICE WATER ACTUATION, AND STEAM GENERATOR BLOWDOWN AND SAMPLE ISOLATION. AN UNUSUAL EVENT WAS DECLARED AT 1818 CST AND TERMINATED AT 1850 CST. THE APPROPRIATE LOCAL AND STATE AGENCIES WERE NOTIFIED. THE RCS TRANSIENT WAS MAINTAINED WITHIN DESIGN PRESSURE BY THE PRESSURIZER POWER OPERATED RELIEF VALVES (PORV). SUSPECTED STROKE REVERSAL OF BOTH PORV BLOCK VALVES CAUSED A TRIP OF THEIR RESPECTIVE CIRCUIT BREAKERS. THIS OCCURRENCE WAS SUBSEQUENTLY RESOLVED. BECAUSE OF INDICATIONS THAT A PORV DID NOT RECLOSE, ITS ASSOCIATED BLOCK VALVE WAS MAINTAINED CLOSED. POWER WAS NOT REMOVED FROM THE BLOCK VALVE WITHIN THE TIME REQUIRED BY TECH SPECS THROUGH LICENSED PERSONNEL ERROR. THE PORV POSITION INDICATION WAS DETERMINED TO BE ERRONEOUS AND WAS CORRECTED BY REPAIRING THE VALVE POSITION INDICATION MECHANISM. THE CAUSE OF THIS EVENT WAS A COGNITIVE PERSONNEL ERROR IN ISOLATING THE INCORRECT STEAMLINE PRESSURE TRANSMITTER.
482 | 4821987004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987004R00.pdf | 1987-01-20 | QR5 | Turbine Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 20, 1987, AT APPROXIMATELY 1800 CST, A REACTOR TRIP OCCURRED FROM 100 PERCENT POWER AS A RESULT OF TURBINE HIGH VIBRATION TURBINE TRIP. A FEEDWATER ISOLATION SIGNAL, AN AUXILIARY FEEDWATER ACTUATION SIGNAL, AND A STEAM GENERATOR BLOWDOWN AND SAMPLE ISOLATION SIGNAL OCCURRED AS DESIGNED FOLLOWING THE REACTOR TRIP. THE REQUIRED SAFETY RELATED EQUIPMENT PERFORMED AS DESIGNED. PRIOR TO THE EVENT, THE UNIT WAS IN MODE 1, POWER OPERATION, AT 100 PERCENT POWER. TO PREVENT ADDITIONAL UNNECESSARY CHALLENGES OF REACTOR PROTECTION SYSTEMS, THE TURBINE HIGH VIBRATION TRIP CIRCUITRY HAS BEEN MODIFIED FROM A TRIP FUNCTION TO AN ALARM FUNCTION. FURTHER EVALUATION OF THE TURBINE VIBRATION TRIP CIRCUITRY IS BEING CONDUCTED TO DETERMINE IF ANY OTHER CHANGES WILL BE REQUIRED. THE MODIFICATION IN CIRCUITRY HAS NO ADVERSE IMPACT ON THE NUCLEAR SAFETY OF THE UNIT. THERE WAS NO DAMAGE TO PLANT EQUIPMENT OR RELEASE OF RADIOACTIVITY AS A RESULT OF THIS EVENT. AT NO TIME DID CONDITIONS DEVELOP THAT MAY HAVE POSED A THREAT TO THE HEALTH OR SAFETY OF THE PUBLIC. TWO OTHER INSTANCES OF TURBINE HIGH VIBRATION TURBINE TRIPS ARE DISCUSSED IN LICENSEE EVENT REPORT 87-005-00.
482 | 4821987017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987017R00.pdf | 1987-04-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Wolf Creek | P | WE | PO | 60 | POWER LEVEL - 060%. REACTOR TRIPS FROM 60 PERCENT AND 52 PERCENT POWER OCCURRED ON APRIL 19, 1987, AT APPROXIMATELY 0846 CDT, AND ON APRIL 23, 1987, AT APPROXIMATELY 1223 CDT, RESPECTIVELY. BOTH OF THESE TRIPS OCCURRED WHILE IN MODE 1, DURING POWER REDUCTION TO COMPLY WITH TECHNICAL SPECIFICATION 3.1.3.1, ACTION STATEMENT 'B' WHICH REQUIRES, IN PART, THAT 'WITH MORE THAN ONE FULL-LENGTH ROD INOPERABLE....BE IN HOT STANDBY WITHIN 6 HOURS'. IHE HIGH FLUX RATE TRIPS OCCURRED WHEN BANK D, GROUP 'A' CONTROL RODS WERE INADVERTENTLY DROPPED DURING TROUBLESHOOTING OF A ROD CONTROL SYSTEM MALFUNCTION. ONE DEGRADED COMPONENT WAS FOUND AFTER THE FIRST EVENT. IT WAS BELIEVED THAT THIS FAULTY COMPONENT HAD CAUSED THE ROD CONTROL PROBLEM. THEREFORE, WHEN IT WAS REPLACED, THE PROBLEM WAS CONSIDERED CORRECTED AFTER THE ROD CONTROL URGENT ALARM WAS CLEARED. ALL CONTROL RODS WERE THEN STEP TESTED AND THE UNIT WAS BROUGHT BACK ON LINE. AFTER THE SECOND EVENT, TROUBLESHOOTING EFFORTS FOUND THAT FIVE ADDITIONAL ROD CONTROL LOGIC CABINET CARDS HAD DEGRADED COMPONENTS, WHICH WERE REPLACED. THE CARDS, WHICH WERE SUPPLIED BY WESTINGHOUSE ELECTRIC CORP., WERE FOUND DURING TESTING OF THE CARDS IN THE ROD CONTROL LOGIC CABINETS.
482 | 4821987017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987017R00.pdf | 1987-04-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Wolf Creek | P | WE | PO | 52 | POWER LEVEL - 060%. REACTOR TRIPS FROM 60 PERCENT AND 52 PERCENT POWER OCCURRED ON APRIL 19, 1987, AT APPROXIMATELY 0846 CDT, AND ON APRIL 23, 1987, AT APPROXIMATELY 1223 CDT, RESPECTIVELY. BOTH OF THESE TRIPS OCCURRED WHILE IN MODE 1, DURING POWER REDUCTION TO COMPLY WITH TECHNICAL SPECIFICATION 3.1.3.1, ACTION STATEMENT 'B' WHICH REQUIRES, IN PART, THAT 'WITH MORE THAN ONE FULL-LENGTH ROD INOPERABLE....BE IN HOT STANDBY WITHIN 6 HOURS'. IHE HIGH FLUX RATE TRIPS OCCURRED WHEN BANK D, GROUP 'A' CONTROL RODS WERE INADVERTENTLY DROPPED DURING TROUBLESHOOTING OF A ROD CONTROL SYSTEM MALFUNCTION. ONE DEGRADED COMPONENT WAS FOUND AFTER THE FIRST EVENT. IT WAS BELIEVED THAT THIS FAULTY COMPONENT HAD CAUSED THE ROD CONTROL PROBLEM. THEREFORE, WHEN IT WAS REPLACED, THE PROBLEM WAS CONSIDERED CORRECTED AFTER THE ROD CONTROL URGENT ALARM WAS CLEARED. ALL CONTROL RODS WERE THEN STEP TESTED AND THE UNIT WAS BROUGHT BACK ON LINE. AFTER THE SECOND EVENT, TROUBLESHOOTING EFFORTS FOUND THAT FIVE ADDITIONAL ROD CONTROL LOGIC CABINET CARDS HAD DEGRADED COMPONENTS, WHICH WERE REPLACED. THE CARDS, WHICH WERE SUPPLIED BY WESTINGHOUSE ELECTRIC CORP., WERE FOUND DURING TESTING OF THE CARDS IN THE ROD CONTROL LOGIC CABINETS.
482 | 4821987022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987022R01.pdf | 1987-05-28 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON MAY 28, 1987, A TURBINE BUILDING FAN BREAKER MALFUNCTION CAUSED A LOSS OF POWER TO 480 VOLT MOTOR CONTROL CENTER PG11K. THIS CAUSED LOSS OF HOUSEPOWER TO THE MAIN TURBINE ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM, WHICH CAUSED CLOSURE OF THE MAIN TURBINE CONTROL VALVES. 'SHRINK' TO THE LO-LO LEVEL SETPOINT, RESULTING IN A REACTOR TRIP, MAIN TURBINE TRIP, MAIN FEEDWATER ISOLATION, AUXILIARY FEEDWATER ACTUATION, AND STEAM GENERATOR BLOWDOWN AND SAMPLE ISOLATION AT 1429 CDT. THIS LICENSEE EVENT REPORT REVISION PROVIDES THE RESULTS OF FURTHER EVALUATIONS CONDUCTED INTO THE FAN BREAKER CUBICLE FAILURE AND THE EHC RESPONSE TO THAT FAILURE. AT 2110 CDT, WHEN ATTEMPTING TO RECLOSE THE REACTOR TRIP BREAKERS (RTB'S) THE RTB'S REOPENED AND A MAIN FEEDWATER ISOLATION OCCURRED BECAUSE A NUCLEAR INSTRUMENTATION 'NEGATIVE RATE TRIP' SIGNAL HAD NOT BEEN RESET FROM THE EARLIER TRIP. THIS EVENT OCCURRED AS A RESULT OF A PROCEDURAL OMISSION, WHICH HAS BEEN CORRECTED. THE APPARENT ROOT CAUSE OF THE FAN BREAKER CUBICLE MALFUNCTION WAS A LOOSE CONNECTION ON THE LINE SIDE OF THE BREAKER.
482 | 4821987027 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987027R00.pdf | 1987-06-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 92 | POWER LEVEL - 092%. AT APPROXIMATELY 0647 CDT ON JUNE 29, 1987, A PARTIAL LOSS OF FEEDWATER FLOW OCCURRED. A FITTING ON AN INSTRUMENT LINE, INTERNAL TO THE LUBE OIL RESERVOIR, SENSING MAIN FEEDWATER PUMP (MFP) TRIP HEADER PRESSURE SEPARATED. THIS CAUSED THE PRESSURE SWITCH, WHICH CLOSES CONTROL VALVES WHEN STOP VALVES ARE TRIPPED, TO INCORRECTLY SENSE AN MFP TRIP SIGNAL (STOP VALVES TRIPPED), WHICH THEN CAUSED THE MFP TURBINE STEAM CONTROL VALVES TO CLOSE ON AN ELECTRIC SIGNAL. THIS CAUSED THE 'A' MFP TURBINE TO COAST DOWN. THE ENSUING SHRINK IN STEAM GENERATOR (S/G) LEVEL CAUSED A REACTOR TRIP DUE TO S/G LO-LO LEVEL AT APPROXIMATELY 0648 CDT. AN AUXILIARY FEEDWATER ACTUATION, A S/G BLOWDOWN AND SAMPLE ISOLATION, A MAIN FEEDWATER ISOLATION, AND A MAIN TURBINE TRIP ALSO OCCURRED DURING THIS EVENT. THE UNIT WAS STABILIZED IN ACCORDANCE WITH CONTROL PROCEDURES. ALL REQUIRED SAFETY EQUIPMENT PERFORMED AS DESIGNED. THE ROOT CAUSE OF THIS EVENT WAS DETERMINED TO BE COGNITIVE PERSONNEL ERROR BY CONTRACTOR OR VENDOR PERSONNEL DURING INITIAL INSTALLATION OF THE MFP. EXAMINATION OF THE FITTING INDICATED THAT THE FITTING WAS NOT PROPERLY TIGHTENED DURING INITIAL INSTALLATION.
482 | 4821987030 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987030R00.pdf | 1987-07-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON JULY 20, 1987. AT APPROXIMATELY 2302 CDT, A PARTIAL LOSS OF OFFSITE POWER OCCURRED WHEN A SWITCHYARD POTENTIAL TRANSFORMER FAILED. THE LOSS OF POWER RESULTED IN A LOSS OF POWER TO THE MAIN FEEDWATER PUMP 'A' (MFP) CONTROLLERS AND A SUBSEQUENT COASTDOWN OF THE MFP 'A' TURBINE. AN EMERGENCY DIESEL GENERATOR START AND SHUT DOWN SEQUENCER ACTUATION OCCURRED, WHICH REENERGIZED THE MFP CONTROLLERS AFTER A MFP COASTDOWN OF APPROXIMATELY 10 SECONDS. CONTROLLERS CAUSED AN MFP TRIP DUE TO TURBINE OVERSPEED. THE PARTIAL LOSS OF FEEDWATER FLOW RESULTED IN A REACTOR TRIP ON LO-LO STEAM GENERATOR LEVEL. A PLANT MODIFICATION WILL BE IMPLEMENTED TO PROVIDE A MORE RELIABLE SOURCE OF POWER FOR THE MFP CONTROLLERS WHEN A PARTIAL LOSS OF OFFSITE POWER OOCURS. THIS WOULD PREVENT LOSS OF CONTROL POWER TO THE MFP TURBINE AFTER A PARTIAL LOSS OF OFFSITE POWER. DURING RECOVERY, ON JULY 21, 1987, AT APPROXIMATELY 1442 CDT, FOLLOWING REPLACEMENT OF THE POTENTIAL TRANSFORMER, A SHUT DOWN SEQUENCER ACTUATION OCCURRED AS A RESULT OF A PERSONNEL ERROR WHILE TRANSFERRING LOADS BACK TO THE SWITCHYARD TRANSFORMER. THE PROCEDURE HAS BEEN ENHANCED TO PREVENT SIMILAR OCCURRENCES.
482 | 4821987037 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987037R00.pdf | 1987-09-10 | QR5 | Turbine Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 10, 1987, AT APPROXIMATELY 2009 CDT, A REACTOR TRIP, FEEDWATER ISOLATION (FWIS), AND AUXILIARY FEEDWATER ACTUATION (AFAS) OCCURRED AS A RESULT OF A FAILED 345 KILOVOLT TRANSMISSION LINE CONDUCTOR BETWEEN THE 'B' PHASE MAIN TRANSFORMER AND THE UNIT SWITCHYARD. SUBSEQUENTLY, A CONTAINMENT PURGE ISOLATION AND CONTROL ROOM VENTILATION ISOLATION OCCURRED AT APPROXIMATELY 2107 CDT DURING INVESTIGATION OF A LOSS OF FLOW TO THE CONTAINMENT ATMOSPHERE RADIATION MONITORS. AT APPROXIMATELY 2157 CDT, A SECOND TURBINE DRIVEN AFAS OCCURRED DUE TO TWO LO-LO STEAM GENERATOR LEVELS. A FWIS AND AFAS OCCURRED DURING RESTART DUE TO HI-HI STEAM GENERATOR LEVEL AT APPROXIMATELY 2200 CDT ON SEPTEMBER 11, 1987, AND AGAIN AT APPROXIMATELY 0207 CDT ON SEPTEMBER 12, 1987. THE PROBABLE CAUSE OF THE LINE CONDUCTOR FAILURE WAS HIGH RESISTANCE AND HEATING AT THE BOLTED T-PAD CONNECTION. THE LINE CONDUCTOR HAS BEEN REPLACED. COMPRESSION T-PAD. IT WILL BE REEMPHASIZED TO CONTROL ROOM OPERATORS THAT POWER ASCENSION SHOULD BE A SLOW EVOLUTION SO THAT FEW PARAMETERS WILL BE VARIED SIMULTANEOUSLY TO AVOID FUTURE FWIS/AFAS ACTUATIONS DUE TO FEEDWATER CONTROL PROBLEMS.
482 | 4821987041 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821987041R00.pdf | 1987-09-27 | QR3 | Reactivity Control Imbalance | [45 empty] | Wolf Creek | P | WE | PO | 86 | POWER LEVEL - 086%. ON SEPTEMBER 27 1987, AT APPROXIMATELY 0232 CDT, A REACTOR TRIP OCCURRED FROM APPROXIMATELY 86 PERCENT POWER. POWER LEVEL WAS BEING REDUCED IN PREPARATION FOR THE REFUEL II OUTAGE. THE REACTORS TRIP OCCURRED AS A RESULT OF POWER RANGE FLUX HIGH NEGATIVE RATE WHEN THE BANK 'D', GROUP 'A' CONTROL RODS DROPPED WHILE ATTEMPTING TO MOVE RODS OUT ONE STEP. THIS EVENT IS BEING REPORTED PERSUANT TO 10CFR 50.73(A)(2)(IV) AS AN UNPLANNED ACTUATION OF ENGINEERED SAFETY FEATURES EQUIPMENT. THE ROOT CAUSE OF THE EVENT WAS COGNITIVE PERSONNEL ERROR BY TWO PERSONNEL. A CONTRACTOR FOR INADVERTENTLY BUMPING THE FUSIBLE LINK DISCONNECTS COIL SWITCH ON THE CONTROL ROD MOVEABLE GRIPPER COIL CABINET AND A LICENSED UTILITY OPERATOR FOR ASSUMING AN ALARM WOULD GENERATED IF THE SWITCH WAS MISPOSITIONED. THIS CAUSED THE PROBLEM NOT TO BE FULLY INVESTIGATED. IT WILL BE REEMPHASIZED TO OPERATIONS PERSONNEL TO REQUEST APPROPRIATE ASSISTANCE INVESTIGATING AN EQUIPMENT PROBLEM IF THE PROBLEM CANNOT BE POSITIVELY RESOLVED BY OPERATORS. AN EVALUATION TO REMOVE THE SWITCH HANDLES TO PREVENT THEM FROM BEING ACCIDENTLY MISPOSITIONED WILL BE CONDUCTED.
482 | 4821989002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821989002R00.pdf | 1989-01-23 | QR5 | Turbine Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 23, 1989, AT 1322 CST, A REACTOR TRIP OCCURRED AS A RESULT OF A HIGH BEARING VIBRATION MAIN TURBINE TRIP. A FEEDWATER ISOLATION SIGNAL, AN AUXILIARY FEEDWATER ACTUATION SIGNAL, AND A STEAM GENERATOR BLOWDOWN AND SAMPLE ISOLATION SIGNAL OCCURRED AS DESIGNED FOLLOWING THE REACTOR TRIP. THE REQUIRED SAFETY RELATED EQUIPMENT PERFORMED AS DESIGNED. PRIOR TO THE EVENT, THE UNIT WAS IN MODE 1, POWER OPERATION, AT 100 PERCENT POWER. THE CAUSE OF THE TRIP WAS DETERMINED TO BE A SPURIOUS SIGNAL IN THE VIBRATION MONITORING CIRCUITRY WHICH INCORRECTLY INDICATED HIGH VIBRATION ON THE MAIN TURBINE NUMBER 7 BEARING. TO PREVENT ADDITIONAL UNNECESSARY CHALLENGES OF REACTOR PROTECTION SYSTEMS, THE TURBINE HIGH VIBRATION TRIP CIRCUITRY HAS BEEN MODIFIED FROM A TRIP FUNCTION TO AN ALARM FUNCTION. FURTHER EVALUATION OF THE TURBINE VIBRATION TRIP CIRCUITRY IS BEING CONDUCTED TO DETERMINE IF INSTALLATION OF MULTI-COINCIDENCE LOGIC IS FEASIBLE FOR THE TRIP CIRCUITRY. THERE WAS NO DAMAGE TO PLANT EQUIPMENT OR RELEASE OF RADIOACTIVITY AS A RESULT OF THIS EVENT. AT NO TIME DID CONDITIONS DEVELOP THAT MAY HAVE POSED A THREAT TO THE HEALTH OR SAFETY OF THE PUBLIC.
482 | 4821989004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821989004R00.pdf | 1989-02-02 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Wolf Creek | P | WE | PO | 100 | POWER LEVEL - 100%. ON 2/2/89, AT APPROXIMATELY 1321 CST, A REACTOR TRIP OCCURRED FROM 100% POWER AS A RESULT OF STEAM GENERATOR (S/G) 'C' REACHING THE LO-LO LEVEL TRIP SETPOINT FOLLOWING CLOSURE OF S/G 'C' MAIN STEAM ISOLATION VALVE (MSIV 'C'). IN ADDITION, A FEEDWATER ISOLATION SIGNAL, AN AUX. FEEDWATER ACTUATION SIGNAL, AND A STEAM GENERATOR BLOWDOWN AND SAMPLE ISOLATION SIGNAL ACTUATIONS OCCURRED AS DESIGNED. THE CAUSE OF THE REACTOR TRIP HAS BEEN DETERMINED TO BE A LOOSE SCREW ON A TERMINAL STRIP IN THE SOLID STATE PROTECTION SYSTEM (SSPS). DURING UNRELATED MAINTENANCE, THIS LOOSE TERMINATION WAS BUMPED RESULTING IN A FAST CLOSE SIGNAL TO MSIV 'C'. EFFORTS TO IDENTIFY THE ROOT CAUSE OF THE LOOSE TERMINAL CONNECTIONS HAVE BEEN UNSUCCESSFUL. OTHER TERMINATIONS IN THE SSPS AND OTHER CONTROL ROOM PROCESS CABINETS WERE CHECKED AND TIGHTENED AS NECESSARY. IN ORDER TO PREVENT RECURRENCE OF THIS EVENT, A CHECK OF SCREWS IN THESE APPLICATIONS WILL BE ADDED TO THE INSTRUMENTATION AND CONTROLS PREVENTATIVE MAINTENANCE PROGRAM.
482 | 4821990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821990001R00.pdf | 1990-02-06 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Wolf Creek | P | WE | PO | 100 | On February 6, 1990, at approximately 0906 CST, a Reactor trip occurred from 100 percent power as a result of a loop low flow condition following a trip of Reactor Coolant Pump (RCP) "A". In addition, a Feedwater Isolation Signal, an Auxiliary Feedwater Actuation Signal, and a Steam Generator Blowdown and Sample Isolation Signal actuations occurred as designed. All required safety related equipment performed as designed.<br /><br /> The trip of RCP "A" was caused by an indicated high differential current on the "A" phase. The differential current relay was tested and no abnormalities were detected. Extensive troubleshooting efforts were unsuccessful in identifying the root cause for the relay actuation. Following installation temporary recorders to monitor inputs to the relay, RCP "A" was restarted at approximately 1630 CST. No significant abnormalities associated with pump operation were detected and the next day, on February 7, 1990, the unit was restarted, entering Mode 2, Startup, at 1631 CST.
482 | 4821990011 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821990011R00.pdf | 1990-05-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 8 | On May 14, 1990, at 2136 CDT, during performance of the Main Turbine overspeed trip test, a Feedwater Isolation Signal (FWIS) and Main Turbine trip signal occurred when Steam Generator 'B' reached the high-high level setpoint. Shortly thereafter, a Reactor trip and Auxiliary Feedwater Actuation Signal (AFAS), and Steam Generator Blowdown and sample Isolation Signal (SGBSIS) occurred when Steam Generator 'C' reached the low-low level setpoint. All Engineered Safety Features and Reactor Protection System equipment responded properly to the actuation signals. <br /><br /> Earlier in the day on May 14, 1990, feedwater preheating using main steam had been removed from service. When the Main Turbine was taken offline in accordance with the overspeed trip test, feedwater heating using extraction steam was lost. As a result of the colder feedwater being supplied to the steam generators, significant level oscillations occurred. Although the Control Room Operators took the appropriate actions to dampen these oscillations, their efforts were unsuccessful in preventing the high-high and low-low level conditions. <br /><br /> The procedure for performing the overspeed trip test has been revised to require feedwater heating to be inservice prior to conducting the test. The revised test was completed successfully on May 16, 1990 at 0002 CDT.
482 | 4821990012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821990012R00.pdf | 1990-05-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Wolf Creek | P | WE | SU | 1 | On May 17, 1990, at 2305 CDT, with the unit at 0.5 percent power, a Reactor trip signal, Main Turbine (TA-TRB) trip signal, Auxiliary Feedwater Actuation Signal (AFAS), Feedwater Isolation Signal (EWIS) and Steam Generator Blowdown and Sample Isolation Signal (SGBSIS) occurred as a result of a low-low water level in Steam Generator 'C'. Prior to this event, the unit had been taken off line and the steam generator atmospheric relief valves (ARV's) were being used to maintain Reactor Coolant System temperature. At approximately 2300 CDT, it was discovered that the was stuck open. Efforts to close the ARV from the Control Room unsuccessful, and operators were dispatched to manually isolate the valve. This valve was isolated at 2310 CDT, and plant conditions were stablized <br /><br /> During subsequent troubleshooting, a current-to-pnueumatic converter in the ARV positioner circuitry was replaced. The ARV was verified to be operating properly and was restored to service at 0716 CDT m May 18, 1990. It is believed that the failure occurred as a result of a pressure regulating Fall in the air bleed off line of the converter being restricted fran free movement. This condition caused the ARV to in the open position.
482 | 4821990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821990013R00.pdf | 1990-05-19 | QR5 | Turbine Trip | [45 empty] | Wolf Creek | P | WE | PO | 97 | On May 19, 1990, at 2353 CDT, a Main Turbine TA-TRB! trip occurred as a result of high-high Moisture Separator Reheater level. Because the unit was operating at greater than 50 percent power, the Main Turbine trip caused a Reactor trip. As expected, an Auxiliary Feedwater Actuation Signal, a Feedwater Isolation Signal and a Steam Generator Blowdown and Sample Isolation Signal also occurred. All Reactor Protection System and Engineered Safety Features equipment functioned properly. <br /><br /> Following this event, extensive troubleshooting activities were conducted. A level switch on Moisture Separator Drain Tank (MSDT) 'A' was found to initially be stuck thus preventing a Main Control Room alarm on high level. The switch was replaced. The remainder of the level control circuitry for MSDT 'A' was found to be operating properly. No abnormalities were identified in the dump valve to the condenser, the normal level control valve, or its upstream check valve. No significant abnormalities could be identified during the troubleshooting. The unit was restarted on May 20, 1990, and levels were closely monitored. No further difficulties were encountered in the level control system.
482 | 4821992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821992002R00.pdf | 1992-02-19 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Wolf Creek | P | WE | PO | 100 | On February 19, 1992, at 2110 CST, after the failure of a gating/sequencing card in the inverter supplying a 120 volt AC safety-related instrument bus, a Reactor trip occurred on low-low water level in Steam Generator "A". As expected an Auxiliary Feedwater Actuation Signal, a Feedwater Isolation Signal, and a Steam Generator Blowdown and Sample Isolation Signal occurred. Also, a Control Room Ventilation Isolation Signal occurred when power was lost to Control Room Air Intake Chlorine Monitor GKAI03. The plant was in Mode 1, Power Operation, at 100 percent rated thermal power. The failed gating/sequencing card was replaced and the inverter restored to its normal power supply at 0745 CST on February 20, 1992.<br /><br /> A detailed evaluation is being conducted to determine the exact root cause of the failed gating/sequencing card. A review of procedure OFN 00-021, "Loss of Vital 120 VAC Instrument Bus", has been conducted and while the procedure provides the necessary guidance to Control Room operators when responding to this type of event, enhancements are being incorporated into the procedure.
482 | 4821992016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821992016R00.pdf | 1992-11-10 | QR5 | Turbine Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | On November 10, 1992, at 1105 CST, a generator trip/turbine trip occurred when a ground fault was initiated by contact between an overhead ground and the energized portion of a 138 kilovolt (kV) ring bus during clearance procedures for a 345/138 kV transformer at a non-nuclear utility substation. This was followed by a reactor trip, feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown and sample isolation. Plant response to the reactor trip and engineered safety features actuation was normal. <br /><br /> The root cause of this event was cognitive personnel errors by two non- nuclear apprentice wiremen who created a single phase to ground fault while attempting to install protective grounds on an energized 138 kV bus. Also, a cognitive personnel error occurred when the differential protection scheme for this section of bus had been taken out of service by a senior non-nuclear control technician and had not yet been reconnected at the time the phase to ground fault condition began. Additional training will be provided to all pertinent personnel and the process for planning, scheduling and coordinating projects involving different departments performing work in the same work location will be improved by the non-nuclear utility company.
482 | 4821995001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821995001R00.pdf | 1995-03-08 | QR8 | Spurious Reactor Trip | [10 empty] | X | [29 empty] | X |  |  |  |  | Wolf Creek | P | WE | PO | 100 | On March 8, 1995, at approximately 1445 hours, Wolf Creek Generating Station experienced a reactor trip caused by a malfunctioning Reactor Trip Manual Actuation Switch. Instrumentation and control personnel were performing Surveillance Test Procedure STS IC-746B, Revision 7, 'Reactor Protection System Reactor Trip Breaker 'B' Time Response Testing.' Plant response to the reactor trip and engineered safety features actuation was normal, with the exception of the failure of non-safety features bus PA01, '13.8 KV Non Vital Bus,' to transfer to its offsite source of power. The failure of PA01 to transfer power sources resulted in the loss of two Circulating Water System Pumps, Condenser Vacuum, two Reactor Coolant Pumps and the subsequent release of steam through the Steam Generator Atmospheric Relief Valves. <br /><br /> The root cause of this event is that the Reactor Trip Manual Actuation Switch slip contacts did not maintain continuity when the switch was moved from the 'normal after close' position to the 'closed' position. This intermittent continuity problem caused both the Main Reactor Trip Breaker 'A' and Bypass Reactor Trip Breaker 'B' to open simultaneously, resulting in the reactor trip. Immediate corrective actions include the revision of the surveillance procedures and establishment of administrative controls to preclude use of this switch at power to conduct surveillances. Long term corrective actions are being evaluated.
482 | 4821996002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821996002R00.pdf | 1996-01-30 | E2 | Partial Loss of Service Water |  |  |  |  | X | [16 empty] | X | [23 empty] | Wolf Creek | P | WE | PO | 98 | On January 30, 1996, at 0337 CST, operators in the Wolf Creek Generating Station (WCGS) Control Room manually tripped the reactor due to ice build-up on the circulating water (CW) traveling screens. The ice inhibited flow to the CW pumps and caused pressure and flow oscillations. As part of the initial actions taken when the ice was discovered, the A and B Essential Service Water System (ESWS) pumps were started. Approximately six hours later, the A ESWS pump was secured due to decreasing bay level and high differential pressure across the strainer. The cause of decreasing bay level was later determined to be ice build-up on the ESWS trash racks. The B ESWS train experienced similar icing conditions, but remained operable. Based on ESWS conditions and the inoperability of the turbine driven auxiliary feedwater pump due to a packing leak, a Notification of Unusual Event (NUE) was declared at 0846 CST. The NUE was terminated later that day, but was reinstated on January 31, 1996, due to continued icing conditions in the ESWS bays (refer to WCNOC LER 96-001-00 regarding the loss of CW and the subsequent reactor trip).
482 | 4821996006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821996006R00.pdf | 1996-06-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 99 | On June 6, 1996, at 1320 (CDST), a reactor trip occurred at the Wolf Creek Generating Station (WCGS). The reactor trip was caused by a 'lo-lo' level in Steam Generator 'C'. The 'lo-lo' level resulted from reduced feedwater flow to the steam generator. Subsequent investigation determined that the failure of a 3/16' roll pin in the 'C' Steam Generator Main Feedwater Regulating Valve (AE-FCV-530) had allowed the valve plug to separate from the valve stem. The plug of the valve then dropped to the closed position, reducing feedwater flow through the valve. The Reactor Protection System (RPS) and the Engineered Safety Features (ESF) performed as required. The automatic actuation of the reactor trip occurred as expected, with all rods inserting fully. <br /><br /> WCNOC had originally replaced this roll pin with a solid pin in 1988. However, during March of 1996, WCNOC replaced valve stem assemblies with spare assemblies from the warehouse which contained roll pins instead of solid pins. <br /><br /> The root cause of this event was inadequate design modification procedures that failed to address stored inventory and future procurement. Following the reactor trip on June 6, 1996, the correct pins were installed in three of the four Main Feedwater Regulating Valves (MFRV). All MFWRVs now have the correct pins. Holds were placed on stored equipment; procedure changes were implemented; and a review is being performed to determine the extent of the programmatic concern.
482 | 4821997008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821997008R00.pdf | 1997-05-20 | QK4 | Steam or Feed Leakage | [45 empty] | Wolf Creek | P | WE | PO | 82 | On Tuesday, May 20, 1997, at 1402, valve AFLV0058C, a non-safety related sixteen inch third stage extraction steam isolation valve, developed a body-to-bonnet steam leak. The steam leak increased to the point that a manual plant trip was initiated at 1457. All rods inserted normally and fully, and all Engineered Safety Features equipment and Reactor Protection System equipment performed as designed. The leak was stopped by shutting the Main Turbine Stop valves. The body-to-bonnet gasket in AFLV0058C was replaced by a new corrugated iron gasket wrapped with graphite tape. No steam cutting or other damage was identified during the rework.The root cause of the event was the lack of guidance on how to determine minimum and maximum gasket seating stress and corresponding bolt torque values for sheet type gasket materials. Corrective actions included evaluation of other equipment for similar concerns, revision of procedures to provide guidance on providing the correct torque necessary to produce the required gasket stress, and training of Maintenance Planners.
482 | 4821997024 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821997024R00.pdf | 1997-11-29 | QR8 | Spurious Reactor Trip | [45 empty] | Wolf Creek | P | WE | SU | 7 | On November 29, 1997, at 14:37 Central Standard Time a reactor trip occurred at the Wolf Creek Generating Station (WCGS). The plant was in mode one, at seven percent power, at the time of the trip. The Engineered Safety Features (ESF) and Reactor Protection System (RPS) performed as required. The automatic actuation of the reactor trip occurred as expected, with all rods inserting fully.Subsequent investigation revealed that the reactor trip was caused by a spike on the Ex-Core Neutron Monitoring System (SE) Nuclear Instrument NI-35 Intermediate Range (IR) Channel. The spike exceeded the Intermediate Range High Flux trip setpoint of the current equivalent of twenty-five percent Rated Thermal Power (RTP). The cause of the spike is indeterminate. Based on the investigations performed, no anomalies have been identified that can be confirmed to have caused the IR High Flux trip. Corrective actions included stabilizing the plant, and investigating causes.
482 | 4821999008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4821999008R00.pdf | 1999-08-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | At 1258 hours, Wolf Creek experienced an automatic reactor trip following closure of valve AEFCV-540, 'D' Steam Generator Feedwater Regulating Valve. When the valve closed steam generator level decreased below the reactor trip setpoint of 23.5 percent, initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven) because of the low-low steam generator levels. All control rods fully inserted, and all safety equipment performed as designed. The Reactor Protection System (RPS) and the Engineered Safety Features (ESF) performed as required.The cause of the Main Feedwater Regulating Valve closure was the failure of a Westinghouse 7300 Process Control NCB Group 1 controller card that provides control for the Main Feedwater Regulating Valve for Steam Generator 'D'. The Westinghouse 7300 Process Control NCB Group 1 controller card was replaced.The safety significance of this event has been evaluated and determined to be low. This event is bounded by the current licensing basis analysis as reported in USAR Section 15.2.7. All safety equipment performed as designed and there were no adverse effects on the health and safety of the public.
482 | 4822000003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822000003R00.pdf | 2000-09-04 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Wolf Creek | P | WE | PO | 100 | On September 4, 2000, at 1132, Wolf Creek Generating Station (WCGS) experienced afire on the Unit Auxiliary Transformer. This resulted in a momentary degraded condition for the station service loads. The "C" and "D" Reactor Coolant Pumps (RCP) tripped on under voltage, which resulted in a reactor trip. A turbine trip then followed. The fire on the transformer was extinguished by installed plant fire suppression equipment, and was declared "out" at 1143. The plant was stabilized at 2235 psig in the Reactor Coolant System. Other actuations were feedwater isolation and actuation of both motor and turbine driven auxiliary feed pumps due to low steam generator water level. These actuations were expected, and safety equipment performed as designed. The fast bus transfer to the start-up transformer source performed consistent with its design. Immediate investigation revealed what appeared to be a dead squirrel below the Transient Recover Voltage (TRV) Capacitor Bank associated with the PA02 side of the Unit Auxiliary Transformer. The root cause is that the Unit Auxiliary Transformer was not designed to be resistant to small animal intrusion. Corrective actions include installing insulating materials on the Unit Auxiliary Transformer and its TRV capacitor banks, and installing insulating material on the Startup Transformer and capacitor banks. On September 4, 2000, at 1424, a separate Feedwater Isolation Signal occurred. The root cause of this subsequent event was a misleading procedure step, which will be clarified.
482 | 4822002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822002003R00.pdf | 2002-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | On May 8, 2002, at 5:07 p.m., Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to low water level in the "D" steam generator (SG). This actuation occurred following the closure of the "D" SG main feedwater regulating valve (FRV) during surveillance testing. When the FRV closed, "D" SG level decreased below the reactor trip setpoint of 23.5 percent, initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven) because of the low-low SG levels. All control rods fully inserted, and the RPS and the Engineered Safety Features (ESF) Systems performed as expected.The cause of the FRV closure was the failure of a Westinghouse 7300-series manual controller card for the "D" SG FRV. The failed controller card was replaced.The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
482 | 4822003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822003001R00.pdf | 2003-01-03 | QR8 | Spurious Reactor Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | On January 3, 2003, at 11:01 a.m. Central Daylight Time (CDT), Wolf Creek Generating Station (WCGS) experienced an automatic actuation of the Reactor Protection System (RPS), including an automatic reactor trip, due to power range neutron flux high negative rate. The reactor trip occurred while restoring the number one rod drive motor generator (RDMG) set to service after routine breaker maintenance. A Reactor Operator (RO) in the plant was simulating how to manually charge the non-operating RDMG set output breaker to two non-licensed operators. The RO manipulated the manual charging handle for the RDMG set number one output breaker outside of procedural guidance and without control room direction. Concurrent with the actuation of the manual charging handle, the number one output breaker closed, then reopened, and the number two RDMG set output breaker opened. When the number two RDMG set output breaker opened, the control rods lost holding power and started to insert. All control rods fully inserted, and the RPS and the Engineered Safety Features (ESF) systems performed as expected. The cause of this event was personnel error. The safety significance of this event is low. All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
482 | 4822003003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822003003R00.pdf | 2003-08-18 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | On August 18, 2003, at 3:54 PM, Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to lo/lo water level in "B" steam generator (SG). This actuation occurred following the closure of the "B" SG main feedwater isolation valve (FWIV). When the FWIV closed, "B" SG level decreased below the reactor trip setpoint, initiating a reactor trip. The unit received an expected feedwater isolation and expected auxiliary feedwater actuation (both motor and turbine driven) because of the lo/lo SG level. All control rods fully inserted, and the RPS and Engineered Safety Features (ESF) performed as expected.The cause of the FWIV closure was a spurious signal from the Engineered Safety Features Actuation System for the "B" SG. The specific component failure could not be determined so all of the electrical components that could have caused the fast closure of the "B" FWIV were replaced. The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in Wolf Creek Generating Station Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
482 | 4822004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822004002R00.pdf | 2004-02-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | On February 13, 2004, at 8:04 AM CST, Wolf Creek Generating Station (WCGS) experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to Lo-Lo water level in the "D" steam generator (SG). This actuation occurred following failure of the "D" SG main feedwater regulating valve (MFRV) resulting in valve closure. When the MFRV failed closed, "D" SG level decreased below the reactor trip setpoint, initiating a reactor trip. The unit received an expected feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven pumps) because of the Lo-Lo SG level. All control rods fully inserted, and the RPS and Engineered Safety Features (ESF) systems performed as expected.The cause of the MFRV closure was separation of the valve plug from the valve stem, which caused the plug to fall into its seated (closed) position. The stem/plug assemblies were subsequently replaced in all four (4) MFRVs.The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
482 | 4822004004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822004004R00.pdf | 2004-08-22 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Wolf Creek | P | WE | PO | 100 | On August 22, 2004 at 1010 a.m. Central Daylight Time, Wolf Creek Generating Station (WCGS) experienced a reactor trip during routine surveillance testing of the "B" train Solid State Protection System (SSPS). To facilitate this testing, WCGS had entered Required Actions for Conditions A and R of Technical Specification (TS) 3.3.1, Table 3.3.1-1, Function 19, which permits operation of the plant with one train of SSPS inoperable and the associated reactor trip breaker (RTB) bypassed for up to two hours. During this testing, WCGS Instrumentation and Controls (I&C) technicians reported to the shift manager in the control room that an indication light did not illuminate as required. During restoration from the procedure, a required step to reinstate the necessary memory circuit blocks for the 25%power reactor trip signals was not performed. When the input error inhibit switch for the "B" train SSPS was returned to the "Normal" position without these memory circuit blocks in place, a reactor trip signal was generated. This was a human performance related event where an I&C technician did not perform the necessary steps to restore from the surveillance test procedure. The safety significance of this event is low. All control rods fully inserted, and all safety-related equipment operated as expected. There were no adverse effects on the health and safety of the public.
482 | 4822004005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822004005R00.pdf | 2004-10-07 | QR8 | Spurious Reactor Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | On October 7, 2004, at 11:48 A.M., Wolf Creek Generating Station (WCGS) experienced an automatic reactor trip due to indicated high main turbine vibrations. Concurrent with this event, several lightning strikes from an electrical storm were observed in the immediate area, including one recorded in the vicinity of the steel high line tower for the Main Startup Transformer. This lightning strike created an electromagnetic interference (EMI) that caused the actuation of the Main Turbine High-High Vibration Trip circuitry. The resultant turbine trip actuated an automatic reactor trip. Subsequent investigation of Main Turbine vibration and other performance data has validated that no actual high vibration was present either at the time of the Main Turbine trip, during the ensuing turbine coastdown, or during the subsequent plant restart. All control rods fully inserted and all safety-related equipment operated as designed. The WA" train of the Residual Heat Removal System (RHR) was out of service for normal maintenance at the time of this event. The safety significance of this event is low. All control rods fully inserted, and all safety-related equipment operated as expected. There were no adverse effects on the health and safety of the public.
482 | 4822008003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822008003R00.pdf | 2008-03-17 | QR6 | Manual Reactor Trip | [45 empty] | Wolf Creek | P | WE | PO | 100 | On March 17, 2008, at approximately 1:00 PM while operating at 100% power, Wolf Creek Generating Station (WCGS) was manually tripped due to loss of steam generator (SIG) level. 4.16-kV busses PB03 and PB04 were cross-tied and being supplied by transformer XPB03. A secondary power cable from transformer XPB03 faulted to ground causing loss of power to all condensate pumps that tripped the main feedwater pump on low suction.The direct cause of the faulted transformer was human error. During previous maintenance the transformer bushing multi-conductor connector was reassembled improperly resulting in a loose connection. Together with the loose connection, the higher current caused by the cross-tied busses overheated the individual conductors and insulation resulting in a fault to ground.The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.7, "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
482 | 4822009001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822009001R00.pdf | 2009-04-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | On April 28, 2009 at 3:27 p.m. Central Daylight Time, Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to low water level in the "B" steam generator (SG). The RPS actuation occurred after the "B" SG Main Feedwater Regulating Valve (MFRV) closed in response to failures of the primary and secondary fuses for the Westinghouse 7300 control card frame that contained the associated control cards for the MFRV. When the "B" MFRV closed, "B" SG level decreased below the reactor trip setpoint initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor-driven and turbine-driven) because of the low SG level. All control rods inserted fully and the RPS and the Engineered Safety Features (ESF) Systems performed as expected.The cause of the "B" MFRV closure was the failure of the primary and secondary fuses for the Westinghouse 7300 card frames. All of the 7300 card frame fuse holders were inspected using thermography and 14 fuse holders and fuses were replaced. The degraded fuse holders and associated fuses were replaced before reactor start-up commenced on April 30, 2009.The safety significance of this event is low. This event is bounded by analyses as reported in the Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
482 | 4822009002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822009002R00.pdf | 2009-08-19 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Wolf Creek | P | WE | PO | 100 | On 08/19/2009 Wolf Creek Generating Station (WCGS) was operating at approximately 100% power. At approximately 1549 hours, WCGS experienced an unplanned automatic shutdown. The turbine and reactor trip occurred due to the momentary loss of offsite power (LOOP) to the onsite buses. Operations personnel and safety equipment responded appropriately to place the plant in a stable condition in Mode 3. All control rods inserted fully and the Reactor Protection System and the Engineered Safety Features System performed as expected. A lightning strike on LaCygne 345 kV line caused the loss of the LaCygne line. The Rose Hill 345 kV line was lost due to a loss of carrier function, causing line operation (opening of switchyard breakers), and subsequent loss of the Benton 345 kV line as a result of the unit heading toward instability. The safety significance of this event is low. Both emergency diesel generators started and supplied power to the safety related buses. There were no adverse effects on the health and safety of the public.
482 | 4822010005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822010005R00.pdf | 2010-03-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 100 | On 3/2/2010 at 1458 CST, while performing procedure SYS PN-200, "Energizing and Deenergizing Inverters PNO9 or PN10," Wolf Creek Generating Station (WCGS) experienced a reactor trip due to Steam Generator (SG) Water Level - Low Low actuation signal. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor-driven and turbine- driven) because of the low SG level. All control rods inserted fully and the Reactor Trip System and the Engineered Safety Feature System performed as expected. The SG Water Level - Low Low actuation signal was initiated due to a trip of the train "A" main feedwater pump as a result of the failed transfer of inverter PNO9 to an alternate power supply. Inverter PNO9 did not transfer from the normal to alternate power supply due to the sticking of the reed relay on the static transfer switch circuit board. The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
482 | 4822010006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822010006R00.pdf | 2010-03-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 42 | On 3/8/2010, Wolf Creek Generating Station (WCGS) was at 42 percent power during a reactor startup when the "A" main feedwater (MFW) pump tripped at 0332 CST. The control room operators manually tripped the reactor due to the decreasing steam generator levels. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Systems performed as expected. The cause of the MFW pump trip was a failed servo in the MFW control circuitry.Emergency boration was actuated when reactor coolant system (RCS) temperature dropped below 550 degrees Fahrenheit. Emergency boration was secured at 0404 CST on 3/8/2010 when RCS temperature was raised to greater than 550 degrees Fahrenheit.The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
482 | 4822010012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822010012R00.pdf | 2010-10-17 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Wolf Creek | P | WE | PO | 15 | On October 17, 2010 at 0952 CDT, Wolf Creek Generating Station was at approximately 15% power during a startup when a turbine trip and Feedwater Isolation Signal occurred due to High-High Steam Generator level. An automatic reactor trip occurred at 0953 CDT due to decreasing SG level. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Systems performed as expected. Emergency boration was initiated when reactor coolant system temperature dropped below 550 degrees Fahrenheit. Emergency boration was secured after 58 minutes when RCS temperature was raised to greater than 550 degrees Fahrenheit.The cause of the trip was the Control Room operators were unable to maintain SG levels at low power. Procedures were revised to address the issue. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow."
482 | 4822011007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822011007R00.pdf | 2011-06-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Wolf Creek | P | WE | PO | 82 | On June 26, 2011, Wolf Creek Generating Station (WCGS) was at 82 percent power during a reactor startup when the 'B' Main Feedwater pump tripped at 1609 CDT. The control room operators manually tripped the reactor. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Actuation System performed as expected. The cause of the trip was the failure of one or both of two controller cards in the Main Feedwater turbine control system. Two controller cards in the main turbine control system were replaced.The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
482 | 4822012001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822012001R01.pdf | 2012-01-13 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Wolf Creek | P | WE | PO | 100 | On January 13, 2012, at approximately 1403 Central Standard Time (CST), the unit experienced an unplanned automatic shutdown from full power operations and a coincidental loss of offsite power. The 345-60 generator output breaker in the switchyard catastrophically failed (fault on 'C' phase) resulting in breaker operations and subsequent loss of the East 345 kV bus and a trip of the main turbine. Coincident with the loss of the East 345 kV bus, a rapid transfer of the non-safety buses from the Unit Auxiliary Transformer to the Startup Transformer occurred. After the rapid transfer, a 'B' phase differential relay trip on the Startup Transformer resulted in a loss of the West 345 kV bus and loss of offsite power.The turbine trip initiated a reactor trip. All control rods inserted into the core. All reactor coolant pumps tripped. Both diesel generators started and supplied power to the 4.16 kV engineered safety features buses. Control room operators initiated action per procedure EMG E-0, "Reactor Trip or Safety Injection," and transitioned into EMG ES-02, "Reactor Trip Response." Subsequently, a natural circulation cooldown was performed to place the unit in Mode 5.
482 | 4822015003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4822015003R00.pdf | 2015-05-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Wolf Creek | P | WE | PO | 25 | On May 3, 2015 at 1021 Central Daylight Time (CDT), Wolf Creek Generating Station (WCGS) was at approximately 25% power during startup from Refueling Outage 20. The 'C' steam generator received a Hi-Hi level signal while the Reactor Operator was manually transferring feedwater control from the Main Feedwater Regulating Valve (MFRV) bypass valves to the MFRVs. This resulted in a main turbine trip, feedwater isolation, and auxiliary feedwater actuation. A manual reactor trip was initiated at 1022 CDT. The root cause was the lack of a reliable and consistent standardization between the operating crews to control the transfer of the steam generator feedwater flow between the MFRV bypass valves and MFRVs and a sense of urgency by the control room operators. <br /><br /> The event is bounded by analyses as reported in the Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow."
483 | 4831987032 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831987032R00.pdf | 1987-11-08 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Callaway | P | WE | SU | 1 | POWER LEVEL - 001%. ON 11/8/87 AT 0252 CST, A REACTOR TRIP, FEEDWATER ISOLATION AND AUXILIARY FEEDWATER ACTUATION OCCURRED AS A RESULT OF LOW LEVEL IN STEAM GENERATOR (S/G) 'B'. THE PLANT WAS IN MODE 2 - STARTUP AT APPROXIMATELY ONE PERCENT REACTOR POWER. THE REACTOR COOLANT SYSTEM (RCS) TEMPERATURE WAS 553.4F (AVERAGE). RCS PRESSURE WAS 2188.5 PSIG. THE LOW S/G LEVEL OCCURRED AS A RESULT OF S/G LEVEL OSCILLATIONS FOLLOWING THE RETEST OF LEAKING MAIN STEAM ISOLATION VALVE (MSIV) 'B' AT 0229. THE LICENSED OPERATORS FAILED TO FOLLOW THE TEST PROCEDURE WHICH REQUIRED PERFORMANCE OF THE TEST ONLY IN MODE 3 - HOT STANDBY. ADDITIONALLY, THE 'B' MAIN STEAM DUMP VALVE GROUP WAS CYCLING DUE TO A LOW CONTROL BAND. THE PLANT. LICENSED OPERATORS WERE UNABLE TO STABILIZE THE OSCILLATIONS; THE REACTOR TRIPPED AT 0252. THE OPERATORS RECOVERED FROM THE TRIP VIA PLANT PROCEDURES AND STABILIZED PLANT CONDITIONS BY 0258. TO PREVENT RECURRENCE, FUTURE SIMILAR MSIV RETESTS WILL BE PERFORMED IN MODE 3. THE LEAKING MSIV WAS REPAIRED. THE CONTROL BAND FOR THE STEAM DUMP VALVE WAS CORRECTED. PROGRESSIVE DISCIPLINE WAS INITIATED WITH THE LICENSED OPERATORS INVOLVED. THE EVENT WAS ALSO DISCUSSED WITH THE OPERATORS TO EMPHASIZE THE NEED TO REVIEW RETEST REQUIREMENTS.
483 | 4831988001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988001R00.pdf | 1988-01-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 100 | POWER LEVEL - 100%. ON 1/4/88 AT 0236 CST, A REACTOR TRIP OCCURRED AS A RESULT OF LOW LEVEL IN STEAM GENERATOR (S/G) 'A'. THE PLANT WAS IN MODE 1 - POWER OPERATIONS, AT 100 PERCENT REACTOR POWER. THE REACTOR COOLANT SYSTEM (RCS) TEMPERATURE WAS 589F (AVERAGE). RCS PRESSURE WAS 2234 PSIG. THE LOW S/G LEVEL OCCURRED DURING THE TROUBLESHOOTING OF THE S/G 'A' MAIN FEEDWATER ISOLATION VALVE (FWIV), AE-FV-0039, AMBER LIGHT CONDITION ON THE ENGINEERING SAFETY FEATURES (ESF) STATUS PANEL SA066X. WHILE TROUBLE-SHOOTING THE INDICATION CIRCUIT FOR THE ACCUMULATOR PRESSURE SWITCH, AE-PSL-0039A, THE CONTROL VOLTAGE FOR AE-FV-0039 WAS SHORTED BY INSTRUMENTATION AND CONTROL (I&C) TECHNICIANS CAUSING A BLOWN FUSE. THE BLOWN FUSE RESULTED IN VALVE AE-FV-0039 FAST CLOSING. THIS WAS FOLLOWED BY FLOW MISMATCH ON ALL FOUR STEAM GENERATORS, WITH AN ACCOMPANYING REACTOR TRIP ON S/G LO-LO LEVEL IN S/G 'A' AT 0236. THE OPERATORS RECOVERED FROM THE TRIP VIA PLANT PROCEDURES. ALL OF THE AVAILABLE WIRING DETAILS OF THE CIRCUIT WERE NOT USED. TECHNICIANS REPLACED THE BLOWN FUSE AND SATISFACTORILY COMPLETED THE TROUBLESHOOTING. TO PREVENT RECURRENCE, I&C TECHNICIANS HAVE BEEN INSTRUCTED TO REVIEW DESIGN DRAWINGS BEFORE TROUBLESHOOTING. ADDITIONAL TRAINING WILL BE GIVEN TO I&C TECHNICIANS ON THE SA066 CABINET POWER DISTRIBUTION.
483 | 4831988004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988004R01.pdf | 1988-02-13 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | POWER LEVEL - 100%. ON 2/13/88 AT 0355 CST, A REACTOR TRIP OCCURRED DURING TURBINE SURVEILLANCE TESTING. THE MECHANICAL TRIP PISTON HAD FAILED TO RESET. PER PROCEDURE, A JUMPER WAS INSTALLED IN THE ELECTRO-HYDRAULIC CONTROLS CABINET TO ALLOW RESETTING THE TURBINE TEST CIRCUIT AND COMPLETING THE TEST. THE CLIP OF THE JUMPER SLIPPED LOOSE, SHORTING THE CIRCUIT TO GROUND, CAUSING THE TURBINE/REACTOR TRIP. BY DESIGN, A FEEDWATER ISOLATION AND AUXILIARY FEEDWATER ACTUATION OCCURRED FOLLOWING THE RPS REACTOR TRIP. FOLLOWING THE TRIP, LICENSED OPERATORS IMPLEMENTED THE CORRECT EMERGENCY PROCEDURES. REACTOR COOLANT SYSTEM (RCS) TEMPERATURE CONTINUED TO DECREASE DUE TO EXCESSIVE STEAM LOADS. THE OPERATORS WERE NOT CONTINUOUSLY COGNIZANT OF THE DECREASING RCS TEMPERATURE. AT 0522, STEAM PRESSURE DECREASED TO 615 PSIG AND A SAFETY INJECTION (SI) AND MAIN STEAM LINE ISOLATION (MSLI) WAS ACTUATED. AN UNUSUAL EVENT WAS DECLARED AT 0532. THE OPERATORS RECOVERED VIA PLANT PROCEDURES AND THE UNUSUAL EVENT WAS TERMINATED AT 0645. A BYPASS SWITCH WAS INSTALLED TO PRECLUDE FUTURE JUMPER USE. OPERATION'S PERSONNEL WERE REMINDED THAT CONSTANT ATTENTION TO RCS TEMPERATURE IS IMPERATIVE. AS INTERIM GUIDANCE, A NIGHT ORDER WAS ISSUED DIRECTING OPERATORS TO SHUT MSLI VALVES IN THE EVENT RCS TEMPERATURE FALLS BELOW 530F.
483 | 4831988005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988005R00.pdf | 1988-04-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Callaway | P | WE | SU | 11 | POWER LEVEL - 008%. ON 4/16/88 AT 0221 CDT, A FEEDWATER (FW) ISOLATION (FWIS) AND AN AUXILIARY FW ACTUATION (AFAS) OCCURRED ON A HIGH LEVEL IN 'C' STEAM GENERATOR (S/G). ON 4/17/88 AT 1734 CDT, AN AFAS, FWIS, AND A REACTOR TRIP OCCURRED ON S/G LEVELS. THE PLANT WAS IN MODE 1 - POWER OPERATIONS FOR BOTH EVENTS. THE PLANT TEMPERATURE, PRESSURE, AND REACTOR POWER FOR EVENTS 1 AND 2 WERE 554F, 2235 PSIG, 8%, AND 562F, 2235 PSIG, 11% RESPECTIVELY. THE HIGH S/G LEVEL IN EVENT 1 OCCURRED WHEN TRANSFERRING FROM THE MAIN FEEDWATER REGULATOR VALVES (FRV) TO THE FW BYPASS VALVES. THE LICENSED OPERATOR'S USE OF INDICATIONS TO ANTICIPATE PLANT RESPONSE LED TO AN ERRONEOUS DECISION AS TO THE CAUSE OF THE S/G LEVEL INCREASE AND THE ACTIONS TAKEN TO CORRECT IT. THE LOW S/G LEVEL IN EVENT 2 WAS DUE TO THE LICENSED OPERATOR'S DECISION TO CONTROL FW USING ONLY THE MAIN FRVS AT A LOW POWER LEVEL. TO PREVENT RECURRENCE, PROCEDURES FOR THE FRV TO FW BYPASS VALVE TRANSFER HAVE BEEN REVISED AND TRAINING WILL BE CONDUCTED FOR LICENSED OPERATORS. EMPHASIZE THE NECESSITY FOR ADDRESSING ABNORMAL INDICATIONS DURING TRANSIENT PERIODS.
483 | 4831988006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988006R00.pdf | 1988-04-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 94 | POWER LEVEL - 094%. ON 4/21/88 AT 0217 CDT, A MANUAL REACTOR TRIP WAS INITIATED IMMEDIATELY FOLLOWING THE FAILURE OF THE 'C' MAIN FEEDWATER REGULATING VALVE (FRV), AE-FE-530. THE MANUAL REACTOR TRIP WAS FOLLOWED BY A FEEDWATER ISOLATION AND AN AUXILIARY FEEDWATER ACTUATION BY DESIGN. AT THE TIME OF THE EVENT THE PLANT WAS IN MODE 1, POWER OPERATIONS AT 94% POWER AND A REACTOR COOLANT SYSTEM TEMPERATURE OF 587 DEGREES F AND PRESSURE OF 2234 PSIG. THE 'C' MAIN FRV FAILED DUE TO MATERIAL FATIGUE OF THE ROLL PIN WHICH SECURES THE VALVE PLUG TO THE VALVE STEM. THE PLUG UNTHREADED AND DROPPED FROM THE STEM BLOCKING FEEDWATER FLOW THROUGH THE VALVE. THE ROLL PIN IN THE 'C' FRV WAS REPLACED WITH A SOLID PIN OF GREATER STRENGTH TACK WELDED IN POSITION. ADDITIONALLY, THE ROLL PINS IN THE THREE REMAINING FRV'S AND IN THE FOUR FEEDWATER BYPASS VALVES WERE REPLACED WITH SOLID PINS. THE MANUAL REACTOR TRIP AND ENGINEERED SAFETY FEATURES PERFORMED AS REQUIRED. THERE WERE NO ADVERSE EFFECTS ON THE PUBLIC HEALTH AND SAFETY.
483 | 4831988007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988007R00.pdf | 1988-05-02 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 99 | POWER LEVEL - 099%. ON 5/2/88 AT 1536 CDT, AN AUTOMATIC REACTOR TRIP OCCURRED ON 'B' STEAM GENERATOR (S/G) LOW LEVEL. THE MAIN TURBINE THROTTLE PRESSURE LIMITER (TPL) SPURIOUSLY ACTUATED, CAUSING THE MAIN TURBINE CONTROL VALVES TO CLOSE. THE LOSS OF STEAM DEMAND CAUSED THE S/G TO SHRINK TO THE LOW LEVEL REACTOR TRIP SETPOINT. A FEEDWATER ISOLATION (FWIS) AND AUXILIARY FEEDWATER ISOLATION WERE RECEIVED BY DESIGN. THE LICENSED OPERATORS RECOVERED FROM THE TRIP VIA PLANT PROCEDURES. FOR THIS EVENT, THE PLANT WAS IN MODE 1, POWER OPERATIONS AT 99% REACTOR POWER. REACTOR COOLANT SYSTEM (RCS) TEMPERATURE WAS 588 DEGREES F AND RCS PRESSURE WAS 2235 PSIG. DURING RESTORATION FROM THE TRIP, THE FWIS WAS RESET PER PROCEDURE. AT 1736, WITH THE PLANT IN MODE 3, HOT STANDBY, A LICENSED OPERATOR RE-OPENED THE REACTOR TRIP BREAKERS AND RECEIVED A FWIS. THE OPERATOR FAILED TO RECOGNIZE THAT RE-OPENING THE REACTOR TRIP BREAKERS AFTER RESETTING THE FWIS WOULD RESULT IN A REINITIATION OF THE FWIS. THE TPL WAS BYPASSED VIA A TEMPORARY MODIFICATION. PERMANENT ELIMINATION OF THE TPL CIRCUIT IS UNDER EVALUATION. PROGRESSIVE DISCIPLINE WAS INITIATED WITH THE LICENSED OPERATOR INVOLVED. THIS EVENT WAS DISCUSSED WITH SHIFT SUPERVISORS, AND TRAINING FOR THE LICENSED OPERATORS WILL BE CONDUCTED ON THIS EVENT DURING THE NEXT REQUALIFICATION CYCLE.
483 | 4831988010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831988010R00.pdf | 1988-09-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1323 CDT ON 9/2/88, WITH THE PLANT IN MODE 1 - POWER OPERATIONS AT 100% REACTOR POWER, AN UNPLANNED REACTOR TRIP OCCURRED FOLLOWED BY AUTOMATIC ACTUATIONS OF ENGINEERED SAFETY FEATURES (ESF); SPECIFICALLY A FEEDWATER ISOLATION (FWIS) AND AN AUXILIARY FEEDWATER ACTUATION (AFAS). THIS OCCURRED DUE TO COGNITIVE PERSONNEL ERRORS WHEN A NON-LICENSED EQUIPMENT OPERATOR OPENED A POTENTIAL TRANSFORMER CABINET DRAWER. TO PREVENT RECURRENCE, THE CABINET DRAWERS WILL BE LOCKED WITH A CONTROLLED KEY. THE TRAINING PROGRAM WILL BE REVISED TO INCLUDE THE FUNCTION OF POTENTIAL TRANSFORMER FUSES AND ASSOCIATED INTERLOCKS. PROGRESSIVE DISCIPLINE HAS BEEN INITIATED. AT APPROXIMATELY 1240 CDT ON 9/3/88 DURING THE SUBSEQUENT STARTUP, WITH THE PLANT IN MODE 1 - POWER OPERATIONS AT 8% REACTOR POWER, UNPLANNED AUTOMATIC ESF ACTUATIONS (FWIS AND AFAS) OCCURRED. THE CAUSE OF THE ACTUATION WAS A HIGH 'D' STEAM GENERATOR LEVEL DUE TO EXCESSIVE SEAT LEAKAGE OF THE 'D' FEEDWATER REGULATING VALVE. THE LEAKAGE IS BELIEVED TO BE THE RESULT OF EITHER DEGRADATION OF THE VALVE SEATING SURFACE OR THE VALVE PLUG NOT FULLY SEATING UPON CLOSURE. CORRECTIVE ACTIONS INCLUDED A VISUAL INSPECTION AND STROKE OF THE 'D' FRV, A VISUAL CAUTION TO OPERATORS THAT THE VALVE LEAKS EXCESSIVELY, AND INITIATION OF ACTION TO INVESTIGATE THE VALVE SEAT LEAKAGE DURING THE NEXT REFUELING OUTAGE.
483 | 4831989006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831989006R00.pdf | 1989-05-29 | QR8 | Spurious Reactor Trip | [45 empty] | Callaway | P | WE | PO | 97 | POWER LEVEL - 097%. ON 5/29/89 AT 1051 CDT, A REACTOR TRIP OCCURRED ON A POWER RANGE NEUTRON FLUX RATE TRIP SIGNAL. THE PLANT WAS IN MODE 1 - POWER OPERATIONS, AT 97 PERCENT REACTOR POWER. THE REACTOR COOLANT SYSTEM (RCS) TEMPERATURE WAS 587F (AVERAGE). RCS PRESSURE WAS 2235 PSIG. THE POWER FLUX RATE TRIP SIGNAL WAS RECEIVED DURING THE PERFORMANCE OF A SURVEILLANCE PROCEDURE FOR INCORE/EXCORE CALIBRATION. A CHANGE IN METER LOCATION OF THE MEASURING & TEST EQUIPMENT (M&TE) INSTALLED FOR THE SURVEILLANCE WAS REQUESTED BY A UTILITY REACTOR ENGINEER. THE TECHNICIAN REMOVED THE LEADS FROM THE M&TE THAT WAS CONNECTED TO POWER RANGE CHANNELS N41 AND N42. WHEN RECONNECTING, THE TECHNICIAN DROPPED THE N42 LEADS CAUSING A GROUND. A GROUND IN ONE OF THE N41 LEADS ALSO OCCURRED, WHICH LEAD TO THE TRIP SIGNAL AND SUBSEQUENT UNIT TRIP/TURBINE TRIP. THIS EVENT WAS CAUSED BY THE LACK OF DETAIL PROVIDED IN PLANT PROCEDURES WHICH RESULTED IN PERSONNEL BEING UNAWARE OF POTENTIAL CONSEQUENCES. NEITHER THE TECHNICIAN NOR THE REACTOR ENGINEER REALIZED THE RISK ASSOCIATED WITH THE CONFIGURATION DUE TO THE MULTIPLE CHANNEL ARRANGEMENT AND NON-ISOLATED TEST POINTS. PROCEDURE ESP-ZZ-00006 INCORE/EXCORE CALIBRATION HAS BEEN REVISED TO INCORPORATE SPECIFIC PRECAUTIONS CONCERNING PLACEMENT, CONNECTION AND REMOVAL OF THE M&TE. THE EVENT WILL BE DISCUSSED WITH THE TECHNICIANS AND ENGINEERS INVOLVED.
483 | 4831989008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831989008R00.pdf | 1989-06-23 | QR3 | Reactivity Control Imbalance |  |  | X | [13 empty] | X | [28 empty] | Callaway | P | WE | PO | 100 | POWER LEVEL - 100%. AT 0840 CDT ON 6/23/89, CONTROL ROD BANK 'B' FAILED TO MOVE AND WAS DECLARED INOPERABLE IN MODE 1 - POWER OPERATION AT 100% REACTOR POWER. AT 1102, A PLANT SHUTDOWN WAS COMMENCED PER TECHNICAL SPECIFICATION (T/S) 3.1.3.1 ACTION B. AT 1418 AT APPROXIMATELY 3% REACTOR POWER, THE MAIN TURBINE WAS TRIPPED. A PROTECTIVE RELAY FOR GENERATOR OUTPUT BREAKER ERRONEOUSLY SENSED A FLASHOVER AND CLEARED THE 345 KV SWITCHYARD BUS 'B'. THIS RESULTED IN A COMPLETE LOSS OF POWER TO THE 4.16 KV SAFEGUARDS BUS NB01. THIS RESULTED IN AN ENGINEERED SAFETY FEATURE ACTUATION OF THE TURBINE DRIVEN AUXILIARY FEEDWATER PUMP. AT 1419, THE REACTOR WAS MANUALLY TRIPPED AT 2% REACTOR POWER. THE PLANT WAS STABILIZED IN MODE 3 - HOT STANDBY. THE LOSS OF NB01 HAD CAUSED RADIATION MONITORS, GK-RE-05 AND GG-RE-27, TO BECOME INOPERABLE. T/S 3.3.3.1 ACTIONS 27 AND 30 WERE NOT COMPLETED WITHIN THE 1 HOUR TIME LIMIT. THE PLANT WAS RESTARTED AT 0210 ON 6/24/89 AND REACHED 100% REACTOR POWER AT ABOUT 1500 ON 6/25/89. TWO CIRCUIT BOARDS IN THE ROD CONTROL LOGIC CABINET WERE REPLACED. THE CAUSE OF THE LOSS OF NB01 WAS THE FAILURE OF A FLASHOVER RELAY DUE TO A LOOSE SET SCREW. THE RELAY WAS REPAIRED. THE CAUSE OF THE LATE COMPLETION OF T/S 3.3.3.1 ACTIONS 27 AND 30 WAS ATTRIBUTABLE TO COGNITIVE PERSONNEL ERRORS. THESE WERE IDENTIFIED BUT WERE NOT COMPLETED WITHIN THE TIME REMAINING.
483 | 4831990005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831990005R00.pdf | 1990-05-01 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | On 5/1/90 at 1331 CDT, a reactor trip, an Auxiliary Feedwater Actuation, and a Feedwater Isolation occurred due to a turbine trip on a loss of main generator Stator Cooling Water (SCW) instrumentation. The plant was in Mode 1 - Power Operations, 100 percent reactor power, at normal operating pressure and temperature.<br /><br /> The SCW low flow turbine trip signal and subsequent reactor trip signal were received during the calibration of the SCW inlet conductivity meter. During restoration of power to the conductivity meter, a conductive foreign particle created a dead short across the power supply leads of the meter assembly. The subsequent transient caused the failure of a 10 amp fuse resulting in a loss of main generator SCW instrumentation power. The loss of instrumentation power initiated a turbine runback at 1328. <br /><br /> With the "loss of SCW flow" signal still present, the main generator protection circuitry initiated a turbine trip at 1331. <br /><br /> Several generator protection SCW runback modifications are being implemented to alleviate false activations and enhance the reliability of the system.
483 | 4831990007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831990007R00.pdf | 1990-06-11 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Callaway | P | WE | PO | 100 | On 6/11/90, at 1016 CDT, a Reactor Protection System (RPS) reactor trips a Feedwater Isolation (FWIS), and an Auxiliary Feedwater Actuation occurred following simulatenous closure of all four Main Steam Isolation Valves (MSIVs). The plant was in Mode 1 - Power Operations at 100 percent reactor power. The MSIVs closed due to a failed input buffer card in the MSIV manual fast close circuitry in the Main Steam and Feedwater Isolation System control cabinet. The failed input buffer card was replaced. <br /><br /> On 6/12/90, at 0501 CDT, while subcritical during reactor startup, four Bank 'B' Rod Control Cluster Assemblies dropped. Options were evaluated and at 0545, the reactor trip breakers were opened, manually tripping the reactor. A FWIS was received as anticipated. The plant was in Mode 2 - Startup (subcritical). A faulty rod control slave cycler counter card for the 1BD control rod power cabinet was identified and replaced. <br /><br /> During startup of the plant on 6/12/90, Operations Surveillance Procedure, "Main Turbine Trip Tests" (OSP-AC-00004), was not performed. This event was discovered on 6/18/90. The plant was in Mode 2 - Startup at 15 percent reactor power. This event was caused by the Shift Technical Advisor mistakenly reading the surveillance schedule book. OSP-AC-00004 was performed satisfactorily on 6/18/90. Notes were added to the surveillance schedule book to provide clarity. Individuals involved will be counseled.
483 | 4831990016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831990016R00.pdf | 1990-11-24 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 48 | On 11/24/90 at 0051 CST, with power being reduced at 20 percent per hour, a turbine trip occurred on a high Moisture Separator Reheater (MSR) high level signal. A reactor trip occurred within ten seconds due to low steam generator levels which had resulted due to the turbine trip. Engineered Safety Features Feedwater Isolation and, Auxiliary Feedwater Actuation were generated per design. The licensed operators immediately stabilized the plant in accordance with plant procedures. The plant was at 48 percent reactor power at the time of the trip, with reactor coolant system temperature at 571 degrees F and pressure at 2235 psig. <br /><br /> One MSR level device was inadvertently installed upside down, causing one high level signal to lock in. The spurious actuation of the second MSR level channel is attributed to vibration caused by the power reductions, This made up the two out of three logic for the MSR level trip signal. Due to narrow trip and reset tolerance, the MSR level devices were very sensitive to vibration. An actual high MSR level had not occurred. <br /><br /> The incorrectly installed MSR level switch was inverted and all 12 switches were adjusted to make them less susceptible to vibration-induced spurious actuations. Other similar level switches in the plant are being evaluated for potential set-up problems due to tight calibration tolerances.
483 | 4831990017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831990017R00.pdf | 1990-12-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 100 | On 12/30/90, at 1152 CST, a reactor trip occurred due to the failure of a controller/driver card for the 'B' Feedwater Regulating Valve (FRV). The FRV failed closed and could not be re-opened by the licensed operators from the Main Control Board in either the automatic or manual mode. The subsequent 'B' Steam Generator low water level actuated the reactor trip signal. As a result of the RPS actuation, a feedwater isolation (FWIS) and an auxiliary feedwater actuation (AFAS) were generated by design. The plant was in Mode 1 - Power Operations at 100 percent reactor power. The reactor coolant system temperature was 588 degrees F and the pressure was 2235 psig. The licensed operators recovered from the trip and Engineered Safety Feature (ESF) actuations via plant procedures. <br /><br /> The FRV controller/driver card was replaced at 1330 on 12/30/90. The manufacturer of the card is Westinghouse (component #2837A16G03). The plant was returned to Mode 1 - Power Operations at 0134 on 12/31/90. A capacitor in the power supply section of the card was the cause of the card failure. The failure of the capacitor is indeterminate. Corrective actions include the failure history and other applications of the use of this capacitor will be evaluated; and an evaluation will be performed to determine the feasibility of adding a redundant controller/driver card to the circuit for the FRV's.
483 | 4831991006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831991006R00.pdf | 1991-11-05 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Callaway | P | WE | PO | 100 | On 11/5/91, at 1031 CST, a reactor trip occurred due to the failure of a gating/sequencing card in the inverter (NN12) supplying a 120 volt AC safety-related instrument bus (NN02). The NN02 bus was de-energized. This failed a controlling feedwater channel resulting in a high water level in the 'A' steam generator which caused a Turbine Trip signal. The reactor trip occurred on a Unit Trip/Turbine Trip signal. A Feedwater Isolation and an Auxiliary Feedwater Actuation were generated by design. The plant was in Mode 1 - Power Operations at 100 percent reactor power. The reactor coolant system temperature was 588 degrees F and the pressure was 2237 psig. The licensed operators recovered from the trip and the Engineered Safety Feature actuations via plant procedures. The NN02 bus was energized from backup power via the Sola transformer at 1109. The failed inverter card was replaced and the inverter lined up to NN02 at 0242 on 11/6/91. <br /><br /> The plant was returned to Mode 1 - Power Operations at 2018 on 11/6/91. Corrective actions include: an analysis of the card failure; a determination if additional preventive maintenance for this card is necessary; procedures will be developed with NN bus load information for operator use; and operator training on this type of event will be developed and performed.
483 | 4831992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831992002R00.pdf | 1992-01-22 | QR8 | Spurious Reactor Trip | [45 empty] | Callaway | P | WE | PO | 100 | On 1/22/92, at 1106 CST, an automatic Reactor Coolant System Loop 'C' low flow reactor trip, Auxiliary Feedwater Actuation and Feedwater Isolation occurred. The plant was in Mode 1 at 100% power at the time of the trip. <br /><br /> Seven utility non-licensed personnel were working on valves in containment at the time of the event. The event was caused by one of the workers in containment inadvertently bumping open the five-valve manifold high side test port isolation valve on transmitter BB-FT-436. Due to the common high pressure sensing line serving the Loop 'C' flow transmitters, the momentary flow into the cavity between the test port plug and the valve seat produced a low pressure spike in the sensing line for the transmitters, thereby initiating the reactor trip. <br /><br /> The plant was returned to Mode 1 - Power Operations at 1705 on 1/23/92. <br /><br /> Corrective actions include an evaluation of methods to further visually identify to plant personnel loop flow and pressurizer pressure transmitters and their manifolds which, if disturbed, could cause a reactor trip. Additional guidelines will be established in the plant procedures for containment entries at power.
483 | 4831992007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831992007R00.pdf | 1992-05-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 97 | On 5/23/92, at 1713 CDT, Steam Generator 'C' Feedwater Isolation Valve, AEFV0041, fast closed causing a low level Steam Generator reactor trip and subsequent Feedwater Isolation. The cause was the failure of a relay driver card in the Main Steam and Feedwater Isolation System Train 'A' Cabinet SA075A. The card was replaced. The plant was in Mode 1N at 97% power with the Reactor Coolant System at 585 degrees F and 2230 psig at the time of the trip. The licensed operators responded to the trip per plant procedures.<br /><br /> The plant was returned to Mode 1 - Power Operations at 1142 on 5/26/92. Corrective actions include testing of the relay driver card. An evaluation will be made on options to improve the reliability of the system.
483 | 4831992010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831992010R00.pdf | 1992-09-20 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | On 9/20/92, at 0059 CDT, during performance of a weekly, preventive maintenance test of the main turbine thrust bearing wear detector, the plant experienced a turbine trip when a lockout relay contact failed. The Turbine trip subsequently caused an interlocked, automatic reactor trip, Feedwater Isolation, and Auxiliary Feedwater Actuation. The lockout relay was replaced. The plant was in Mode 1 at 100% power with the Reactor Coolant System at 588 degrees F and 2230 psig at the time of the trip. The licensed operators responded to the trip per plant procedures. <br /><br /> The plant was returned to Mode 1 - Power Operations at 0610 on 9/21/92. The lockout relay was replaced and satisfactorily tested prior to returning the unit to service. In order to minimize the potential for future trips during turbine system testing, a review of the current turbine test program was performed to evaluate the risk of a failure during testing causing a trip versus the reliability benefit gained from the testing. Test frequencies will be adjusted accordingly.
483 | 4831995004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831995004R00.pdf | 1995-06-08 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Callaway | P | WE | PO | 100 | On 6/8/95 at 0553 CDT, a reactor trip was automatically initiated due to Reactor Coolant System low flow caused by the tripping of Reactor Coolant Pumps (RCPs) 'C' and 'D'. The pumps were tripped via actuation of 13.8 KV bus PA02 negative phase sequence voltage relays (PA02132471B2 and PA02142472B2) in response to a two phase line to line fault caused by a tree limb blown onto one of two sets of transmission lines to the non-safety related intake water supply building. PA0210, the intake building feeder breaker fed from PA02, tripped due to time overcurrent relay (PA0210-250-251/f) actuation after the RCPs tripped. Opening of PA0210 led to tripping of various loads at the intake building. The negative phase sequence voltage relays actuated before PA0210 due to setpoint drift from the factory setting. The settings varied approximately 8% from the factory setting of the negative sequence filter. Licensed operators responded to the event and the plant was stabilized in accordance with emergency procedures. All safety-related systems performed as designed. The plant was in Mode 1 - Power Operations at 100% reactor power the time of the trip. <br /><br /> The limb was removed from the lines. A walkdown of the power lines from the plant to the intake structure was performed. No additional problems were found. The negative sequence filter in each of the relays in PA02 were checked and adjusted accordingly. Preventative maintenance task scope and frequency will be evaluated. In addition, enhanced protective relaying schemes will be evaluated. The plant was returned to Mode 1 - Power Operations at 1817 on 6/8/95.
483 | 4831995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831995005R00.pdf | 1995-08-16 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Callaway | P | WE | PO | 100 | On 8/16/95 at 0943 CDT, with the plant at 100% reactor power, the 'A' Circulating Water Pump breaker tripped due to a failed field excitation rheostat. This resulted in an automatic main turbine load setback with actuation of the main condenser steam dump valves. of the valves, caused pressure in the condenser to increase rapidly to the main turbine trip setpoint. The main turbine trip resulted in a reactor trip, feedwater isolation, and auxiliary feedwater actuation. <br /><br /> Subsequent investigation determined that main condenser pressure increased to the main turbine trip setpoint before Condenser Pressure Interlock (C-9) closure of the condenser steam dump valves could reduce pressure buildup. This was due in part to the main turbine trip and C-9 setpoints being out of tolerance. <br /><br /> The pump rheostat was replaced and the transmitters for the C-9 loops and main turbine trip switches were recalibrated. The plant was returned to Mode 1 at 0300 on 8/17/95. Improvements to circulating water pump field excitation system reliability and the design/calibration of the main turbine trip switches and C-9 transmitters will be evaluated.
483 | 4831996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831996001R00.pdf | 1996-04-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 100 | On 4/2/96, at 1045 CDT, a fuse in the 125vdc power supply to the yellow train fast close solenoid on 'B' Main Feedwater Isolation Valve (MFIV), AEFV0040, failed and caused the MFIV to close. The licensed control room operators immediately recognized the closure of the isolation valve, and understanding the inability to maintain steam generator levels with this condition, initiated a manual reactor trip with the plant in Mode 1 at 100% reactor power. All safety systems responded as expected. However, the source range channel N-32 for neutron flux detection failed high subsequent to the trip. <br /><br /> Investigation into the N-32 high flux alarm revealed that the high voltage power supply for neutron flux detection failed high. This resulted in N-32 reading high flux and alarm actuation. Licensed personnel responded in accordance with OTO-SE-00001, 'Source Range Nuclear Channel Failure' and entered Technical Specification 3.3.1 on the inoperable source range. The power supply for N32 was replaced. <br /><br /> The fuse failure was attributed to mechanical failure of the thermal link inside the fuse. The failure was not indicative of an electrical overload. The failed fuse and, as a precautionary measure, all corresponding MFIV fast close solenoid 125vdc power fuses were replaced. The plant was returned to Mode 1 at 0508 CDT on 4/3/96. Further evaluation into the source range high voltage power supply failure is being conducted.
483 | 4831999003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831999003R01.pdf | 1999-08-11 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Callaway | P | WE | PO | 100 | At approximately 0917 on August 11, 1999 with the plant operating at 100 percent power, a pipe rupture occurred in a six inch drain line located between the "D" Moisture Separator Reheater first stage reheater drain tank and the "6B" feedwater heater. The reactor was manually tripped and fast closure of the Main Steam Isolation Valves was manually initiated. No personnel were injured during this event and all safety related systems operated per design. Some non-safety related equipment failures were observed for components located in the vicinity of the pipe rupture. The location of the pipe rupture was determined to be immediately downstream of a 45 degree elbow. Root cause analysis indicates that the failure was attributed to Flow Accelerated Corrosion (FAC) with an abnormally high wear rate. The ruptured piping was replaced with Chromium - Molybdenum piping. Additional piping inspections were performed on locations with similar operating conditions/configurations with no other abnormal wear rates observed. Lessons learned from this event will be incorporated into FAC program guidelines for determining inspection points.
483 | 4831999008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4831999008R01.pdf | 1999-11-26 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Callaway | P | WE | PO | 100 | On 11/26/99 at 1227 CST with the plant at 100% power, a reactor trip occurred on low steam generator level due to a momentary power loss in control cabinet RP043. Annunciators initially alerted the control room of a power failure in this cabinet. Investigations revealed the primary power supply was deenergized and the secondary power supply was supplying the cabinet. An Equipment Operator (EO) was dispatched to investigate the primary power supply feeder breaker. However, the breaker number for the secondary power supply was given to the EO due to a misinterpretation of the annunciator response procedure. Upon investigation, the EO noted the breaker handle did not appear to be fully engaged in the closed position. The EO pushed the breaker handle towards the closed position to verify it was not tripped. At this point, the closed breaker contacts were momentarily interrupted resulting in a momentary power loss to the secondary power supply. As a result, the "A" main feedwater (MFW) regulating valve closed and both MFW pumps went to their low speed stop. The Reactor Operator attempted to take manual control of the MFW system, but was unsuccessful prior to the "A" steam generator reaching its low level reactor trip setpoint. All safety systems operated per design following the reactor trip. It was determined that procedures did not use standard terminology in referencing these power supplies. Personnel were also unaware of this molded case circuit breaker's inherent operational characteristic. The applicable procedure was clarified and other procedure revisions are under evaluation to standardize power supply terminology. Training will be provided to Operations personnel regarding this event.
483 | 4832000002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832000002R01.pdf | 2000-02-13 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [10 empty] | X | [29 empty] | X |  |  |  |  | Callaway | P | WE | PO | 100 | At 07:34 on February 13, 2000, automatic actuation of the reactor protection system (RPS) was initiated due to a low reactor coolant flow condition. This condition resulted when a reactor coolant pump (RCP) motor's protective relay sensed an electrical disturbance occurring on the transmission system, subsequently tripping the pump. The cause of the disturbance was attributed to a transmission line breaker failing to operate due to a defective electrical connection within the neighboring electric cooperative's protective relaying scheme. This resulted in an eight-minute system disturbance. At the time of the event, the plant was operating in Mode 1 at 100 percent power. Upon receiving the RPS actuation, all safety-related and nonsafety-related systems functioned per design.Ameren took corrective action to review the adequacy of their transmission system and RCP protective relaying setpoints. Completion of this review determined that Ameren's transmission system and RCP relay setpoints were adequate in the level of protection they provided and that the relays functioned per designed during the event. Ameren is also monitoring corrective actions of the electric cooperative, which has committed to installing backup relaying at the affected substation.
483 | 4832001003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832001003R00.pdf | 2001-03-09 | QR8 | Spurious Reactor Trip | [45 empty] | Callaway | P | WE | PO | 100 | At 1252, 3/9/01, with the Plant in Mode I at 100 percent Reactor Power, after opening the output breaker for 'B' Rod Drive Motor Generator (RDMG) in preparation for maintenance, the output breaker for 'A' RDMG opened. This deenergized the Rod Control System and caused all rods to insert into the Reactor (Rx) core. As a result of the rod insertion, primary temperature and pressure decreased and caused an OTdeltaT Rx trip to occur which opened both Rx Trip breakers. All systems operated as expected except for rod K-10 which had a faulty indication. The primary was borated an additional 150 ppm. Troubleshooting found a faulty circuit card which when replaced, corrected the K-10 indication problem. Plant startup and return to service was delayed by equipment problems with 'B' Main Feedwater Regulating Valve. After completion of repairs, the Plant returned to service on 3/13/01. The cause of the RDMG output breaker opening has been traced to a 40-volt ripple, which caused an over voltage condition to be sensed. The 40-volt ripple vanished the day after the trip and its source has not been determined.
483 | 4832002014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832002014R00.pdf | 2002-12-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Callaway | P | WE | PO | 100 | At 0421, 12/14/2002, Callaway plant experienced an automatic reactor trip on Overtemperature delta T (OTDT). The trip occurred while reducing power from 100 percent power to approximately 80 percent at 1 percent per minute to secure "C" Condensate pump due to an oil leak. While reducing power, OTDT penalty, points accumulated due to:a) control rod insertion which caused Axial Flux Deviation to go further negative,b) an existing Axial Offset Deviation andc) a pre-existing conservative gain adjustment in the electronic circuitry for the OTDT trip function.Control rods were placed in automatic at the beginning of the down power evolution in accordance with plant procedures. The accumulation of penalty points culminated in a rod stop and turbine runback. Subsequently at approximately 83 percent power, the reactor tripped on OTDT. Initial plant response, including Auxiliary Feedwater actuation, was per design. The Turbine Driven Auxiliary Feedwater Pump (TDAFP) was secured but later received a start signal when two steam generator (S/G) levels decreased below the actuation setpoint, and experienced an overspeed condition. SIG levels were restored to normal using the motor driven auxiliary feed pumps. The plant was stabilized in Mode 3 at normal operating temperature and pressure. Emergency Notification System notifications were completed at 0811.
483 | 4832004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832004002R00.pdf | 2004-01-27 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | At 1830, 1/27/04, while at 100 percent power, Callaway Plant experienced a main electrical generator trip which in turn caused a reactor trip due to power being above 50 percent. The cause of the generator trip was a failed electrical relay. This relay was designed to sense remote faults in order to prevent exceeding thermal limits for the stator windings. Plant systems responded as designed, including automatic actuation of the auxiliary feedwater system.The faulted relay was repaired, calibrated, and reinstalled. This relay contained a second set of unused contacts which were used instead of the initial faulted contacts. This relay configuration was successfully retested and plant operation resumed without further problems. A review of relevant operating experience did not identify similar failures, and a review of past plant preventative maintenance did not reveal abnormalities. Preventive maintenance procedures will be revised to provide additional detailed instructions for inspection of these relay contacts for this failure mechanism.
483 | 4832004003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832004003R00.pdf | 2004-02-03 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 10 | At 0439, 2/3/04, with Callaway Plant at 100 percent power, a reactor trip occurred while operating breakers in the site distribution switchyard. Plant operators responded to the event using plant procedures and stabilized the plant in Mode 3. All safety systems initially responded as required to the event. Investigations determined a faulted timer relay in the dead machine protection circuit for the main generator caused a trip of the main generator output breakers and subsequent reactor trip.3 hours 17 minutes after the trip, the Turbine Driven Auxiliary Feedwater Pump (TDAFP) tripped. Extensive methodical investigation resulted in replacement of three components in the control system, and the TDAFP was declared operable. Due to the complexity of the TDAFP investigation, an emergency one-time change to Technical Specification 3.7.5 was requested and approved.The failed timer relay in the dead machine circuit, and the three suspect control system components were all replaced and both pieces of equipment were returned to service.
483 | 4832004005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832004005R00.pdf | 2004-02-15 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Callaway | P | WE | PO | 26 | On 2/15/04, during plant startup and synchronizing to the grid, Callaway experienced oscillations in Steam Generator (SIG) levels which resulted in a main turbine generator trip and subsequent reactor trip. After the reactor trip occurred, to reduce the plant cooldown rate, operators attempted to secure the Turbine Driven Auxiliary Feedwater Pump (TDAFP). However, due to an automatic actuation signal being present, the TDAFP experienced an electrical and mechanical overspeed trip. Post trip investigations determined that the SIG oscillations were due to not having aligned extraction steam to provide feedwater preheating. The overspeed trip of the TDAFP was per system design. A TDAFP actuation signal was present when the operators closed the steam supply valves, causing the valves to reopen automatically and in such a sequence as to cause an overspeed condition. A Root Cause Analysis team was assembled and identified four Root Causes, plus several Corrective Actions to Prevent Occurrence.
483 | 4832005001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832005001R00.pdf | 2005-01-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 100 | At 1251, 1/19/05, a reactor trip occurred while replacing the primary power supply in Control Cabinet RP043. During replacement of the failed power supply, pressure was applied to the top of the secondary power supply located beneath the failed power supply. The top cover of the secondary power supply flexed inward and shorted out an energized heat sink that caused a momentary failure of that power supply. This resulted in "A" Main Feedwater Regulating Valve going closed and causing a reactor trip on Low-Low level in "A" Steam Generator (S/G). The plant was stabilized in Mode 3 and both the primary and secondary RP043 power supplies were replaced. Callaway Plant returned to power at 1735 on 1/20/05. A Root Cause Analysis was conducted and concluded that the impact of not placing pressure on top of a power supply was not clearly understood, work instructions did not adequately address power supply removal techniques, and appropriate tools were not available. Corrective actions include additional training, procurement or fabrication of necessary tools, and development of improved work instructions for future power supply replacements.
483 | 4832006004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832006004R01.pdf | 2006-05-12 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 47 | On 5/12/2006 reactor power was being reduced to 45% for a planned maintenance activity. Reactor power had been lowered to approximately 48% when vibration on main turbine bearings started rising eventually reaching the turbine trip criteria. The turbine was manually tripped at 0047 on 5/12/2006. Control rods subsequently stepped in under automatic rod control, as designed. The control rods continually stepped in reducing power below 10% in approximately four minutes. Feedwater flow was controlled through the Main Feedwater Regulating Valves which are not normally in service below 20% power. At 0052, the Steam Generator High-High Level setpoint was exceeded on the A Steam Generator resulting in a Feedwater Isolation Signal and Motor Driven Auxiliary Feedwater Actuation Signal. All safety systems responded as designed. A manual reactor trip was initiated at 0053 in accordance with procedural guidance for the loss of both main feedwater pumps. The cause of this event is an inadequate mitigation strategy in procedure OTO-AC-00001, "Turbine Trip below P-9" (50% power permissive setpoint). The procedural deficiency was the result of an inadequate procedure change review process used in 1991. Corrective Actions to Prevent Recurrence include revision of the procedure change review process and revision of OTO-AC-00001 to incorporate an appropriate mitigation strategy.
483 | 4832007002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832007002R00.pdf | 2007-03-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 30 | On March 9, 2007, while operating at 100 percent power, Callaway Plant experienced a main condenser tube leak. At 0824, high sodium levels were indicated in the main steam condenser, requiring power reduction to less than five percent power until all Action Levels for condenser sodium were exited. The on-shift Operations crew began reducing power to enter MODE 3 in accordance with procedural guidance. During the transition from the Main Feedwater Regulation Valves (MFRV) to the Main Feedwater Regulation Bypass Valves(MFRBV), problems were experienced controlling water level in the "C" steam generator (S/G). At 1043, with both the MFRV and MFRBV indicating closed and the "C" S/G level still increasing, the reactor was manually tripped. The level control problem was attributed to a failed 1/P positioner on the MFRV. The controller was replaced with a like kind controller.Digital rod position indication for control rod K10 failed during the event. The control rod was fully inserted. This failure was attributed to a bent connector pin in the digital rod position indication system. The connector pin was repaired and tested satisfactorily.
483 | 4832008005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832008005R00.pdf | 2008-11-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Callaway | P | WE | PO | 97 | On 11/11/2008, while operating at 97-percent reactor power, with power increasing following Refuel 16, the "B" main feedwater pump (MFP) turbine tripped. Since the loss of one MFP at greater than 80-percent power challenges the plant's ability to maintain steam generator (SG) water levels to support continued plant operations, the reactor was manually tripped per plant operating procedures.All control rods fully inserted during the event and all safety systems responded as designed. Operation of the Auxiliary Feedwater system restored SG levels. Operation of the main steam supply system provided the heat sink for decay heat removal following shutdown. No primary relief valves or main steam relief valves lifted during the event. No primary to secondary leakage existed. No radioactive material was released. This event was considered an uncomplicated reactor trip.The cause was that the o-rings in the MFP lube oil strainer were a material susceptible to swelling in petroleum-based lubrication systems. An o-ring originally located in one of the MFP lube oil basket strainers swelled, became dislodged, and traveled into a MFP turbine bearing oil supply pressure regulating valve. The corrective actions to prevent recurrence included identification of a replacement for the o-rings. The correct o-rings were installed in both strainers for the "A" and "B" MFP turbine oil system.
483 | 4832008006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832008006R01.pdf | 2008-12-11 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Callaway | P | WE | PO | 100 | At 2254 on December 11, 2008 the 'C' condensate pump tripped. After confirming the trip, operators began a reduction in power and entered the Callaway off-normal procedure for Feedwater System Malfunction. However, the manual load reduction rate was approximately 31% in one minute, exceeding the procedural guidance of 5% per minute. At 2256 the control rods automatically stepped in and the condenser steam dumps opened as designed. Subsequently, steam generator (SIG) level deviation annunciators actuated for all 4 S/Gs and a turbine trip/reactor trip occurred at 2300. The turbine tripped on a Hi-Hi S/G level feedwater isolation signal (FWIS) from the 'B' S/G, and the reactor trip immediately followed. Additionally, as a result of the FWIS, both main feedwater pumps tripped. Hence, a motor-driven auxiliary feedwater actuation occurred as expected.Investigations were performed for the 'C' condensate pump motor failure and system actuations. The root cause of the motor failure was determined to be a ground fault. The root causes of the system actuations (including the reactor trip) were human performance errors which resulted in the excessively rapid load reduction and a configuration control process deficiency related to field-tuning of the feedwater controller gain settings. The corrective actions to prevent recurrence of these root causes are discussed in Section III.
483 | 4832008008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832008008R00.pdf | 2008-12-14 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Callaway | P | WE | PO | 98 | On 12/14/2008, while operating at 98-percent reactor power with two of three condensate pumps available and running, the control room received steam generator (SG) feed flow/steam flow mismatch annunciators followed by SG level deviation alarms. Immediately thereafter, control room operators confirmed the loss of the "B" condensate pump. With only one condensate pump running at greater than 45-percent reactor power, the reactor was manually tripped.All control rods inserted during the event and all safety systems responded as designed. Operation of the Auxiliary Feedwater system restored SG levels. Operation of the main steam supply system adequately provided the heat sink for decay heat removal following shutdown. No primary to secondary leakage existed. No radioactive material was released. This event was considered an uncomplicated reactor trip.The cause of the "B" condensate pump trip is a stator turn-to-turn winding failure of the pump motor that progressed to a ground fault. The Root Cause is voltage surge damage to motor winding insulation. The Corrective Action to Prevent Recurrence is to install surge capacitors at the condensate pump motor lead boxes to minimize the slope of the voltage transient wave front.
483 | 4832013008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832013008R00.pdf | 2013-07-26 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Callaway | P | WE | PO | 100 | At approximately 2333 on July 26, 2013, electrical faults caused damage to the isophase bus to the unit auxiliary transformer and main generator neutral connection box. Protective relaying initiated a generator trip to isolate the faulted area and to trip the main turbine. A reactor trip from 100% power resulted from the turbine trip. A small cable insulation and oil collection pan fire initiated from the main generator neutral connection box fault and created smoke throughout the Turbine Building. An Unusual Event was declared as a result of the fire and resulting smoke.<br /><br /> The fire was extinguished within 30 minutes and smoke was removed from the building using installed equipment.<br /><br /> The electrical faults were the result of a damper blade that was loose within the isophase bus ductwork, creating arcing between the bus, damper blade, and duct. The loose damper blade is attributed to damper failure based on the determination that the operational isophase bus duct airflow rate exceeded the design flow rate for the backdraft dampers. Design and installation errors were made at the main generator neutral connection box during plant construction.<br /><br /> Redesigned backdraft dampers were installed, and grating was added to prevent debris from entering the isophase bus ducts. Modifications were also made to the generator neutral connection box.
483 | 4832014006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832014006R00.pdf | 2014-12-03 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | At 00:22 hours on December 3, 2014, during normal power operations, A turbine and reactor trip occurred, when the main generator excitation transformer faulted to ground. The reactor trip was classified as "uncomplicated." Safety systems performed as designed. During recovery the valve providing flow from Motor Driven Auxiliary Feedwater Pump "B" to Steam Generator "D" failed to throttle closed afterwards. Repair of the excitation transformer was completed and the plant returned to power operations on December 6, 2014.<br /><br /> The construction of the excitation transformer includes high voltage jumper cables between termination points inside its protective enclosure and the winding taps of the transformer coils. These jumper cables are routed above the iron core of the transformer and are supported by insulating boards as well as restrained by nylon cable ties. The fault to ground was caused when a jumper cable dropped onto the iron transformer core after failure of the nylon cable ties. These cable ties were an original part of the transformer installed in 2007.<br /><br /> The root cause of the transformer failure was inadequate design (routing cables above the transformer core) and material selection (use of nylon cable ties) during the manufacture of the transformer.
483 | 4832015003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4832015003R01.pdf | 2015-08-11 | QR5 | Turbine Trip | [45 empty] | Callaway | P | WE | PO | 100 | On August 11, 2015, at 01:39 Callaway plant tripped from 100% power due to an incorrect, automatic response to a transmission line fault on the Montgomery-Callaway 8 line by transformer bus differential relaying. This resulted in Reactor Protection System (RPS) and Auxiliary Feedwater System actuations. The plant response to the trip was as expected except for a problem encountered with Auxiliary Feedwater flow control valve ALHV0007 subsequent to the plant trip. <br /><br /> This event was caused by the inadvertent inclusion of jumpers in the current transformer (CT) circuits of the main transformers that were installed as part of Main Transformer Replacement Modification 09-0044 implemented in Refuel 19. Following the event, the inadvertently placed CT jumpers were removed and the plant was successfully restarted.<br /><br /> The root cause of the incorrect main transformer CT wiring was that a drawing originally depicting the wiring configuration was not revised properly when it was converted from a generic Standardized Nuclear Unit Power Plant System (SNUPPS) drawing (E-03MA02) to a Callaway-specific drawing (E-23MA02) in the 1983 timeframe. This eventually resulted in design and testing errors during modification development. <br /><br /> Corrective actions include additional design, testing and job reviews, as well as reviews of similar drawings to identify and correct missing information.
498 | 4981988026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981988026R00.pdf | 1988-03-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | South Texas 1 | P | WE | SU | 7 | POWER LEVEL - 007%. AT APPROXIMATELY 2112 HOURS ON MARCH 30, 1988 WITH UNIT 1 IN MODE 1 AT 7% POWER, A PARTIAL LOSS OF OFFSITE POWER RESULTED IN A REACTOR TRIP. A LOW-LOW COMPENSATED T-COLD SIGNAL INITIATED A SAFETY INJECTION (ESF ACTUATION) SEQUENCE. A NOTIFICATION OF UNUSUAL EVENT WAS DECLARED. ALL SAFETY SYSTEMS FUNCTIONED NORMALLY AND OFFSITE POWER WAS RESTORED AT APPROXIMATELY 2202 HOURS ON MARCH 30, 1988. LOSS OF OFFSITE POWER OCCURRED DUE TO PERSONNEL ERROR BY PLANT ELECTRICIANS WHO INADVERTENTLY TRIPPED THE SWITCHYARD SUPPLY BREAKERS WHILE THEY WERE INVESTIGATING A PREVIOUS MAIN GENERATOR TRIP. A DESIGN INADEQUACY IN THE EXCESSIVE COOLDOWN PROTECTION SYSTEM RESULTED IN A SUBSEQUENT SAFETY INJECTION ACTUATION. CORRECTIVE ACTIONS INCLUDE INCORPORATION OF A CASE STUDY OF THIS EVENT INTO TRAINING SESSIONS FOR MAINTENANCE PERSONNEL AND AN EVALUATION OF THE EXCESSIVE COOLDOWN PROTECTION SYSTEM TO PREVENT FUTURE UNNECESSARY SAFETY INJECTION ACTUATIONS.
498 | 4981988045 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981988045R00.pdf | 1988-07-19 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 1 | P | WE | PO | 54 | POWER LEVEL - 054%. ON JULY 19, 1988, AT 0922 HOURS WITH UNIT 1 IN MODE 1 AT 54 PERCENT POWER, A REACTOR TRIP OCCURRED ON OVER TEMPERATURE/DELTA TEMPERATURE. NO SAFETY INJECTION OCCURRED AND PLANT EQUIPMENT PERFORMED AS EXPECTED. THE CAUSE OF THE TRIP WAS PERSONNEL ERROR. AN HL&P INSTRUMENTATION AND CONTROLS (I&C) TECHNICIAN RESET A CHANNEL OF THE QUALIFIED DISPLAY PROCESSING SYSTEM (QDPS) WHILE A REDUNDANT CHANNEL WAS IN TEST. CORRECTIVE ACTIONS INCLUDE ADDITION OF DETAILED INSTRUCTIONS ON QDPS RESET TO APPLICABLE PROCEDURES, TRAINING OF I&C TECHNICIANS, INITIATION OF A VERIFICATION BY RESPONSIBLE FOREMEN OF I&C TECHNICIAN ACTIONS WHICH COULD AFFECT THE OPERATION OF THE REACTOR TRIP SYSTEM (RTS), REVISION OF MAINTENANCE PROCEDURES TO INCLUDE HUMAN FACTORS CONSIDERATIONS AND AN EVALUATION OF THE FEASIBILITY OF REVISING THE SEPARATION GROUPS ASSIGNED TO THE QDPS PROCESSORS TO MAKE THEM CONSISTENT WITH THE RTS CHANNELS.
498 | 4981988048 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981988048R00.pdf | 1988-08-16 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1053 HOURS ON AUGUST 16, 1988, WITH UNIT 1 IN MODE 1 (POWER OPERATION) AT 100 PERCENT POWER, A REACTOR TRIP OCCURRED AS A RESULT OF A MAIN TURBINE TRIP. THE TURBINE TRIP WAS ATTRIBUTED TO LOW STATOR COOLING WATER FLOW, WHICH RESULTED FROM FAILURE OF A DISCHARGE CHECK VALVE TO CLOSE WHEN A PUMP WAS SECURED IN PREPARATION FOR PREVENTIVE MAINTENANCE. THE AUXILIARY FEEDWATER SYSTEM ACTUATED ON LOW STEAM GENERATOR LEVEL, WHICH IS NORMAL FOR A TRIP FROM FULL POWER, AND MAIN FEEDWATER ISOLATED. PLANT SYSTEMS RESPONDED AS DESIGNED, AND OPERATORS STABILIZED THE PLANT IN ACCORDANCE WITH APPROVED PROCEDURES. CORRECTIVE ACTIONS INCLUDED REPLACING THE PACKING ON THE CHECK VALVE AND INCREASING THE TIME DELAY FOR A TURBINE TRIP FROM LOW STATOR COOLING WATER FLOW.
498 | 4981988049 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981988049R00.pdf | 1988-08-26 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | South Texas 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON AUGUST 26, 1988 WITH UNIT 1 IN MODE 1 AT 100 PERCENT POWER, A REACTOR TRIP OCCURRED DUE TO A TURBINE TRIP AT 1724 HOURS. A SAFETY INJECTION ACTUATION SUBSEQUENTLY OCCURRED ON LOW STEAM PRESSURE AT 1728 HOURS DUE TO MISOPERATION OF THE MAIN STEAM ISOLATION CONTROLS BY A CONTROL ROOM OPERATOR. THE CAUSE OF THE TURBINS TRIP WAS DETERMINED TO BE A DEFECTIVE FUSE BLOCK IN THE STATOR COOLING WATER TRIP CIRCUIT WHICH CAUSED INTERMITTENT DE-ENERGIZATION OF THE STATOR COOLING WATER LOW DIFFERENTIAL PRESSURE TIME DELAY RELAY. CORRECTIVE ACTIONS INCLUDE REPLACEMENT OF THE FUSE BLOCK, EVALUATION OF THE STATOR COOLING WATER TRIP CIRCUITRY AND OPERATOR TRAINING.
498 | 4981989001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981989001R00.pdf | 1989-01-03 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1317 HOURS ON JANUARY 3, 1989 WITH UNIT 1 IN MODE 1 AT 100% POWER, A REACTOR TRIP OCCURRED ON OVER TEMPERATURE/DELTA TEMPERATURE AS A RESULT OF A FAILURE IN THE MAIN TURBINE GENERATOR ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM WHICH CLOSED THE TURBINE GOVERNOR VALVES. THE MOST PROBABLE CAUSE OF THIS EVENT WAS DETERMINED TO BE A POORLY CRIMPED LUG ON AN INTERCONNECTING WIRE WHICH SUPPLIED POWER TO SEVERAL FRAMES OF PRINTED CIRCUIT CARDS IN THE EHC CABINET. THIS RESULTED IN A HIGH RESISTANCE CONNECTION WHICH DROPPED THE POWER SUPPLY VOLTAGE TO SEVERAL CARDS WHICH CONTAIN DIGITAL AND ANALOG CIRCUITS RESPONSIBLE FOR CONTROL OF TURBINE VALVES, TURBINE PROTECTION AND OPERATOR INTERFACE. CORRECTIVE ACTIONS INCLUDE REPLACEMENT OF THE DEFECTIVE WIRE AND CHECK OF OTHER SIMILAR WIRES FOR EXCESSIVE VOLTAGE DROP.
498 | 4981989005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981989005R00.pdf | 1989-01-20 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | South Texas 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 20, 1989, UNIT 1 WAS IN MODE 1 AT 100% POWER. AT 1017 HOURS, ALARMS WERE RECEIVED IN THE CONTROL ROOM FOR TURBINE GENERATOR HIGH VIBRATION, AND BEARING 8 AND 9 HIGH TEMPERATURE. A FIRE WAS SUBSEQUENTLY REPORTED AT BEARING 9. THE DELUGE SYSTEM WAS ACTUATED, THE TURBINE WAS MANUALLY TRIPPED AND THE REACTOR AUTOMATICALLY TRIPPED AT 1123 HOURS. THE FIRE WAS EXTINGUISHED IN 14 MINUTES. THE CAUSE OF THE EVENT WAS LOSS OF COOLING OF THE GENERATOR HYDROGEN. THE RESULTING INCREASE IN HYDROGEN TEMPERATURE AND PRESSURE CAUSED LEAKAGE FROM THE BEARING SEALS. THE LOSS OF COOLING OF THE HYDROGEN IS BELIEVED TO HAVE BEEN CAUSED BY A LOOSE TEMPERATURE SENSOR CONNECTION TO THE HYDROGEN GAS TEMPERATURE CONTROLLER. THE EFFECTS OF THE LOSS OF COOLING WERE NOT IMMEDIATELY DETECTED DUE TO THE FAILURE OF TWO INPUTS TO THE HYDROGEN SYSTEM COMMON TROUBLE ALARM IN THE CONTROL ROOM. CORRECTIVE ACTIONS INCLUDE INSPECTION OF THE GENERATOR, REPAIR OF THE BEARING SEALS, REPAIR OF THE HYDROGEN CONTROLLER, MODIFICATION OF THE CONTROLLER DESIGN AND REPAIR OF THE INPUTS TO THE CONTROL ROOM ANNUNICATOR.
498 | 4981989015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981989015R01.pdf | 1989-07-04 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 7/4/89, UNIT 1 WAS IN MODE 1 AT 100% POWER. AT 1915 HOURS, THE MAIN GENERATOR OUTPUT CIRCUIT BREAKER OPENED. THE MAIN TURBINE GOVERNOR VALVES CLOSED TO LIMIT TURBINE OVERSPEED AND A REACTOR TRIP SYSTEMS RESPONDED AS DESIGNED AND NO UNEXPECTED POST-TRIP TRANSIENTS OCCURRED. THE CAUSE OF THIS EVENT WAS THE FAILURE OF A 125 VDC RATED AUXILIARY RELAY WHICH WAS ERRONEOUSLY USED IN THE 250 VDC GENERATOR CIRCUIT BREAKER TRIP CIRCUIT. IT HAS BEEN DETERMINED THAT THE INCORRECT RELAY WAS SUPPLIED TO HL&P BY THE VENDOR. AN ERROR WAS MADE IN TRANSPOSING THE HL&P PURCHASE ORDER REQUIREMENTS TO THE VENDOR'S PURCHASE ORDER WITH THE RELAY SUB-SUPPLIER. SINCE THE VENDOR TAGGED THE RELAYS CORRECTLY, THE ERROR WAS NOT DETECTED DURING RECEIVING VERIFICATION. THE FAILED RELAY AND ONE OTHER 125 VDC RELAY HAVE BEEN REPLACED WITH THE CORRECT MODEL. 250 VDC CONTROL CIRCUITS IN UNIT 2 HAVE BEEN INSPECTED FOR SIMILAR RELAYS WHICH ARE NOT OF THE CORRECT RATING. NO OTHERS WERE FOUND.
498 | 4981990005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990005R00.pdf | 1990-03-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On March 29, 1990, Unit 1 was in Mode 1 at 100 percent power. At approximately 1443 hours, Feedwater Booster Pump (FBP) 11 tripped upon actuation of a ground fault relay. The standby pump, FBP 13, automatically started; but did not deliver sufficient flow to prevent Steam Generator Feedwater Pump 12 from tripping on low suction pressure. Attempts to maintain steam generator level were unsuccessful and the reactor tripped on low steam generator level. The plant was brought to a stable shutdown in Mode 3. The cause of the FBP 11 trip has not yet been identified; however, it is believed that a weakness of the FBP 11 windings or feeder cables aggravated by moisture intrusion and dirt due to clogged air inlet filters resulted in the ground fault. Corrective action is being taken to disassemble, inspect and clean the FBP 11 motor during the current refueling outage. The preventive maintenance activity to inspect the pump motor has been revised to periodically inspect and clean the cooling air filters. Backup FBP 13 did not provide adequate flow because the recirculation valve had been manually set in the open position until the valve controller could be repaired. Repair to the FBP 13 recirculation valve controller will be completed during the current refueling outage.
498 | 4981990014 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990014R00.pdf | 1990-06-20 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 1 | P | WE | SU | 15 | On June 20, 1990 at 0410 hours with Unit 1 in Mode 1 at 15% power while performing synchronization of the main generator to the grid, a reactor trip-turbine trip occurred due to undervoltage to the reactor coolant pumps. During the event electrical power was lost to the Digital Rod Position Indication (DRPI) system, necessitating a manual emergency boration since it could not be verified that all rods were on bottom. The reactor trip was initiated by a generator breaker lockout which was caused by the spurious actuation of a generator breaker pole failure relay. This generator breaker lockout led to the loss of power to the Unit Auxiliary Transformer with resulting loss of power to the reactor coolant pumps and subsequent reactor trip. Corrective actions include calibrating the relay and including it in the preventative maintenance program. In addition, corrective actions are being considered to minimize the possibility of loss of power events during generator synchronization.
498 | 4981990015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990015R00.pdf | 1990-06-28 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 76 | At 0554 hours on June 28, 1990 with Unit 1 in Mode 1 at 76 percent power a reactor trip occurred due to a turbine trip which was caused by low electrohydraulic control (EHC) system fluid pressure. The plant was brought to a stable condition in Mode 3. The cause of this event was failure of an EHC supply line to a main turbine generator throttle valve. The line failed due to excessive vibration induced by oscillation in a main turbine generator governor valve. The oscillations were caused by a loose connection in the control circuit. Investigation revealed that the EHC System piping contained a number of less than adequate supports and that portions of the piping had less than the specified wall thickness. Corrective actions include repairing the loose connection and replacing the less than adequate piping and supports.
498 | 4981990016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990016R00.pdf | 1990-07-02 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | South Texas 1 | P | WE | PO | 100 | On July 2, 1990, Unit 1 was in Mode 1 at about 100 percent power. At 1808 hours a reactor trip was initiated when 2 out of 4 coincidence was satisfied on over temperature/delta temperature (OT Delta T). Unit 1 was in power ascension and Loop 4 Delta temperature and T average bistables were in a trip condition to support the surveillance in progress. Due to a decrease in Reactor Coolant System (RCS) pressure, Loop 3 OT Delta T tripped when the setpoint reached the actual Delta T. Two of the four channels in a tripped condition satisfied the trip logic and initiated the reactor trip. A Feedwater Isolation occurred on low average Reactor Coolant System temperature and an Auxiliary Feedwater System actuation occurred on low steam generator level as expected. The Main Steam Isolation Valves were manually closed to limit the cooldown and the plant was stabilized in Mode 3. No unexpected post trip transients were observed. Corrective actions to prevent this incident include logging OT Delta T and actual Delta T every shift and requiring that power not be increased when above 90 percent unless all channels of OT Delta T are operable during power ascension.
498 | 4981990020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990020R00.pdf | 1990-07-16 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | At 0236, on July 16, 1990 with Unit 1 at 100% power, a reactor trip occurred during performance of a Solid State Protection System (SSPS) surveillance test. The trip was caused by a malfunction in a test switch which resulted in one train of SSPS remaining in the Urgent Alarm condition, coupled with completion of a subsequent procedural step that placed the other SSPS train in the Urgent Alarm condition. The SSPS is designed such that if both logic trains are placed in the Urgent Alarm condition, a reactor trip occurs. The test switch will be replaced prior to startup from the next refueling outage. In addition, test procedures have been revised to ensure that Urgent Alarm conditions are satisfactorily cleared prior to continuing with procedural steps that could result in a reactor trip.
498 | 4981990006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990006R00.pdf | 1990-07-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On July 30, 1990, Unit 1 was in Mode 1 at 100% power. At approximately 1946, Feedwater Isolation Valve 1A fully closed during a partial stroke surveillance test. The resultant loss of feedwater flow caused a decrease in steam generator level and the reactor was manually tripped. The unit was stabilized with the exception of level in Steam Generator 1A which did not recover due to a mispositioned recirculation test valve in the Train A Auxiliary Feedwater System (AFW). The recirculation test valve was returned to the required position and Steam Generator 1A level was recovered. The Feedwater Isolation Valve closure was caused by a technician inadvertently contacting the wrong terminal with a test jumper. The cause of the mispositioned recirculation test valve could not be conclusively established; however, it is likely that the valve was not correctly repositioned during a surveillance test prior to the event, and this error was not discovered due to a lack of adequate independent verification. Corrective actions include: issuance of training bulletins concerning use of jumpers; evaluation of alternative designs to obviate the need to perform the partial stroke test with jumpers; and, issuance of a memorandum to operations personnel to reinforce the requirements pertaining to independent verification.
498 | 4981990023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990023R00.pdf | 1990-09-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On September 29, 1990, Unit 1 was in Mode 1 at 100% power. At 0232 hours, Feedwater Isolation Valve 1A fully closed during an "alternate" partial stroke surveillance test. The resultant loss of feedwater flow caused a decrease in steam generator level and the reactor was manually tripped. During recovery, a Steam Generator Power Operated Relief Valve (PORV) was manually opened to approximately 30% while indicating approximately 5% open. At 0345 hours, an Auxiliary Feedwater (AFW) actuation occurred on low-low Steam Generator (SG) level. The SG PORV was closed, and the plant was stabilized. The Feedwater Isolation Valve closure was caused by a technician inadvertently contacting the wrong terminal with a test jumper. The cause of the AFW actuation during recovery was failure of a Reactor Operator to confirm the position of the SG PORV by monitoring SG level and pressure indications when the Valve Position Indicator displayed some uncertainty. Corrective actions include: addition of special connectors on the terminals identified in the "alternate" partial stroke test procedure; the use of special insulated jumpers during performance of the stroke test; performance of the partial stroke test on a monthly basis vice weekly; development of a training module emphasizing the importance of attention to detail of self verification which was presented to employees engaged in operations and maintenance of the plant.
498 | 4981990025 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981990025R01.pdf | 1990-11-24 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On November 24, 1990, Unit 1 was in Mode 1 at 100% power. At 1448 hours, the generator running ground fault relay actuated due to a stator coil end turn failure which initiated an automatic reactor trip. All systems responded as expected. Feedwater isolation occurred on low Reactor Coolant System average temperature, and Auxiliary Feedwater (AFW) actuated on low - low steam generator level as expected. Initial internal inspection of the generator revealed damage to the end turn of bottom stator coil #23 at the turbine end. The stator coil end turn failure was due to vibration-induced fatigue cracking brought on by excessive end turn vibration which resulted from structural degradation of generator blocking and lacing. The most probable cause of the structural degradation was latent damage that resulted from the January 20, 1989 generator hydrogen cooling transient (refer to LER 89-005). Extensive remedial actions to repair the damage have been implemented for the Unit 1 generator. Corrective actions include installation of "Winding Improvement Modules;" installation of an End Turn Vibration Monitoring System; and, installation of a dual tower hydrogen gas dryer. The latter two actions are also scheduled to be implemented in Unit 2. A Turbine-Generator Task Force, consisting of HL&P and Westinghouse personnel, has been initiated to address issues of concern regarding the Units 1 & 2 turbine-generator and to exchange relevant operational information.
498 | 4981991012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981991012R01.pdf | 1991-04-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | South Texas 1 | P | WE | PO | 40 | On April 12, 1991, at 0418, the Unit 1 reactor tripped from 40% power. A turbine trip, feedwater isolation and auxiliary feedwater actuation occurred as a result of the reactor trip. Systems operated as designed in response to the reactor trip. It was determined that Rod Drive Motor Generator (RDMG) Set #11 tripped due to a transient induced by RDMG #12 which was found running with its motor and generator breakers closed with no output voltage to the Reactor Trip Switchgear. It is believed that intermittent pick-up and drop-out of the 2R relay, which actuates contacts to supply power to the RDMG Set #12's generator voltage regulator, caused instability in the voltage regulator operation. The 2R relay malfunction was due to a defective output switch. The instability of the voltage regulation resulted in transients that caused a reverse current to the RDMG Set #11 and a subsequent trip of the generator output breaker. It is also believed that the 2R relay contacts supplying power to the voltage regulator eventually remained open long enough to allow a loss of the generator field in the RDMG Set #12. A loss of the generator field results in zero output voltage from the generator. The loss of both of the power sources to the Reactor Trip Switchgear resulted in a reactor trip. The 2R relay's timer and control relay were replaced and a procedural change has been made to enhance the detection of relay timer malfunctions. An additional procedural change has been made to require the marking of leads that do not have unique identification markings.
498 | 4981991021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981991021R00.pdf | 1991-10-10 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 1 | P | WE | PO | 100 | On October 10, 1991, at 2056, Unit 1 was in Mode 1 at 100% power when power from the 1J Bus was lost. During the performance of work activities, a Maintenance Electrician misapplied multimeter test leads in an energized circuit with the multimeter set to read "RESISTANCE". The misapplied test leads energized relay 2A which actuated the 86X lockout relay causing breaker P150 to trip and de-energize the 1J Bus. Upon loss of power on 1J Bus, Reactor Coolant Pump (RCP) 1D tripped and caused a reactor trip due to low coolant flow. The bus was re-energized at 2059 from the Unit Auxiliary Transformer with no further incidents. The primary cause of this event was personnel error. The Maintenance Electrician's attention to detail during work performance, elementary drawing reading and troubleshooting techniques were less than adequate. A training session is being held for appropriate Plant Personnel stressing the application of Self Verification during work performance.<br /><br /> A testing program will be implemented to ensure that applicable personnel are qualified to use elementary drawings to aid in performance of maintenance activities.
498 | 4981991022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981991022R00.pdf | 1991-10-14 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On October 14, 1991, at 2304 hours, Unit 1 was in Mode 1 at 100% power. Solid State Protection System (SSPS) Logic Train R Functional Test was in progress when the Licensed Operator performing the surveillance misunderstood the intent of a note in the procedure and failed to block the Turbine Trip signal before proceeding to the next step. The "Memories" test switch was placed in position 16 and an automatic Train R trip signal was generated. Train R trip signal generated a "Turbine Trip upon Reactor Trip" signal which had not been blocked and the "Memories" test switch also malfunctioned, which if it had functioned properly should have also blocked the trip signal. Subsequently, the Main Turbine tripped and, coincident with a "Reactor Power Above 50%" signal, a valid Train S Reactor Trip signal was generated tripping the reactor. The cause of this event was personnel error by the Licensed Operator who exercised poor judgement while performing the test. Contributing factors were a less than ideal procedure and the malfunction of the "Memories" test switch. Corrective actions include site-wide training sessions for appropriate plant personnel stressing the application of self verification during work performance, counseling of the licensed operator involved in the event, revision of all SP series surveillances performed at power that have the potential to trip the unit/main turbine, to specifically require that an appropriate turbine/reactor trip block be instituted whenever there is a possibility that the SSPS will generate an unwanted trip signal.
498 | 4981992003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981992003R01.pdf | 1992-03-14 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On March 14, 1992, Unit 1 was in Mode 1 at 100% power. A reactor trip occurred at approximately 1108 hours from a momentary false reactor coolant low flow trip signal. Instrumentation & Control Technicians calibrating the Reactor Coolant flow transmitter reversed the procedural sequence of restoring the transmitter causing a momentary low (below setpoint) differential pressure to be detected by the two adjacent flow transmitters. This event completed the logic in the Solid State Protection System to trip the reactor. The cause of this event was failure to follow procedures which resulted from insufficient supervisory and management emphasis on the risk associated with the task, and a limited sense of responsibility by the technicians to ensure proper task completion. The actions taken to correct the event are: supervision is required to be present to ensure emphasis is placed on completing the activity correctly when a potential reactor trip could occur; clear direction for use and physical presence of procedures has been provided to maintenance craftsmen; and a memorandum from management was issued emphasizing the self-checking principle.
498 | 4981994009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981994009R01.pdf | 1994-02-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 29 | On February 28, 1994 at 2212 hours, Unit 1 was in Mode 1 at 29% power when a steam flow/feed flow mismatch alarm was received on Steam Generator ID. The reactor was manually tripped at 2213 hours following an unsuccessful attempt to take remote manual control of the ID Main Feedwater Regulating Valve. The malfunction of the 1D Main Feedwater Regulating Valve was caused by a failed transformer coil in the torque motor in the current to pneumatic convertor (Fisher Controls Type 546 Current to Pneumatic Converter). The root cause of the failed transformer coil has been attributed to a weak solder connection on one end of a wire which connects the two sets of transformer coils together in the torque motor section of the convertor. Corrective actions include performing failure analyses on the current to pneumatic convertor and the associated Westinghouse 7300 Series driver card which had failed and was replaced earlier. The failed current to pneumatic convertor was replaced as were two other Unit 1 current to pneumatic convertors.
498 | 4981994015 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981994015R01.pdf | 1994-09-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On September 20, 1994, Unit 1 was in Mode 1 at 100% power. At 0105 hours, Unit 1 received an automatic reactor/turbine trip due to Steam Generator 1C low-low level. Immediately prior to the unit trip, efforts were in progress to reduce Reactor Power and Turbine Load following the unanticipated trip of the #13 Steam Generator Feedwater Pump. The cause of this event was that management expectations, procedural guidance, training, and personnel experience placed initial emphasis on expected plant response rather than actual plant conditions. This event was initiated when Steam Generator Feedwater Pump tripped on overspeed due to a failed speed feedback device (Tachometer Pack) in the speed control circuits. Contributing causes were determined to be inadequate communications and the Start-up Feedwater Pump recirculation valve not closing due to a coarse gain misadjustment on the flow controller card in the Miscellaneous Analog Cabinet and internal damage on the valve. Corrective actions include discussing managements expectations regarding the use of all indications for proper equipment operations and crew communications with the involved crew, revising the off-normal procedure, replacing a failed speed sensor, ensuring proper operation of the Start-up Feedwater Pump Recirculation Valve, developing a scenario similar to this event for the simulator and including this event in Operators lessons-learned training.
498 | 4981995001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981995001R00.pdf | 1995-01-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On January 24, 1995, Unit 1 was in Mode 1 at 100% power. At approximately 1528 hours, Unit 1 experienced a reactor trip due to Low-Low Steam Generator Level on 1C Steam Generator after the loss of Main Feedwater Pump 13. The initiating cause of this event was a failed thrust bearing wear probe assembly which caused signal spiking resulting in the generation of a trip signal to the Feedwater Pump Control System. Power reduction could not be accomplished rapidly enough to prevent a reactor scram from low Steam Generator level. Corrective actions include replacing the thrust bearing wear probe assembly, providing lessons learned from this event to Unit 1 and Unit 2 operations personnel, and incorporating empirical data of key primary and secondary system parameters from two Unit 1 loss of Feedwater Pump events into the newly acquired simulator model.
498 | 4981995009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981995009R00.pdf | 1995-08-29 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 1 | P | WE | PO | 100 | On August 29, 1995, Unit 1 was in Mode 1 at 100% power. At approximately 1127 hours, Unit 1 experienced a reactor trip on Loss of Flow due to a loss of power to 1C Reactor Coolant Pump. At the time of this occurrence, preventive maintenance of a ground relay in the 13.8 kV switchgear was being conducted. During the performance of the preventive maintenance activity, a lockout relay was inadvertently actuated causing the feeder breaker to an auxiliary bus to open and loss of power to 1C Reactor Coolant Pump. The principal cause of this event was inadequate supervisory practices, inattention to detail, failure to self check, improper work practices during performance of maintenance activities, and ineffective execution of the Work Risk Assessment process. Corrective actions include providing lessons learned from this event to maintenance personnel and developing and providing expectations and clarifications of the Work Risk Assessment process to first-line supervision.
498 | 4981995013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981995013R01.pdf | 1995-12-18 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On December 18, 1995, Unit 1 was in Mode 1 at 100% power. At approximately 0336 hours, a Backup Pilot Wire Monitoring Relay actuated and resulted in a lockout of the Unit 1 main and auxiliary transformers. This event tripped open the generator output breaker, the main turbine, the breakers for all four 13.8 kV auxiliary abuses and caused loss of offsite power to the A Train Engineered Safeguards Features Bus. the reactor trip, three control rods indicated a rod position of six steps from rod bottom. All other control rods had indication of their rod bottom lights illuminated. Human performance issues identified regarding this event involved compliance with Emergency Operating Procedures, notification timeliness and accuracy, and inappropriate manual starting of Train B and C Standby Diesel Generators. The root cause of the trip was improper maintenance performance that resulted in a pinched wire which grounded the A phase of the backup pilot wire current transformer when the cover was reinstalled during the Unit 1 refueling outage in the Spring of 1995. Root cause determination for the control rod insertion anomaly is subject of an ongoing investigation. Core physics analyses for this condition were performed and determined continued operation of Unit 1 is acceptable until the end of the current operating cycle. Corrective actions include repair of the grounded connection; reinforcement of management's expectations regarding control rod insertion indication, Emergency Operating Procedure usage and accuracy of notifications; training on lessons learned from this event; and procedure enhancements.
498 | 4981997012 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981997012R00.pdf | 1997-11-10 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | South Texas 1 | P | WE | PO | 100 | On November 10, 1997, Unit 1 was in Mode 1 at 100% power. At approximately 1701 hours, an Overspeed Protection Control solenoid for the Unit 1 Main Turbine momentarily energized resulting in the closing and opening of the Main Turbine governor valves. This valve response was followed by a secondary system transient and oscillating Steam Generator levels. The oscillating Steam Generator levels resulted in main feedwater flow oscillation and deviations between steam flow and feedwater flow. The secondary system transient was reflected in the primary system as an increase in average Reactor Coolant System temperature. An automatic Reactor trip occurred on two of four Over Temperature/Delta Temperature signals to the Solid State Protection System. A Main Turbine trip followed the Reactor trip. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. During the response to the Reactor trip, the Engineered Safeguards Features System actuated the Auxiliary Feedwater System during the transition of Main Steam Dump system modes when Steam Generator levels momentarily dropped below the LOW-LOW level setpoint. The cause of the Reactor trip was the momentary energization of the Overspeed Protection Control solenoid due to failure of a solid state relay in the control circuitry. It was determined that the solid state relay was redundant and not required for the Overspeed Protection Control circuit to perform its function. Corrective actions included removal of the redundant solid state relay from both the Unit 1 and 2 Main Turbine Overspeed Protection Control circuits.STI: 30489212
498 | 4981999004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981999004R00.pdf | 1999-05-16 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 1 | P | WE | PO | 100 | On May 16, 1999, Unit 1 was operating in Mode 1 at 100% power. At 0452 hours CDT, Unit 1 experienced an automatic reactor trip due to a low flow condition in Reactor Coolant Loop 3 (C). The low flow condition was caused by the trip of Reactor Coolant Pump 1C due to a low voltage condition in the control circuit on 13.8kv switchgear 1H. The undervoltage condition was caused by the degradation of a fuse in a potential transformer circuit. All control rods fully inserted and all systems functioned as required. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. Computer data shows that the potential transformer fuse began to degrade at 0335 on the same day and that at 0452 the potential transformer secondary side voltage reached the setpoint for undervoltage relay 27/A1HB-C. Actuation of the relay tripped Reactor Coolant Pump 1C. The degrading fuse opened completely at 0740 on May 16, 1999. Troubleshooting under a work document found that a fuse on the primary side of the potential transformer on the "C" phase had failed. Repair activities included checking accessible connections, verifying Potential Transformer insulation resistance, verifying fuses in the secondary circuit for proper size and functionality, and installing four new fuses in the primary side of the Potential Transformer. Reactor coolant pump 1C was successfully restarted at 1411 on May 16, 1999.
498 | 4981999006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981999006R00.pdf | 1999-06-27 | QR3 | Reactivity Control Imbalance | [45 empty] | South Texas 1 | P | WE | PO | 100 | At approximately 1059 hours on June 27, 1999, Unit 1 experienced an automatic reactor trip due to an overtemperature delta-temperature actuation. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All systems functioned as required. The plant was stabilized utilizing the Emergency Operating Procedures as expected. The over-temperature delta-temperature actuation resulted from spurious actuation of the main turbine overspeed protection control circuit momentarily causing the main turbine governor and intercept valves to shut. The closing of the main turbine valves removed the primary heat sink from the reactor coolant system and resulted in a rapid increase in average reactor coolant temperature. The root cause of the spurious actuation was a degraded flag-lug connection for the -15 VDC power supply to the printed circuit card racks. Corrective action included re-crimping the failed flag-lug connection.
498 | 4981999008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4981999008R00.pdf | 1999-09-12 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On September 12, 1999, Unit 1 was operating in Mode 1 at 100% power. At approximately 0344 the unit tripped during the performance of the Main Turbine Emergency Trip Test procedure. Operators had successfully performed Channel One Low Bearing Oil Pressure, Low Vacuum, and Electrical Overspeed tests. Subsequently, during the Low Stator Cooling Water Differential Pressure test, the operator depressed the "Test Trips" pushbutton, at which time an electrical overspeed trip signal was generated resulting in a turbine trip/reactor trip. The shift crew entered the emergency operating procedures and stabilized the plant. The cause of this event was a failure in the turbine trip test circuitry causing an inadvertent actuation of the electrical overspeed trip. This failure may be attributed to dust and lint contamination of the turbine trip test selector switch. Corrective actions include cleaning the Main Control Board switches in both units, inspecting other panels to ensure any dust and lint was removed, and evaluating the preventive maintenance frequencies of existing main control board cleaning. In addition, STP currently has a task force that is addressing balance of plant equipment reliability and material condition.
498 | 4982000007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982000007R00.pdf | 2000-12-16 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On December 16, 2001 at 2300, a manual reactor trip was initiated when all main turbine governor valves closed during preparations to perform the monthly main turbine valve testing surveillance. During the ensuing transient an automatic safety injection occurred due to lowering reactor coolant system pressure resulting from a pressurizer spray valve control anomaly. Plant pressure decrease was terminated when partially open pressurizer spray valves shut and auxiliary feedwater flow was throttled. The highest reactor coolant pressure achieved during this transient was 2310 psig which is 75 psig above the normal operating value. Adequate subcooling was maintained and the reactor head area remained full during the transient. Maximum pressurizer level during the transient was approximately 63.8% which is below the high level alarm setpoint. Reactor coolant system pressure reached a minimum of 1480 psig during the transient due to partially open pressurizer spray valves. The cause of the main turbine governor valves shutting was a failure a logic card in the analog electro-hydraulic controller. The cause of the pressurizer spray valves anomaly was a calibration shift of the spray valve UP converters. Corrective actions included replacement of the gate logic card, calibration of spray valve I/P converters, and planned replacement of the pressurizer spray valve I/P converters with an improved model.
498 | 4982002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982002003R00.pdf | 2002-11-16 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | South Texas 1 | P | WE | PO | 100 | On November 16, 2002 Unit 1 was operating at 100% power, at approximately 2036 the Unit 1 control room personnel received unexpected electrical system trouble alarms in the control room. Within several minutes Open Loop Cooling Water pump 12 tripped. The control room staff attempted to start Open Loop pump 13. Open Loop pump 13 did not start. The Reactor Operator (RO) noted that the Open Loop header pressure was approximately 30 to 40 psig and relatively stable. The yard watch operator that had been dispatched to the Circulating Water Intake Structure (CWIS) reported to the control room that the pump bay was filling with water and that it was believed to be coming from the Open Loop system header. While the off-normal procedure actions were being implemented for loss of Open Loop auxiliary cooling water, Open Loop header pressure indication in the control room dropped to zero psig. The Unit Supervisor directed the Unit 1 reactor be tripped manually and that Open Loop pump 11 be secured. Water level in the CWIS was observed to still be rising even after the last Open Loop pump was secured. Investigation revealed that the water was issuing from a large hole in the side of Circulating Water (CW) pump 11 casing. Circulating Water pump 11 was then secured.An Auxiliary Feedwater (AFW) actuation occurred approximately 25 seconds following the manual reactor trip due to Lo-Lo water level in the 2C Steam Generator. The AFW system operated and maintained water level in all four Steam Generators.All actuated safety related equipment operated as required.
498 | 4982003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982003002R01.pdf | 2003-03-01 | QP3 | Loss of Condensate Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | At 0149 on March 1, 2003, a 24-volt DC (VDC) power supply in the Unit 1 Condensate Polishing System failed. This failure caused the Condensate Polishing service vessel outlet valves to close, as well as failure of the system bypass valve to open on high Condensate System differential pressure. The pressure transmitter signal that is required for opening the bypass valve was also not available due to the failed power supply. With all Condensate Polishing service vessel outlet valves closed and the system bypass valve closed, condensate flow to the deaerator was isolated. The Unit 1 reactor was manually tripped because of the ensuing decrease in deaerator level.The cause was a design characteristic in which loss of one power supply disabled the differential pressure signal required to open the system bypass valve and the signal required to maintain the output valves open for the normal system flow path. The power supply was determined to have failed due to age-related degradation.The affected power supply units have been replaced. A lock-up feature has been incorporated to ensure the Condensate Polishing Service Vessel outlet valves are locked in place in the event of a power supply failure. A fault tolerant power circuit will be developed and installed to prevent recurrence. This event resulted in no personnel injuries, offsite radiological releases, or damage to safety-related equipment. There were no challenges to plant safety.
498 | 4982004001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982004001R00.pdf | 2004-01-23 | QP5 | Excessive Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On 01/23/04 with Unit 1 at 100% power, the Class 1E 7.5 KV Inverter 1201 failed, resulting in a reactor trip when steam generator level could not be controlled. The plant was stabilized, and after troubleshooting and repair, the reactor was restarted at approximately 2237 hours on 01/25/04.The cause of the inverter failure was a Ferro-Resonant transformer short due to heat-related degradation of the transformer insulation. The technical root cause of the event is that the design of the Class 1E Vital Instrument Power Supply (VA) System is not single train fault-tolerant and failure of the inverter causes significant operational challenges. Additionally, the organizational root cause is that the station did not aggressively pursue effective failure prevention strategies even though previous events have shown that the inverters are susceptible to failure and the Instrument Power Supply (VA) System is not single train fault-tolerant.Corrective actions include the replacement/repair of all Class 1E 7.5 KV Inverter Ferro-Resonant Transformers and design enhancements that will minimize inverter failures and the effects of initiating transients requiring significant operator rapid response.This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
498 | 4982010003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982010003R00.pdf | 2010-02-03 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On August 20, 2010 at 1525 hours, the Unit 1 Reactor automatically tripped during the performance of a scheduled surveillance test of the Solid State Protection System (SSPS). The reactor trip was caused by a human performance error that occurred when the procedure performer and verifier missed a procedure step. The Root Cause for the reactor trip was determined to be:1. Procedure place keeping standards for the site were less than adequate and2. Supervisory Oversight of surveillance test procedure 0PSP03-SP-0006R became ineffective when the Senior Reactor Operator (SRO) stepped outside of his oversight role and became involved in the process.There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment.
498 | 4982015001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982015001R00.pdf | 2015-12-21 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | South Texas 1 | P | WE | PO | 48 | On December 21, 2015, at 1519 hours, Operators manually tripped the Unit 1 Main Turbine due to excessive load swings caused by Main Turbine Governor Valve 2 (GV2) oscillations. Prior to and following the trip of the Main Turbine, the Steam Dumps did not respond as expected, resulting in a Main Feedwater Isolation at 1524 hours due to rising Steam Generator (SG) level. Operators initiated a manual reactor trip at 1533 hours due to lowering SG levels. Approximately six seconds after the reactor trip, the Auxiliary Feedwater (AFW) system automatically actuated on a SG low level signal. <br /><br /> The cause of the GV2 oscillations was an intermittent ground on the signal wire to the Linear Variable Differential Transmitter (LVDT) for GV2. The fluctuations in steam flow due to the GV2 oscillations caused the spring clips in the valve positioners that modulate the Group 1 Steam Dumps to become dislodged, causing the Group 1 Steam Dumps to be unresponsive. As corrective actions, the LVDT and associated cabling for GV2 was replaced and the Group 1 Steam Dump valve positioners were repaired. The manual actuation of the Reactor Protection System and subsequent automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
498 | 4982016001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982016001R00.pdf | 2016-01-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 1 | P | WE | PO | 100 | On January 26, 2016, at 2324 hours, the Control Room received a Steam Generator Steam Flow/Feed Flow mismatch alarm. Operators found Steam Generator (SG) Train C Feedwater Regulating Valve closed and in manual. SG C Feedwater Regulating Valve could not be manually reopened. At 2325 hours, Operators manually tripped the Unit 1 reactor due to lowering level on SG C. The Auxiliary Feedwater (AFW) system automatically actuated on a SG low level signal and operators took manual control of AFW at 2327 hours.<br /><br /> The cause of loss of Main Feedwater to SG C was a failure of the Manual 7300 Series Tracking Driver (NTD) circuit card which forced SG C Feedwater Regulating Valve closed and prevented the operators from taking manual control or switching back to automatic valve control. As a corrective action, the Manual NTD circuit card was replaced. The manual actuation of the Reactor Protection System and subsequent automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
498 | 4982016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4982016002R00.pdf | 2016-05-01 | QR5 | Turbine Trip | [45 empty] | South Texas 1 | P | WE | PO | 100 | On May 1, 2016 at 2020 hours, STP Unit 1 experienced a Main Generator lockout due to a ground relay actuation resulting in an automatic turbine trip that lead to an automatic reactor trip. Visual inspections revealed that a rubber boot located where Main Generator phase B enters the isolated phase bus duct was degraded. A piece of the boot was hanging down and intermittently contacting the generator bushing causing a resistance path to ground, resulting in a Main Generator lockout and turbine trip signal. With the reactor at greater than fifty percent power, the automatic reactor trip was initiated in response to the turbine trip. The Auxiliary Feedwater (AFW) system actuated in response to low Steam Generator level. All safety systems operated as expected.<br /><br /> As immediate corrective actions, the A, B and C phase rubber boots were replaced in Unit 1. The cause evaluation determined that the design of the rubber boot and its retaining ring is inadequate. Design change packages are being developed to permanently remove the rubber boots and retaining rings for both Unit 1 and Unit 2. <br /><br /> The automatic actuation of the Reactor Protection System and automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
499 | 4991989009 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989009R00.pdf | 1989-04-05 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 2 | P | WE | SU | 11 | POWER LEVEL - 011%. ON 4/05/89, UNIT 2 WAS IN MODE 1 AT 11% POWER PERFORMING INITIAL SYNCHRONIZATION TO THE GRID. AT 0729 HOURS, APPROXIMATELY FOUR SECONDS AFTER CLOSURE OF THE GENERATOR BREAKER, A REACTOR TRIP AND LOSS OF OFFSITE POWER ON THE AUX. BUSSES AND THE 4.16KV TRAIN A ENGINEERED SAFETY FEATURES BUS OCCURRED. ONCE THE PLANT STABILIZED, OFFSITE POWER WAS RESTORED. REACTOR COOLANT PUMP 2D RESTARTED IMMEDIATELY BECAUSE ITS BREAKER FAILED TO TRIP WHEN POWER WAS LOST. THIS RESULTED IN ACTUATION OF AUX. FEEDWATER. THE CAUSE OF THIS EVENT WAS IMPROPER INSTALLATION OF A WIRING CHANGE TO THE GENERATOR PROTECTIVE RELAYING BY STARTUP TECHNICIANS PRIOR TO SYSTEM TURNOVER TO PLANT OPERATIONS. THE CAUSE OF THE INADVERTENT RCP 2D RESTART WAS A BROKEN LUG IN THE TRIP CIRCUIT DUE TO ITS ASSOCIATED WIRE CATCHING ON THE BREAKER ENCLOSURE WHEN THE BREAKER WAS RACKED IN LAST. CORRECTIVE ACTIONS INCLUDE CORRECTION OF THE GENERATOR PROTECTIVE RELAY WIRING, TESTING OF OTHER PROTECTIVE CIRCUITRY, REPLACEMENT OF THE RCP 2D BREAKER LUG AND CHECKING THE OTHER UNIT 2 RCP BREAKERS.
499 | 4991989013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989013R00.pdf | 1989-04-15 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 24 | POWER LEVEL - 024%. ON APRIL 15, 1989, UNIT 2 WAS IN MODE 1 AT 24 PERCENT POWER. AT 0517 HOURS A REACTOR TRIP OCCURRED WHEN THE TRAIN S REACTOR TRIP BREAKER OPENED UNEXPECTEDLY. A REACTOR TRIP SYSTEM ACTUATION SUBSEQUENTLY OCCURRED ON 'POWER RANGE NEGATIVE RATE'. THE REACTOR WAS BROUGHT TO AN ORDERLY SHUTDOWN AND NO UNEXPECTED POST-TRIP TRANSIENTS OCCURRED. THE CAUSE OF THIS EVENT IS UNKNOWN. THE REACTOR TRIP BREAKERS AND ASSOCIATED CIRCUITRY WERE TESTED. ADDITIONAL DIAGNOSTIC ACTIVITIES WERE ATTEMPTED, HOWEVER NO PROBLEMS WERE FOUND.
499 | 4991989016 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989016R00.pdf | 1989-06-02 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 76 | POWER LEVEL - 076%. ON JUNE 2, 1989, UNIT 2 WAS IN MODE 1 AT 76 PERCENT POWER. AT 0354 HOURS, DURING THE PERFORMANCE OF THE MAIN TURBINE STEAM INLET VALVE OPERABILITY TEST, A REACTOR TRIP AND TURBINE TRIP OCCURRED ON COMPLETION OF TWO OUT OF FOUR LOGIC FOR CLOSED TURBINE INLET THROTTLE VALVES. THE PLANT WAS BROUGHT TO AN ORDERLY SHUTDOWN WITH NO UNEXPECTED TRANSIENTS. THE EVENT OCCURRED AFTER A LIMIT SWITCH ON TURBINE INLET VALVE TV-1 STUCK. WHEN THE VALVE WAS CLOSED AND REOPENED DURING THE PERFORMANCE OF THE TEST, THE LIMIT SWITCH STUCK IN THE VALVE-CLOSED POSITION WHICH PREVENTED CLEARING OF THE TRIP BISTABLE. THIS CONDITION WAS NOT RECOGNIZED AS A RESULT OF A DEFICIENT TEST PROCEDURE. WHEN A SECOND VALVE WAS TESTED AND STROKED CLOSED, THE MINIMUM TRIP LOGIC WAS SATISFIED AND THE REACTOR TRIP OCCURRED. THE DEFECTIVE LIMIT SWITCH HAS BEEN REPLACED. CORRECTIVE ACTIONS INCLUDE A REVISION TO THE TURBINE INLET VALVE TEST PROCEDURES AND REVIEW OF OTHER SURVEILLANCE PROCEDURES FOR SIMILAR WEAKNESSES. ADDITIONALLY, THE TURBINE INLET THROTTLE VALVE LIMIT SWITCHES, THE ONLY SIMILAR SWITCHES FROM THIS MANUFACTURER WHICH PERFORM A SAFETY-RELATED ACTUATION, WILL BE REPLACED.
499 | 4991989017 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989017R00.pdf | 1989-07-13 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 99 | POWER LEVEL - 099%. ON JULY 13, 1989, UNIT 2 WAS IN MODE 1 AT 99 PERCENT POWER. AT 2002 HOURS, AN INTERNAL FAULT OCCURRED IN THE UNIT 2 MAIN STEP-UP TRANSFORMER 2A. THE PROTECTIVE RELAYS TRIPPED THE TURBINE AND ACTUATED THE SWITCHYARD AND GENERATOR BREAKERS TO CLEAR THE FAULT. THE REACTOR TRIPPED ON THE TURBINE TRIP. THE PLANT WAS BROUGHT TO AN ORDERLY COOLDOWN WITH NO UNEXPECTED PRIMARY SYSTEM POST TRIP TRANSIENTS. THE INVESTIGATION OF THE TRANSFORMER FAILURE IS ONGOING. THE MOST PROBABLE CAUSE WAS FAILURE OF THE HIGH SIDE, PHASE A BUSHING. THE TRANSFORMER WILL BE RETURNED TO THE MANUFACTURER FOR REPAIR AND THE BUSHING AND TRANSFORMER WILL BE ANALYZED FURTHER TO DETERMINE THE CAUSE OF THIS EVENT.
499 | 4991989019 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989019R00.pdf | 1989-08-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 8/23/89, UNIT 2 WAS IN MODE 1 AT 100% POWER. AT 0119 HOURS, FEEDWATER ISOLATION VALVE C CLOSED FULLY DURING A PARTIAL STROKE SURVEILLANCE TEST. THE RESULTANT LOSS OF FEEDWATER FLOW AND DECREASE IN STEAM GENERATOR LEVEL CAUSED A REACTOR TRIP. THE UNIT WAS STABILIZED IN MODE 3 WITH NO UNEXPECTED POST TRIP TRANSIENTS. THE CAUSE OF THIS EVENT WAS A FAILURE IN THE FEEDWATER ISOLATION VALVE CONTROL CIRCUIT WHICH ALLOWED IT TO STROKE FULLY CLOSED. THE SPECIFIC COMPONENT WHICH FAILED IS UNKNOWN AT THIS TIME. THE FAILURE DID NOT AFFECT THE ABILITY OF THE VALVE TO PERFORM ITS SAFETY FUNCTION. FURTHER TROUBLESHOOTING OF THE VALVE CONTROL CIRCUITS WILL BE PERFORMED DURING THE NEXT SCHEDULED MAINTENANCE OUTAGE. THE FEEDWATER VALVE CONTROL CIRCUITS ARE BEING REVIEWED TO DETERMINE IF MODIFICATIONS CAN BE PERFORMED TO REDUCE THE POTENTIAL FOR FULL CLOSURE OF THE VALVES DURING TESTING.
499 | 4991989020 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989020R00.pdf | 1989-08-29 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 8/29/89, UNIT 2 WAS IN MODE 1 AT 100% POWER. AT 1400 HOURS ALL THREE OPERATING TURBINE DRIVEN FEEDWATER PUMPS TRIPPED. THE LICENSED CONTROL ROOM OPERATOR IMMEDIATELY TRIPPED THE REACTOR IN ANTICIPATION OF LOW STEAM GENERATOR LEVEL. AN AUXILIARY FEEDWATER ACTUATION SUBSEQUENTLY OCCURRED ON LOW STEAM GENERATOR LEVEL. THE UNIT WAS STABILIZED IN MODE 3 WITH NO UNEXPECTED POST-TRIP TRANSIENTS. THE CAUSE OF THIS EVENT WAS A MOMENTARY INTERRUPTION OF CONTROL POWER TO THE FEEDWATER PUMP OVERSPEED PROTECTION CIRCUITS DUE TO THE FAILURE OF AN INVERTER. A CONTRIBUTING CAUSE WAS THE DESIGN OF THE FEEDWATER PUMP OVERSPEED PROTECTION CIRCUITS WHICH COULD NOT TOLERATE THE MOMENTARY LOSS OF CONTROL POWER WITHOUT TRIPPING THE PUMPS. THE INVERTER HAS BEEN REPAIRED AND RETURNED TO SERVICE. THE DESIGN OF THE FEEDWATER PUMP OVERSPEED PROTECTION HAS BEEN MODIFIED TO AN 'ENERGIZE TO TRIP' SCHEME ON UNIT 2 AND WILL BE MODIFIED ON UNIT 1 PRIOR TO STARTUP FROM THE FIRST REFUELING OUTAGE.
499 | 4991989021 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989021R00.pdf | 1989-09-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 5, 1989, UNIT 2 WAS IN MODE 1 AT 100 PERCENT POWER. AT APPROXIMATELY 1607 HOURS, CONTROL ROOM OPERATORS OBSERVED SPEED OSCILLATIONS ON THE TURBINE DRIVEN STEAM GENERATOR FEEDWATER PUMP (SGFP) 21. THE OPERATORS ATTEMPTED TO REGAIN SPEED CONTROL; HOWEVER, THE PUMP DID NOT RESPOND AND SUBSEQUENTLY TRIPPED ON OVERSPEED. THE RESULTANT LOSS OF STEAM GENERATOR LEVEL CAUSED A REACTOR TRIP AND AUXILIARY FEEDWATER SYSTEM ACTUATION. NO SAFETY INJECTION ACTUATION OCCURRED. THE PLANT WAS STABILIZED IN MODE 3. THE CAUSE OF THIS EVENT WAS A DEFECTIVE SGFP 21 SPEED CONTROLLER CARD EDGE CONNECTOR WHICH WAS DISTURBED BY A MAINTENANCE TECHNICIAN DURING TROUBLESHOOTING OF A CARD ASSOCIATED WITH SGFP 22 IN THE SAME CARD FRAME. THE DEFECTIVE CONNECTOR WAS REPAIRED, THE CARD FRAME ALIGNMENT CHECKED, THE REMAINING PRINTED CIRCUIT CARDS AND EDGE CONNECTORS WERE INSPECTED AND THE CONTACT SURFACES WERE CLEANED. THE PRINTED CIRCUIT CARDS IN THE SPEED CONTROLLER CIRCUITS ON UNIT 1 WERE ALSO INSPECTED AND CLEANED.
499 | 4991989022 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989022R00.pdf | 1989-09-19 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 19, 1989, UNIT 2 WAS IN MODE 1 AT 100 PERCENT POWER. AT 1237 HOURS DURING THE CROSS CALIBRATION OF THE INCORE AND EXCORE NUCLEAR INSTRUMENTATION, AN OVERTEMPERATURE DELTA TEMPERATURE (OTDT) TURBINE RUNBACK OCCURRED RESULTING IN AN OTDT REACTOR TRIP. THE TURBINE TRIPPED ON THE REACTOR TRIP AND AN AUXILIARY FEEDWATER ACTUATION OCCURRED ON LOW STEAM GENERATOR LEVEL. THE MAIN STEAM ISOLATION VALVES WERE CLOSED TO PREVENT EXCESSIVE REACTOR COOLANT SYSTEM COOLDOWN. THE ENGINEERED SAFETY FEATURES FUNCTIONED AS DESIGNED. THE CAUSE OF THIS EVENT WAS THAT THE TURBINE RUNBACK SETPOINT DESIGN DID NOT PROVIDE SUFFICIENT OPERATING MARGIN TO ALLOW FOR SMALL DEVIATIONS IN RCS AVERAGE TEMPERATURE. THE OTDT RUNBACK FEATURE HAS BEEN DISABLED AND ANALYSIS IS BEING PERFORMED TO DETERMINE IF IT CAN BE RESTORED WITHOUT CAUSING UNWANTED PLANT TRANSIENTS.
499 | 4991989023 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989023R00.pdf | 1989-09-22 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 94 | POWER LEVEL - 094%. ON 9/22/89, UNIT 2 WAS IN MODE 1 AT 94% POWER. AT 0201 HOURS A TURBINE TRIP OCCURRED ON LOSS OF POWER TO THE FOUR MAIN TURBINE AUTO STOP SOLENOIDS. THE REACTOR TRIPPED ON THE TURBINE TRIP. A MAIN FEEDWATER ISOLATION AND AUXILIARY FEEDWATER ACTUATION OCCURRED ON LOW AVERAGE REACTOR COOLANT SYSTEM TEMPERATURE AS EXPECTED. THE UNIT WAS STABILIZED IN MODE 3 WITH NO UNEXPECTED POST-TRIP TRANSIENTS. THE CAUSE OF THIS EVENT WAS FAILURE OF A NON-SAFETY-RELATED INVERTER WHICH INTERRUPTED POWER TO THE MAIN TURBINE AUTO STOP SOLENOIDS. A CONTRIBUTING CAUSE WAS THAT THE DESIGN DID NOT PROVIDE FOR THE SINGLE FAILURE OF A POWER FEED. THE INVERTER HAS BEEN REPAIRED AND RETURNED TO SERVICE. THE POWER FEED DESIGN HAS BEEN CHANGED TO ADD AN ADDITIONAL POWER SOURCE.
499 | 4991989026 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991989026R00.pdf | 1989-10-13 | QR3 | Reactivity Control Imbalance | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON OCTOBER 13, 1989, UNIT 2 WAS IN MODE 1 AT 100% POWER. AT 1745 HOURS, A REACTOR TRIP OCCURRED DUE TO THE DETECTION OF HIGH NEUTRON FLUX NEGATIVE RATE ON 2 OF 4 POWER RANGE NEUTRON MONITORING CHANNELS. THE PLANT WAS BROUGHT TO A STABLE CONDITION IN MODE 3 WITH NO UNEXPECTED POST-TRIP TRANSIENTS. THE CAUSE OF THE EVENT IS BELIEVED TO BE AN INTERMITTENT HIGH RESISTANCE CONNECTION ON A STATIONARY GRIPPER DIODE IN THE ROD CONTROL SYSTEM WHICH CAUSED ROD F-8 IN CONTROL BANK A TO DROP. THE DIODE HAS BEEN REPLACED. THE REMAINING STATIONARY GRIPPER DIODES ON BOTH UNITS WILL BE INSPECTED DURING THE NEXT SCHEDULED MAINTENANCE OUTAGE ON EACH UNIT.
499 | 4991990002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991990002R00.pdf | 1990-02-02 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On February 2, 1990, Unit 2 was in Mode 1 at 100 percent power. At 0259 hours the Train S Reactor Trip Breaker spuriously opened. This initiated a turbine trip and subsequent reactor trip. Feedwater isolation occurred on low average Reactor Coolant System Temperature and an Auxiliary Feedwater System actuation occurred on low steam generator level as expected. The plant was stabilized in Mode 3. No unexpected post trip transients occurred. Extensive troubleshooting of the Solid State Protection System and the Reactor Trip Breaker was performed; however, the cause of the spurious breaker opening is unknown. As a conservative measure, the fifteen Universal Logic Cards associated with the reactor trip function in Train S of the Solid State Protection System have been replaced. Instrumentation has been installed on the reactor trip breaker in an attempt to isolate the source of the spurious trip signal should it recur.
499 | 4991990004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991990004R00.pdf | 1990-03-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On March 26, 1990, Unit 2 was in Mode 1 at 100 percent power. At 0721 hours, a steam flow/feed flow mismatch alarm was received on Steam Generator 2 C. Feedwater flow to Steam Generator 2 C had decreased to 50 percent of full power flow. Attempts to manually control the Steam Generator 2 C feedwater regulating valve to restore feedwater flow were unsuccessful. The reactor subsequently tripped on low steam generator level. The plant was brought to a stable condition in Mode 3 with no unexpected post trip transients. The cause of this event was separation of the feedwater regulating valve stem from the plug which allowed the plug to lodge in the feedwater flow stream restricting flow to approximately 50 percent. The Unit 2 feedwater regulating valve stems have been welded to the plugs to prevent separation. The Unit 1 feedwater regulating valve stems will be welded during the current refueling outage.
499 | 4991990005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991990005R00.pdf | 1990-04-14 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On April 14, 1990, Unit 2 was in Mode 1 at 100 percent power. At 1704 hours, a simultaneous reactor and turbine trip occurred on low turbine electrohydraulic control (EHC) fluid pressure. The plant was brought to a stable shutdown in Mode 3 with no unexpected post-trip transients. The cause of this event was failure of the EHC supply line to a main turbine governor valve. The line failed due to fatigue stress of a weld caused by governor valve-induced vibration. The valve vibration was caused by valve plug rotation. Interim corrective action has been taken to repair the EHC supply piping and add additional supports. The valve used to throttle flow during full power operation will be modified to add anti swirl baffles and anti rotation pins on the plug to stem connection during the first refueling outage.
499 | 4991990013 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991990013R00.pdf | 1990-09-17 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On September 17, 1990, Unit 2 was at 100% power. At 0330 hours, a reactor trip occurred during performance of the Train S Reactor Trip Breaker Trip Actuating Device Operational Test. A main feedwater isolation occurred on low Reactor Coolant System average temperature and the Auxiliary Feedwater System actuated on low steam generator level. Control room personnel responded in accordance with procedures and stabilized the plant. All systems responded as expected. The cause of the event was failure of a non-licensed operator to self verify that he was in position to open the correct reactor trip breaker panel prior to manipulation of the auto shunt trip test pushbutton. The non-licensed operator was counseled and received disciplinary action, in addition a training module emphasizing the importance of attention to detail and self-verification was developed and presented to employees engaged in operations and maintenance of the plant.
499 | 4991991001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991991001R00.pdf | 1991-01-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On January 9, 1991, Unit 2 was in Mode 1 at 100% power. At 2207 hours, Feedwater Isolation Valve (FWIV) 2C closed during the investigation of low nitrogen and low hydraulic pressure alarms for FWIV 2C. The resultant loss of feedwater flow caused a decrease in Steam Generator (SG) level and the reactor was manually tripped. The cause of the manual reactor trip was a failed-closed feedwater isolation valve. The feedwater isolation valve closed when an operator incorrectly removed a power supply fuse to the trip solenoid. The fuse was removed when trying to determine the source of power loss to the FWIV hydraulic skid. This was caused by failure to coordinate operational problem investigation and the use of information without providing necessary verification; annunciator response procedures did not provide direction pertaining to a loss of power; and lack of formal training on the investigation of power supplies. Corrective actions include: training of licensed and non-licensed operators; revision of annunciator response procedures; as well as other recurrence measures.
499 | 4991991003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991991003R00.pdf | 1991-03-14 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On March 14, 1991, Unit 2 was operating at 100% while Unit 1 was in Mode 5. At 1810 hours, Unit 1 Control Room personnel closed the switchyard breaker to energize the Unit 1 Main and Auxiliary Transformers. Immediately following this breaker closure, the Unit 2 B Phase Generator Isophase Bus differential relay actuated. This caused the generator lockout relay to actuate which resulted in a turbine trip and reactor trip. During the recovery process the Main Steam Isolation Valves (MSIV) were closed. A Steam Generator (SG) MSIV was subsequently reopened while a SG level was near the low-low setpoint and caused an Auxiliary Feedwater actuation. The protective relay actuation was caused by differences in the saturation rates of the two current transformers that supply the differential relay. The AFW actuation was caused by operating procedures that failed to provide guidance regarding minimum SG levels during MSIV manipulations. The corrective actions relative to the current transformers will be reported in LER 91-004, which describes a similar subsequent reactor trip event. Procedures will be revised and this event will be included in requalification training to minimize the potential for unnecessary AFW actuations.
499 | 4991991004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991991004R00.pdf | 1991-03-30 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On March 30, 1991, Unit 2 was operating at 100% while Unit 1 was in Mode 3. Unit 1 Control Room personnel closed the switchyard breaker to energize the Unit 1 Main and Auxiliary Transformers. Immediately following this breaker closure, the Unit 2 B Phase Generator Isophase Bus differential relay actuated. This caused the generator lockout relay to actuate which resulted in a turbine trip and reactor trip. The protective relay actuation was caused by differences in the saturation rates of the two current transformers that supply the differential relay. An evaluation is underway to establish the feasibility of hardware changes to address this problem. As an interim measure, a temporary modification has been installed that removes the protective function from the affected differential relay. Redundant protection is provided by other protective relays.
499 | 4991991007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991991007R01.pdf | 1991-05-22 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On May 22, 1991, Unit 2 was in mode 1 at 100% power. At approximately 2220 hrs, while waiting in the area of the main generator breaker to unlock a local cabinet for an Electrical Maintenance individual, a non-licensed operator inadvertently actuated the local generator breaker emergency trip pushbutton. The sudden loss of secondary load caused an automatic over temperature delta temperature (OTDeltaT) reactor trip. Pressurizer spray was unable to reduce the pressure before the pressurizer PORVs opened at approximately 2335 psig. Steam generator 2C power-operated relief valve (PORV) failed to open even though the pressure exceeded the lift setpoint. The non-licensed operator responsible for the trip was counselled with regards to paying strict attention to performance of operations activities. The Steam Generator 2C PORV has been repaired. Other switch designs have been reviewed to identify changes that can prevent similar inadvertent actuations.
499 | 4991991010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991991010R01.pdf | 1991-12-24 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | South Texas 2 | P | WE | PO | 16 | On December 24, 1991, at 1644 hours, Unit 2 was operating at 30% Rated Thermal Power (RTP) when pressurizer spray valve PCV-655C failed open. This ultimately caused an automatic reactor trip and Safety Injection (SI) actuation on low pressure at 1648 hours from 16% RTP. Three Reactor Coolant Pumps (RCPs) were secured to terminate the transient. All available safety equipment performed as designed and no actual injection to the reactor occurred. The cause was disengagement of the feedback arm linkage to the valve stem connecting plate on the pressurizer spray valve controller. Locking nuts were added to the spray valve feedback arm linkage connecting screws. Corrective actions included improving maintenance work instructions, conducting plant management reviews with personnel to discuss the event, and providing training on lessons learned from the event. LER\92227001.U2
499 | 4991992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991992001R00.pdf | 1992-01-22 | QR3 | Reactivity Control Imbalance | [45 empty] | South Texas 2 | P | WE | PO | 100 | On January 22, 1992, Unit 2 was in Mode 1 at 100% power. At 0909 hours, Unit 2 experienced a reactor trip due to power range high neutron flux negative rate. The plant was brought to a stable condition in Mode 3 with no unexpected post-trip transients. The cause of the power range high neutron flux negative rate trip was dropping of control rod H-6 into the reactor core. The control rod dropped when the blocking diode and its associated stationary gripper coil's power circuit failed open, resulting in an interruption of current to the stationary gripper coil. The cause of the diode failure remains unknown. The faulty diode was replaced, along with all other blocking diodes sharing the faulty diode's manufacturer's date code. HL&P has sent the faulty diode and the other selected diodes to an independent laboratory for analysis. HL&P will evaluate the results of the analysis and initiate further corrective actions as needed. Additionally HL&P, in cooperation with Westinghouse, will perform testing to determine if the blocking diodes can be eliminated from the present rod control system design.
499 | 4991992003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991992003R00.pdf | 1992-02-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On February 24, 1992 at 1515 hours, Unit 2 was in Mode 1 at 1004 power. Feedwater flow oscillations were observed on the Steam Generator Feedwater Pump - Turbine Driven (SGFPT) #23. At 1703 hours, the linear variable differential transformer for the high pressure governor valve for SGFPT #22 failed low and the turbine subsequently tripped on overspeed. At 1810 hours, SGFPT #21 was observed to have decreasing speed. The SGFPT #21 was placed in manual and given a 100% demand signal but the speed continued to decrease. Subsequently, manual turbine load reduction began and control rods were placed in automatic. At 1811 hours, the reactor was manually tripped with steam generator water levels at 47% (narrow range) and decreasing. The cause of this event was rain water leaking through expansion joints in the Turbine Generator Building (TGB) roof and into the Electrohydraulic Control (EHC) cabinet, which is the common control for all three SGFP's. The EH electronic control system was dried out and SGFPT #21 and #22 controls were recalibrated.<br /><br /> Belzona Flexible Membrane was applied to the leaking expansion joints on the roof of the TGB. Modifications will be implemented to seal the TGB roofs of both units.
499 | 4991992010 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991992010R00.pdf | 1992-12-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On December 27, 1992, Unit 2 was in Mode 1 at 100% power. A manual reactor trip was initiated at 0850 hours, due to the closure of the 'D' Steam Generator feedwater regulating valve which resulted in an uncontrollable reduction in 'D' Steam Generator level. The cause of the reactor trip was the failure of a driver card (NCD) in the Westinghouse 7300 process control system for the affected feedwater regulating valve. This card failure resulted in a loss of signal to the 'D' feedwater regulating valve causing the valve to move to its default (closed) position. Analysis of the specific component failure within the circuit card indicates that the power supply for the board coupled with the clock counter failed resulting in the loss of card output. Corrective actions include performing an evaluation of the power supply failure mode and reliability using industry data, Westinghouse data and the as found failure mode. Based on the evaluation additional corrective actions will be developed as necessary.
499 | 4991993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991993001R01.pdf | 1993-01-23 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On January 23, 1993, Unit 2 was in Mode 1 at 100% power. At 2324 hours, Unit 2 automatically tripped from full power due to a turbine trip above the P-9 (50% power) setpoint as the result of a depressurization of the Electro-Hydraulic Control (EHC) supply header. The low EHC System pressure was due to a leak on the low pressure governor valve line of the Steam Generator Feedwater Pump (SGFP) #22. The failure initiated on the outside surface with no defect present. Towards the latter part of the failure, secondary fatigue initiated from the inside as well. Rapid changes in the valve position created excessive movement within the valve and low pressure line. The excessive movement was apparently the result of an exposed wire on the Linear Variable Differential Transformer (LVDT). Corrective actions include replacing the failed EHC line and the LVDT.
499 | 4991993004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991993004R00.pdf | 1993-02-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On February 3, 1993, Unit 2 was in Mode 1 at 100% power. At 1448 hours, Unit 2 experienced an automatic reactor trip due to low Steam Generator water level. The low Steam Generator water level was caused by a loss of Steam-driven Feedwater pump #21 in conjunction with a failure of the Startup Feedwater Pump due to low oil pressure. The cause of this event was ineffective action to correct previous failures of the Startup Feedwater pumps and Steam Driven Feedwater pumps. Corrective actions include troubleshooting and repairing the Startup Feedwater pump and Steam Driven Feedwater pump. A walkdown of both units' Feedwater Isolation Bypass Valves was conducted to identify similar problems with valve positioners. Modifications to improve the reliability of the Steam Driven Feedwater pumps and Startup Feedwater pumps will be implemented. \
499 | 4991994007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991994007R00.pdf | 1994-06-25 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 47 | On June 25, 1994, Unit 2 was in Mode 1 at 47% power. At 1715 hours, a Main Transformer Lockout Relay actuated. This tripped the Main Turbine, the Generator output breaker, the breakers for all four 13.8 kV auxiliary buses and two switchyard breakers. This caused a loss of power to all Unit 2 auxiliary power busses which resulted in a loss of all Reactor Coolant Pumps and a reactor trip on Reactor Coolant Pump undervoltage at 1715 hours. The plant was stabilized in Mode 3. The cause of the trip was the failure of a capacitor within the pilot wire relay. Corrective actions are described within the Licensee Event Report.
499 | 4991995003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991995003R00.pdf | 1995-03-28 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On March 28, 1995, Unit 2 was in Mode 1 at 100% power. At approximately 0832 hours, Unit 2 experienced a reactor trip on Over Temperature/Delta Temperature due to a failed fuse holder. At the time of this event, Instrument and Control Technicians were performing setpoint changes in the Protection System Loop 1, Channel 1 (loop 410) Over Temperature/Delta Temperature instrumentation with the channel in trip. During the performance of this setpoint change, Loop 4, Channel 4 (loop 440) generated a spurious trip signal which actuated the second logic channel required to complete the two out of four coincidence logic, resulting in a reactor trip. The cause of this event is a failure of the Protection Channel 4 primary power supply fuse holder in Card Frame 2. The fuse holder was found broken on the back side of the holder where the wiring lugs are attached. The fuse was in intermittent contact with the terminal lugs, resulting in spurious arcing from the terminal lug to the fuse. This arcing created spikes with a subsequent Channel 4 Over Temperature/Delta Temperature bistable trip. Corrective actions include replacing the defective fuse and fuse holder, performing thermographic surveys of the Unit 1 and Unit 2 process and control cabinet power supply fuses to identify degraded components, and revising the associated preventive maintenance procedures to include the monitoring of the protection set panel meters to detect load sharing, and sharing the lessons learned with other nuclear stations.
499 | 4991995008 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991995008R00.pdf | 1995-11-15 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On November 15, 1995, Unit 2 was in Mode 1 at 100% power. At approximately 0702 hours, Unit 2 experienced a reactor trip due to a main turbine trip after loss of generator excitation. At the time of this occurrence, reactor power was being lowered in response to a turbine generator exciter voltage increase to over 150 volts and failure of a number of exciter circuitry fuses. The cause of this event was a sudden degradation of the rectifier diodes and rectifier fuses in the main generator exciter resulting in an actuation of the loss of generator excitation relays. Corrective actions include replacement of all exciter rectifier diode/fuse modules, inspection of the Unit 1 turbine generator for any similar turbine generator exciter degradation problems, and preventive maintenance enhancements based on lessons learned from this event.
499 | 4991997004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991997004R00.pdf | 1997-03-19 | QR8 | Spurious Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. On March 19, 1997, Unit 2 was in Mode 1 at 100% power. At approximately 1555 hours while performing main turbine testing, a unit trip occurred. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed for a normal reactor trip. During post-maintenance testing on the Unit 2 Main Turbine Emergency Trip System, a condition developed that resulted in low Electro-Hydraulic Control System pressure causing a rapid closure of the main turbine throttle stop valves. The closure of the main turbine throttle stop valves resulted in a reactor trip followed by a main turbine trip. The cause of this occurrence was the intermittent failure of the inverter power supply for the channel two Automatic Stop Trip valve in the Electro-Hydraulic Control System. The inverter power supply was replaced and the condition of the other three inverters in the Electro-Hydraulic Control System were assessed and all were found to be in satisfactory condition.
499 | 4991997005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991997005R00.pdf | 1997-03-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | POWER LEVEL - 100%. On March 26, 1997, Unit 2 was in Mode 1 at 100% power. At approximately 2146 hours, a 2B Steam Generator feed flow/steam flow mismatch alarm was received. The 2B Main Feedwater Regulating Valve was discovered not responding in the automatic mode of control. After attempts to manually control the 2B Main Feedwater Regulating Valve were unsuccessful and with 2B Steam Generator level decreasing towards the automatic trip setpoint, Unit 2 reactor was manually tripped at 2147 hours. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed for a normal reactor trip. Subsequent troubleshooting determined that the cause of this occurrence was the failure of a seal-in relay for one of the two solenoid controlled air valves used to operate the 2B Main Feedwater Regulating Valve. seal-in relay and verifying other seal-in relays affecting Main Feedwater Regulating Valves in both Unit 1 and 2 had proper coil resistances.
499 | 4991997006 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991997006R00.pdf | 1997-04-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On April 30, 1997, Unit 2 was operating at 100% power in Mode 1. At approximately 2150 hours on April 30, 1997, feedwater flow oscillation to the 2D Steam Generator was observed. Attempts to manually control 2D Main Feedwater Regulating Valve resulted in erratic response. With 2D Steam Generator level at 35% and decreasing, the reactor was manually tripped at 2158 hours on April 30, 1997. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed. The cause of this occurrence was a failure of two integrated circuits in the 2D Main Feedwater Regulating Valve automatic control circuit and a hairline crack in the solder run leading to a resistor in the manual control circuit. Corrective actions included replacing the 2D Main Feedwater Regulating Valve controller-driver card and testing the control circuit satisfactorily, and performing alignment checks of the Main Feedwater Regulating Valve controller-driver cards in each Unit 2 train prior to unit restart.e:\wp\n1\nrc-wk\LER-97\5650.wpw STI: 30279653
499 | 4991997007 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991997007R00.pdf | 1997-11-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On November 21, 1997, Unit 2 was in Mode 1 at 100 percent power. At 0213 hours, multiple alarms were received the Unit 2 Control Room. The feedwater regulating valve to Steam Generator 2D was observed indicated closed Manual operation of the regulating valve electronic controls in the open direction was not effective. When Steam Generator 2D level approached 40 percent and decreasing, the reactor was manually tripped in accordance wit plant procedures. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected. Inspection of the 7300 system Process Control Cabinet 08, which provides control to the Steam Generator 2D feedwater regulating valve, determined a loss of power to the internal components of the cabinet existed. Troubleshooting determined a failed capacitor on the voltage to pulse converter circuit card had occurred and a capacitor mounting strap in the primary power supply had caused an internal short. It was determined that the fault protection design of the cabinet circuitry permitted a single circuit card capacitor failure to cause a loss of both the primary and secondary power supplies to the cabinet. The cause of the event was two separate failure mechanisms that combined to result in loss of power to the cabinet. Corrective actions include replacing the failed components associated with Process Control Cabinet 08, and initiation of evaluations to identify permanent modifications, as appropriate, to prevent failure recurrence.E:\wp\nl\nrc-ap\ler-97\0041.doc 12/18/97 (7:31AM)
499 | 4991998002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991998002R00.pdf | 1998-09-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On September 22, 1998, Unit 2 experienced an automatic reactor trip from 100 percent power when the water level in Steam Generator 2A decreased below the Reactor Protection System trip setpoint. The level decrease followed the inadvertent closure of Main Feedwater Regulating Valve 2A during corrective maintenance on the control circuitry for Low Power Feedwater Regulating Valve 2A. Work instructions governing the activity were technically incorrect, in that they directed personnel to install an unintended jumper across terminals associated with the Main Feedwater Regulating Valve. The jumper was removed subsequent to the reactor trip. Corrective actions include reviewing other similar work in progress, discussing lessons learned with key stakeholders, and developing a case study.
499 | 4991999002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4991999002R00.pdf | 1999-01-21 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On January 21, 1999, Unit 2 was in Mode 1 at 100% power. At 0607 hours CDT, Unit 2 experienced an automatic reactor trip due to closure of the turbine throttle valves. The throttle valves closed due to a loss of power to the turbine control circuitry resulting from an inadvertent opening of a 120-volt supply breaker. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. Efforts were underway to isolate a ground on 480-volt Load Center 2G1. The individual performing the ground checks opened breakers in Distribution Panel DP0408 when he should have been in Distribution Panel DP0407. The root cause for being in the wrong panel was inadequate self-verification by the individual. The inadequate verification was due to fatigue and overconfidence in performing an evolution perceived as being low risk. A contributing factor was inadequate guidance for ground isolation. Actions taken or planned in response to the cause of the trip include addressing personnel performance issues with the individuals involved in accordance with the Constructive Discipline Program, reviewing self verification training with plant operators and reactor operators, development of guidance for ground isolation, and guidance for identifying and discussing error-likely situations in pre-job briefings, and training on electrical theory for licensed operators.
499 | 4992001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992001001R00.pdf | 2001-02-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | South Texas 2 | P | WE | PO | 10 | On February 7, 2001, at 1828, Unit 2 was operating at 10% power, escalating to 12-14% power, in preparation for closing the Main Generator Breaker when a Reactor Operator performing electrical plant bus transfer operations inadvertently deenergized the 2F Auxiliary and Standby 13.8 kV busses. As a result Reactor Coolant Pump 2A was de-energized, requiring the operating crew to initiate a manual reactor trip in accordance with plant procedures. All control rods fully inserted. All actuated safety equipment operated as required. The root causes identified for this event include time pressure imposed by electrical alarms and interlocks that lead to a deviation from fundamental work practices, and less than adequate procedural direction. Corrective actions include revising procedural guidance for this activity, training Plant Operations personnel on the pitfalls for time pressure driven evolutions, and revisiting the time limit setpoints for parallel operations of 13.8 kV busses.This event was reviewed for risk impact and found to be risk insignificant since the conditional core damage probability is less than 2x10-7.
499 | 4992001002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992001002R00.pdf | 2001-03-01 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | South Texas 2 | P | WE | PO | 95 | On March 1, 2001, at 0821, Unit 2 was operating at 95% power, activities were underway to remove the 345kV switchyard North Bus for maintenance. Switchyard breaker Y590 was opened. Unknown to the operating crew, the C phase pole of switchyard breaker Y600 which had been previously closed, remained opened. With the C phase pole of breaker Y600 still opened, the Control Room received electrical panel alarms and the three operating Circulating Water Pumps tripped off line, requiring the operating crew to initiate a manual reactor trip in accordance with plant procedures. All control rods fully inserted. All actuated safety equipment operated as required. The root cause identified for this event is failure of the operating linkage of switchyard breaker Y600 C phase pole. The bushing required between the linkage pin and the operating linkage was not installed and most likely left out during fabrication. Corrective actions include repair of the failed breaker, inspection of a similar switchyard breaker, and further review of switchyard breaker inspection procedures.This event was reviewed for risk impact and found to be risk insignificant since the conditional core damage probability is less than 2x10-7.
499 | 4992001004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992001004R00.pdf | 2001-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On May 8, 2001, at 1528, Unit 2 was operating at 100% power. Activities were in progress to monitor the valve positioner on steam generator `2A' Feedwater Regulating Valve (FRV) using a laptop computer and Hart communication adapter connected to the positioner signal leads. After several minutes of monitoring, the troubleshooting team connected the laptop computer to a utility outlet to keep its battery charged. Unknown to the team, the Hart adapter was designed with one of its leads connected to the laptop computer ground. The grounded Hart adapter lead was connected to the positive signal lead of the FRV positioner. The FRV control circuit is designed with the negative signal lead connected to plant ground in the 7300 Process Cabinets. When the laptop AC power cord with ground plug was plugged into the utility outlet, both signal leads for the FRV were connected to ground. This resulted in a loss of positioner control signal, closure of the FRV and rapid decrease in steam generator `2A' water level. The operators observed the loss of feedwater flow and attempted to reopen the FRV in manual control. Operations directed the team to remove test equipment. Operations staff ordered a manual reactor trip; however, steam generator `2A' reached the LO-LO Level setpoint and the reactor tripped automatically. All control rods fully inserted. All actuated safety equipment operated as required. The root causes identified were that personnel did not recognize the ground potential of the laptop and adapter, and the work control process did not provide adequate controls for this activity. Corrective actions include improving the work control process and establishing programmatic controls for the use of test equipment.
499 | 4992002002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992002002R00.pdf | 2002-06-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On June 14, 2002 Unit 2 was operating in Mode 1 at 100% power. At approximately 0435 Unit 2 lost feedwater flow to steam generator 2C during the performance of Feedwater Valve Operability Test. This test performs a partial stroke of the feedwater isolation valve from 100 percent open to 90 percent open. During the test the valve failed closed. After verifying there was no indication of feedwater flow to the 2C steam generator, the Unit Supervisor directed the Reactor Operator to manually trip the reactor. The reactor was in the tripped condition approximately 15 seconds following closure of the feedwater isolation valve (FWIV). The unexpected closure of the 2C feedwater isolation valve resulted from a blown fuse in the class-1E control circuit for the B-train safety solenoid for the 2C isolation valve. The blown fuse was the result of a shorted rectifier assembly used for surge suppression on the B-train safety solenoid for the 2C FWIV.This event resulted in no personnel injuries, offsite radiological releases or damage to important safety related equipment. Following the reactor trip, auxiliary feedwater automatically actuated as expected. There were no human performance issues or challenges to plant safety and the plant responded as expected.
499 | 4992002003 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992002003R01.pdf | 2002-07-07 | QP5 | Excessive Feedwater Flow | [45 empty] | South Texas 2 | P | WE | PO | 100 | On July 7, 2002 Unit 2 was operating in Mode 1 at 100% power. The Unit 2 main turbine generator tripped automatically due to a High-High level in the 2B steam generator (SG). The reactor tripped automatically as a result of the main turbine trip. The trips occurred shortly after the Channel II inverter and distribution panel de-energized. The loss of the distribution panel and inverter resulted in the loss of power to the instrumentation channels selected to control narrow range steam generator water level. This failure resulted in loss of SG level signal to all four SG Main Feedwater Regulating Valve (MFRV) control circuits because they were all selected to the same channel. This caused the MFRVs to go fully open. With the MFRVs fully open, water level increased in all four steam generators. Steam generator 2B reached its high-high level set point resulting in the main turbine trip and the feedwater isolation signal. The cause of the inverter failure and distribution panel loss of power was a change in breaker E2D11/3A characteristics. As the breaker has aged, the time differential between opening of the breaker contacts has increased. As a result, the contact opening has become more sequential and less simultaneous. The second cause of the reactor trip was having all four steam generator level control switches aligned to a single control channel coupled with the loss of power to instruments on that channel. Corrective actions include splitting the SG level channels to two separate control channels, revising a procedure to deselect the channel affected by the battery charger swap at the SG level controls and inverter replacement. Additionally, the installation and testing of suppression diodes to Class 1E battery charger relays was included. This event resulted in no personnel injuries, offsite radiological releases or damage to safety related equipment. There were no challenges to plant safety and the plant responded as expected.
499 | 4992002004 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992002004R01.pdf | 2002-12-15 | QR6 | Manual Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | At 1808 hours on December 15, 2002, Unit 2 was at 100% power when it was manually tripped due to excessive vibration in Low Pressure Turbine 22. Subsequent investigation identified that a blade had cracked and broken off and was ejected from the low pressure turbine into the condenser. Additional cracked blades were found in Low Pressure Turbines 22 and 23. The cause of the blade cracking was a design flaw with the rotor train (natural frequency modes near 120 Hz) and a faulty new generator rotor (differences between old and new rotor cause increased rotor train response). These flaws were not recognized by the vendor, Siemens-Westinghouse, due to errors in their modeling of the Turbine-Generator rotor system. Corrective actions include repairing the Unit 2 rotor system and damaged blades, installing vibration monitoring equipment, and evaluating the data taken during and after the Unit 2 restart. Subsequent studies confirmed that the corrective actions were effective in reducing torsional vibrations and the plant has operated continuously since March 2003. This event resulted in no personnel injuries, offsite radiological releases or damage to safety related equipment. There were no challenges to plant safety and the plant responded as expected.
499 | 4992010005 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992010005R02.pdf | 2010-11-03 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | South Texas 2 | P | WE | PO | 100 | On November 3, 2010, the Startup Feed Pump (SUFP) 24 was being started to support a scheduled Partial Discharge Analysis as a preventive maintenance activity. At 1021 hours the SUFP was started but then after approximately 4 seconds the pump breaker tripped open. Computer data shows that approximately 8 seconds after the pump breaker tripped the voltage on Standby Bus 2H (which supplies power to the SUFP) spiked low to near zero volts and the Unit 2 reactor tripped on Reactor Coolant Pump (RCP) Undervoltage (the 2C RCP is also powered by Standby Bus 2H) . Standby Diesel Generator 23 started and began supplying Engineered Safety Features (ESF) Bus E2C due to Loss of Offsite Power to the ESF bus. Standby Bus 2F experienced a momentary voltage drop of approximately 1 second (Standby Buses 2F and 2H are both fed by the X winding of the Unit 2 Auxiliary Transformer) resulting in some A train loads being secured. Following the reactor trip, the plant was stabilized in MODE 3 at Normal Operating Pressure and Temperature.At 1038 hours an Unusual Event was declared for Unit 2 due to the breaker cubicle explosion associated with the SUFP breaker failure (ENS Event Number 46387). The breaker malfunction did not result in a fire. The Unusual Event was terminated at 1240 hours when the plant was stabilized in MODE 3.There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment.This LER is the planned LER supplement described in Revision 1 including a correction to the reporting criteria where criterion 20.2203(a)(3)(i) was inadvertently checked. This LER supplement provides the results of the respective Root Cause Evaluation and revises the appropriate reporting criteria accordingly.
499 | 4992011002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992011002R00.pdf | 2011-11-29 | QR5 | Turbine Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | On 11/26/11 at 2121 hours, Unit 2 received the Stator Coil Water (SCW) Differential Temperature high alarm. The crew determinedgenerator thermocouple T6144 on the SCW outlet of Coil 33T was reading higher than the other thermocouples. l&C Techniciansconducting a local check subsequently reported the Coil 33T thermocouple was reading within the differential temperature band. On11/27 multiple Generator Condition Monitoring (GCM) alarms were received. The operating crew subsequently removed the Coil 33Tthermocouple from service by substituting a known value. At 0310 on 11/29/11 a Stator Cooling Water trouble alarm was received. The Unit 2 Reactor tripped at 0329 hours on 11/29/11 due to Main Generator Lockout. An initial inspection of the main generator revealedsignificant stator coil damage. Approximately three feet of stator Coil 33T (top coil in slot 33) was melted or missing on the exciter end.The failure analysis determined the most likely cause was a very small leak in a hollow strand in Coil 33T. Analysis supports that thisleak existed for a long time and allowed moisture to travel inside the coil. The moisture degraded the resin in the coil allowing theconductor bundle to come loose. This condition allowed some individual conductor strands to move and vibrate. The strand-to-strandvibrations wore away the insulation and created shorts. The shorts caused excessive heating. The affected area grew due to thermaldamage until the coil arced across the missing melted area. The potential exists that the small leak was located in the portion of thecoil that is melted/missing. If so, it will not be possible to ascertain the root cause of the leak. After the final failure analysis reports arereceived, the root cause report and LER will be evaluated and revised if warranted.This condition is considered reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual orautomatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). There were no personnel injuries, nooffsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not havean adverse effect on the health and safety of the public.
499 | 4992013001 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992013001R00.pdf | 2013-01-04 | QR6 | Manual Reactor Trip | [45 empty] | South Texas 2 | P | WE | PO | 100 | At 07:05 on 1/4/2013, Unit 2, while at 100% power, commenced surveillances 0PSP03-RS-0004 and 0PSP03-RS-0001 to satisfy the monthly requirements of Technical Specification 4.1.3.1.2 and to demonstrate the shutdown and control rods are Operable by movement of at least 10 steps in any one direction.During testing, two rods on shutdown bank E (SBE) dropped to the bottom of the core and a manual reactor trip was required. The dropped rods on SBE occurred while inserting shutdown bank C (SBC) rods in 6 steps. After SBE rod M-8 dropped, rod motion was stopped. While validating the dropped rod, a second rod, D-8, in SBE dropped. At 09:41, once both dropped rods were validated by diverse indications of power, flux, and rod positions, a manual reactor trip was performed. Troubleshooting identified the problem as high resistance on Rod Holdout Mode Selector (RHMS) switch contacts in Rod Control Power Cabinet SCDE when the contacts should have been closed. This blocked the multiplexing signal to the SBE Stationary Regulation card resulting in dropped rods.This condition is considered reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
499 | 4992013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::4992013002R01.pdf | 2013-01-08 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | South Texas 2 | P | WE | PO | 100 | On January 8, 2013, at 16:40 CST, with South Texas Project Unit 2 at 100% power, a fault in the 'C' phase of the Unit 2 2A Main Transformer (MT2A) occurred resulting in a Unit 2 automatic trip and partial loss of offsite power. Pressure from the fault ruptured the transformer tank and the oil ignited. The onsite fire brigade responded, and the fire suppression system worked as designed. The fire was extinguished at 16:56. There were no injuries and no radiological impacts to the public or station personnel.<br><br> An Unusual Event was declared at 16:55 CST for initiating condition HU-2, "Fire or explosion in protected area or switchyard which affects normal plant operations". Local, county, and state offices were notified as required, and the Unusual Event was terminated at 19:47 CST, after the partial loss of offsite power was restored.<br><br> Failure analysis concluded the most likely cause was an internal ground fault or an internal turn-to-turn fault inside the "C" phase high voltage windings due to untimely degradation of the paper insulation from the cumulative effects of passthrough faults, elevated temperatures, elevated moisture, and grid disturbances over a period of years. The damage to the transformer challenged a determination of the direct root cause of the fault. If warranted, the root cause report and LER will be revised after failure evaluation forensics are complete.<br><br> Corrective actions include replacement of MT2A with an on-hand spare, installation of wireless monitoring and notification features for the online dissolved gas monitors, approval for future replacement of all four main transformers with new units to support reliable operation through the end of the currently projected plant life, and implementation of a Large Equipment Asset Management process.
528 | 5281987003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281987003R00.pdf | 1987-01-10 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 40 | POWER LEVEL - 040%. AT 0906 ON 1-10-87 PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) OPERATING AT 100% POWER WHEN A REACTOR POWER CUTBACK (RPCB) OCCURRED DUE TO A LOAD REJECTION. THE LOSS OF LOAD OCCURRED WHEN BOTH OF THE GENERATOR OUTPUT BREAKERS OPENED. THE RPCB REDUCED REACTOR POWER TO ABOUT 40%. A FEEDWATER CONTROL SYSTEM TRANSIENT WAS INITIATED BY THE LOAD REJECTION AND RPCB. A REACTOR TRIP OCCURRED AT 0910 DUE TO HIGH STEAM GENERATOR LEVEL IN STEAM GENERATOR #2. THE CAUSE OF THE GENERATOR OUTPUT BREAKER TRIP WAS DETERMINED TO BE A MALFUNCTION IN A LOGIC CHIP IN THE SUB-SYNCHRONOUS RELAY. THE CAUSE OF THE REACTOR TRIP WAS DETERMINED TO BE A COGNITIVE PERSONNEL ERROR BY A CONTROL ROOM OPERATOR (UTILITY LICENSED) CONTROLLING FEEDWATER FLOW. THE ROOT CAUSE OF THE CHIP MALFUNCTION IS UNDER INVESTIGATION. ALSO THE 1 OF 2 TRIP LOGIC OF THE SUB-SYNCHRONOUS RELAYS WILL BE REVIEWED TO DETERMINE THE FEASIBILITY OF UTILIZING 2 OF 2 TRIP LOGIC RATHER THAN 1 OF 2 TRIP LOGIC. AS CORRECTIVE ACTION FOR THE REACTOR TRIP, A NIGHT ORDER WAS ISSUED PRIOR TO RESUMPTION OF POWER OPERATION WHICH DISCUSSED THE DESIRABLE STRATEGY TO FOLLOW DURING A FEEDWATER TRANSIENT.
528 | 5281987014 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281987014R00.pdf | 1987-05-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | POWER LEVEL - 100%. AT 0218 MST ON MAY 30, 1987, PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) OPERATING AT APPROXIMATELY 99.5 PERCENT POWER, WHEN THE MAIN FEEDWATER PUMP (MFP) 'A' TRIPPED DURING THE WEEKLY MFP TURBINE OVERSPEED TEST. A REACTOR POWER CUTBACK WAS INITIATED AS A RESULT OF THE MFP TRIP. SUBSEQUENTLY AN AUTOMATIC REACTOR PROTECTION SYSTEM ACTUATION INITIATED A REACTOR TRIP DUE TO VARIABLE OVERPOWER TRIP SIGNALS RECEIVED FROM CHANNELS A AND B. THE PLANT WAS STABILIZED IN MODE 3. THE ROOT CAUSE OF THE EVENT WAS DETERMINED TO BE A FAILED LIMIT SWITCH IN THE OVERSPEED TRIP LOCKOUT VALVE CIRCUIT OF THE MFP TURBINE. AS CORRECTIVE ACTION, THE LIMIT SWITCH WAS REPAIRED, SUCCESSFULLY TESTED, AND RETURNED TO SERVICE. NO PREVIOUS SIMILAR REPORTS HAVE BEEN SUBMITTED REGARDING A REACTOR TRIP WHICH RESULTED FROM A FAILED LIMIT SWITCH DURING MFP TURBINE TESTING.
528 | 5281987018 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281987018R01.pdf | 1987-08-27 | QG9 | Primary System Leak | [45 empty] | Palo Verde 1 | P | CE | PO | 8 | POWER LEVEL - 008%. THIS IS A SUPPLEMENT TO LER 87-018-00. AT APPROXIMATELY 2037 MST ON AUGUST 27, 1987 PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 8 PERCENT REACTOR POWER WHEN A REACTOR TRIP OCCURRED DUE TO THE AXIAL SHAPE INDEX OF THE REACTOR CORE. THE TRIP OCCURRED AS THE UNIT WAS SHUTTING DOWN TO EVALUATE A POSSIBLE REACTOR COOLANT SYSTEM (RCS) PRESSURE BOUNDARY LEAK. THE PRESENCE OF A PRESSURE BOUNDARY LEAK WAS CONFIRMED AFTER THE UNIT WAS STABILIZED IN MODE 3 (HOT STANDBY). THE ROOT CAUSE OF THE REACTOR TRIP WAS A DEFICIENT PROCEDURE. TO PREVENT RECURRENCE PROCEDURAL ENHANCEMENTS HAVE BEEN IMPLEMENTED. THE CAUSE OF THE LEAK WAS A CRACKED SOCKET WELD ON THE UPSTREAM SIDE OF THE ISOLATION VALVE FOR THE FLANGED REFUELING WATER LEVEL INDICATION. THE ROOT CAUSE FOR THE CRACKED WELD WAS FATIGUE FAILURE, INDUCED IN PART BY CYCLIC LOADING. AS CORRECTIVE ACTION THE VALVE WAS CUT OUT AND REPLACED, AND PIPE SUPPORTS WERE ADDED TO THIS PIPE AND TO FIVE ADDITIONAL PIPES OF SIMILAR CONFIGURATION TO REDUCE CYCLIC LOADING.
528 | 5281988011 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281988011R00.pdf | 1988-04-19 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 0148 MST ON APRIL 1-9, 1988, PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) AT 100% REACTOR (RCT) POWER WHEN THE UNIT EXPERIENCED A 100% LOAD REJECTION AND RESULTANT REACTOR POWER CUTBACK (RPCB). APPROXIMATELY 30 SECONDS AFTER THE RPCB, A REACTOR TRIP OCCURRED DUE TO A LOW DNBR TRIP FROM THE CORE PROTECTION CALCULATOR (CPC)(CPU). A CONTROL ROOM OPERATOR (UTILITY, LICENSED) INADVERTENTLY OPENED THE MOTOR OPERATED DISCONNECT (MOD) FOR UNIT 1 MAIN GENERATOR (GEN)(MOD PL-910). THIS INITIATED A LOAD REJECTION AND SUBSEQUENT GENERATOR TRIP AND TURBINE (TRB) TRIP RESULTING IN A RPCB. AN INTERLOCK BETWEEN MOD PL-910 AND THE ASSOCIATED 525 KV (FK) BREAKERS (BKR) AND MANUAL DISCONNECTS PL-916 AND PL-917 DID NOT FUNCTION. THIS ALLOWED MOD PL-910 TO OPEN INITIATING THE LOAD REJECTION. IMMEDIATE CORRECTIVE ACTION WAS TO REPAIR THE PERMISSIVE CONTACTS ON PL- 916 AND PL-917 AND ENSURE THAT THE INTERLOCK WAS OPERABLE. FOR CORRECTIVE ACTION TO PREVENT RECURRENCE, THE INTERLOCK CIRCUIT WILL BE ELECTRICALLY CHECKED PERIODICALLY FOR PROPER OPERATION. AN ENGINEERING EVALUATION REQUEST HAS BEEN INITIATED FOR A REANALYSIS OF THE RPCB AND THE SOFTWARE/DATA FOR THE CPC'S. ALSO APPROPRIATE DISCIPLINARY ACTION WILL BE ADMINISTERED. NO PREVIOUS SIMILAR EVENTS HAVE BEEN REPORTED.
528 | 5281988015 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281988015R00.pdf | 1988-05-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 91 | POWER LEVEL - 091%. AT 1315 MST ON MAY 12, 1988, PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 91% POWER WHEN AN AUTOMATIC ACTUATION OF THE REACTOR (RCT)(AC) PROTECTION SYSTEM (RPS)(JC) OCCURRED. SURVEILLANCE TEST 36ST-9SB04 (PLANT PROTECTIVE SYSTEM (PPS)(JC) FUNCTIONAL TEST- RPS/ENGINEERED SAFETY FEATURE ACTUATION SYSTEMS (ESFAS)(JE)) WAS IN PROGRESS WHEN THE REACTOR (RCT)(AC) TRIP OCCURRED. PERFORMANCE OF 36ST-9SB04 INVOLVES A SEPARATE POWER SUPPLY (JX)(JC) UTILIZED ONLY DURING TESTING TO 'HOLD' THE BISTABLE AND MATRIX RELAYS FROM ACTUATION DURING THE TEST. THE POWER SUPPLY WAS FOUND TO BE VARYING IN AMPLITUDE INTERMITTENTLY WHICH WOULD CAUSE VARYING REMOVAL AND REINSTATEMENT OF THE BUCK AND BOOST VOLTAGE. THIS CAUSED THE TRIP OF THE 'A' AND 'D' REACTOR TRIP CIRCUIT BREAKERS. IMMEDIATE CORRECTIVE ACTION WAS TO REPLACE THE POWER SUPPLY WITH A PROPERLY OPERATING POWER SUPPLY. A PRECAUTION WAS ADDED TO 36ST-9SB04 TO ENSURE THAT THE TEST PERFORMER IS AWARE THAT THE POWER SUPPLY MAY EXHIBIT INSTABILITIES AS INDICATED BY LAMP 'FLICKERING'.
528 | 5281988010 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281988010R01.pdf | 1988-07-06 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Palo Verde 1 | P | CE | PO | 100 | POWER LEVEL - 100%. ON JULY 6, 1988, PALO VERDE UNIT I WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 100 PERCENT POWER WHEN THE REACTOR TRIPPED ON A LOW DEPARTURE FROM NUCLEATE BOILING RATIO (DNBR). THE NON-CLASS IE 13.8 KV BUS IE-NAN-S02 FAULTED TO GROUND EXACERBATING AN EXISTING WEAKNESS IN THE UNIT AUXILIARY TRANSFORMER CAUSING THE UNIT AUXILIARY TRANSFORMER TO RUPTURE AND CATCH FIRE. THIS CAUSED A LOSS OF ELECTRICAL POWER TO THE REACTOR COOLANT PUMPS INITIATING THE LOW DNBR TRIP. THE REACTOR WAS STABILIZED IN MODE 3 (HOT STANDBY) ON NATURAL CIRCULATION. A NOTIFICATION OF UNUSUAL EVENT (NUE) WAS DECLARED AT 1215 MST DUE TO THE FIRE. THE FIRE WAS EXTINGUISHED AND THE NUE TERMINATED AT 1221 MST. AT 1303 MST AN ATTEMPT WAS MADE TO REENERGIZE THE FAULTED BUS 1E-NAN-S02 AND A FIRE STARTED IN THE SWITCHGEAR. AN NUE WAS DECLARED DUE TO THE FIRE AND LOSS OF NON-CLASS 13.8 KV ELECTRICAL POWER. THIS FIRE WAS EXTINGUISHED AT 1322 MST. FOLLOWING VISUAL INSPECTIONS, CLEANING, AND MEGGERING, IE-NAN-SOI WAS REENERGIZED AT 1749 MST. REACTOR COOLANT PUMP IA WAS STARTED AT 0033 MST ON JULY 7, 1988, AND FORCED CIRCULATION WAS REESTABLISHED. THE NUE WAS TERMINATED AT 0102 MST ON JULY 7, 1988 AND A COOLDOWN WAS COMMENCED. CORRECTIVE ACTIONS TAKEN TO PREVENT RECURRENCE INCLUDE THE REWORK OF BUS IE-NAN-S02 AND THE REPLACEMENT OF THE UNIT AUXILIARY TRANSFORMER.
528 | 5281988021 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281988021R00.pdf | 1988-08-21 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 75 | POWER LEVEL - 075%. ON AUGUST 21, 1988 AT APPROXIMATELY 1125 MST, PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 75 PERCENT POWER WHEN THE REACTOR TRIPPED DUE TO HIGH PRESSURIZER PRESSURE. AT APPROXIMATELY 1124 MST ON AUGUST 21, 1988 THE MAIN TURBINE TRIPPED ON LOW STATOR COOLING WATER FLOW SIGNAL. THE CAUSE OF THE TURBINE TRIP WAS THE FAILURE OF A MICROSWITCH IN THE STATOR COOLANT FLOW TRIP CIRCUIT. THE CAUSE OF THE REACTOR TRIP WAS HIGH PRESSURIZER PRESSURE DUE TO STEAM BYPASS CONTROL VALVES (SBCV) 1001 AND 1004 CLOSING FASTER THAN EXPECTED AND THE MALFUNCTION OF SBCV 1003. OTHER THAN THE REACTOR TRIP, NO MANUALLY OR AUTOMATICALLY INITIATED SAFETY SYSTEM RESPONSES WERE RECEIVED AND NONE WERE NECESSARY. IMMEDIATE CORRECTIVE ACTION WAS TO REPLACE THE MICROSWITCH. TO PREVENT RECURRENCE, TROUBLESHOOTING AND REWORK OF THE SBCVS HAS BEEN PERFORMED.
528 | 5281988024 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281988024R00.pdf | 1988-08-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 1 | P | CE | PO | 12 | POWER LEVEL - 012%. AT 0826 MST ON AUGUST 27, 1988, PALO VERDE UNIT 1 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 12 PERCENT REACTOR POWER WHEN A REACTOR TRIP OCCURRED DUE TO LOW LEVEL IN STEAM GENERATOR 1. THE MAIN GENERATOR WAS SYNCHRONIZED TO THE GRID AT 0816 MST ON AUGUST 27, 1988 AND LOADED TO APPROXIMATELY 80 MWE. A REACTOR COOLANT SYSTEM (RCS) COOLDOWN BEGAN AND PRESSURIZER LEVEL BEGAN TO DECREASE. A REACTOR OPERATOR INCREASED DILUTION FLOW IN AN ATTEMPT TO RAISE TEMPERATURE AND STARTED THE THIRD CHARGING PUMP IN AN ATTEMPT TO INCREASE PRESSURIZER LEVEL. ALSO, CONTROL ELEMENT ASSEMBLY (CEA) GROUP 5 WAS WITHDRAWN AND THE LOAD ON THE MAIN GENERATOR WAS DECREASED TO APPROXIMATELY 45 MWE IN AN ATTEMPT TO MITIGATE THE COOLDOWN. AS A RESULT OF THE DILUTION AND CEA WITHDRAWAL, REACTOR POWER INCREASED TO THE POINT OF SWAPOWER FOR THE FEEDWATER REGULATING VALVES. THE ISOLATION VALVES WERE SHUT FOR THE ECONOMIZER FEED REGULATING VALVES AND ALL FEED FLOW WAS LOST. THE DOWNCOMER VALVES WERE REOPENED AND FEEDWATER FLOW REESTABLISHED. THE EVENT APPEARED TO BE STABILIZED WHEN THE 'B' MAIN FEED PUMP TRIPPED ON HIGH DISCHARGE PRESSURE. STEAM GENERATOR LEVEL DECREASED AND THE REACTOR TRIPPED. TO PREVENT RECURRENCE, 40AC-9ZZ02 (CONDUCT OF SHIFT OPERATIONS) WILL HAVE A REQUIREMENT ADDED WHICH SPECIFIES THAT A BRIEFING OR 'TAILBOARD' MEETING SHOULD BE HELD PRIOR TO COMMENCEMENT OF ALL MAJOR PLANT EVOLUTIONS.
528 | 5281989004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281989004R00.pdf | 1989-03-05 | QR8 | Spurious Reactor Trip | [7 empty] | X | [25 empty] | X | X | [10 empty] | Palo Verde 1 | P | CE | PO | 100 | POWER LEVEL - 100%. ON MARCH 5, 1989, PALO VERDE UNIT 1 WAS OPERATING AT APPROXIMATELY 100 PERCENT POWER WHEN, AT APPROXIMATELY 1001 MST A REACTOR TRIP OCCURRED ON DEPARTURE FROM NUCLEATE BOILING RATIO (DNBR) DUE TO A CONTROL ELEMENT ASSEMBLY CALCULATOR (CEAC) FAILURE. DURING THE ENSUING TURBINE/GENERATOR TRIP, POWER WAS LOST TO ONE OF THE TWO 13.8 KV NON- CLASS ELECTRICAL BUSSES WHEN THE BUS'S NORMAL FEEDER BREAKER DID NOT TRIP AS REQUIRED. A SMALL FIRE WAS OBSERVED AND SUBSEQUENTLY EXTINGUISHED ON THE FEEDER BREAKER TRIP COIL. THE CAUSE OF THE TRIP WAS A FAILURE OF THE CEAC #2 PROCESSOR BOARD. THE PROCESSOR BOARD WAS REPLACED.
528 | 5281990006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281990006R00.pdf | 1990-08-14 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On August 14, 1990 Palo Verde Unit 1 was operating in Mode 1 at 100 percent power. At approximately 2159 MST it was discovered that the 'B' phase of the Main Transformer had lost forced cooling. A rapid power reduction was initiated in order to unload the transformer within 30 minutes as required by the alarm response procedure for a loss of transformer cooling and to minimize the transient on the plant. The Main Turbine was manually tripped at approximately 2223 with the reactor at approximately 65 percent power. Approximately 30 seconds after the Main Turbine trip, the reactor tripped on high pressurizer pressure. All systems functioned as designed and the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The loss of cooling to the Main Transformer was caused by the failure of a control power transformer. The reactor trip has been determined to be the expected result of a load reject with the reactor at 65 percent power with steam bypass control configured for normal (100 percent power) operation.<br /><br /> The control power transformer was replaced. The alarm response procedure for the Main Transformer will be revised to enhance directions for the "No Voltage Alarm". Enhancements to the steam bypass control system are currently under evaluation.
528 | 5281991009 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281991009R00.pdf | 1991-09-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Palo Verde 1 | P | CE | PO | 55 | On September 14, 1991, at approximately 1722 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 55 percent power when a reactor trip and a Main Steam Isolation Signal (MSIS) Engineered Safety Features actuation occurred due to high steam generator level. Prior to the reactor trip and MSIS, reactor power had been reduced as a result of a Part-Length Control Element Assembly slipping part way into the core during monthly testing. This power reduction was required by Technical Specifications. There were no other safety system responses required. The reactor trip was diagnosed as an uncomplicated reactor trip. The plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip and MSIS on high steam generator level was due to the number 1 steam generator economizer valve failing open which resulted in overfeeding the steam generator. The economizer valve failure was due to a failure of the economizer valve positioner. <br /><br /> Troubleshooting was performed, the ability to withdraw the part-length CEA was restored, the economizer valve positioner replaced and tested, and both were returned to service. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
528 | 5281991010 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281991010R00.pdf | 1991-10-27 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On October 27, 1991, at approximately 0722 MST, Palo Verde Units 1 and 3 were operating at approximately 100 percent power when a grid perturbation caused the Main Turbine Control System to fast close and immediately reopen the turbine control valves (TVCs). The momentary reduction in steam flow caused the steam bypass control valves in Units 1 and 3 to quick open. A reactor power cutback occurred in Unit 3, but not in Unit 1. Reactor trips in Units 1 and 3 occurred when reactor power exceeded the Core Protection Calculator Variable Overpower Trip setpoints. Immediately following the trips, Safety Injection Actuation System (SIAS) and Containment Isolation Actuation System (CIAS) Engineered Safety Feature Actuation System actuations occurred on low pressurizer pressure. All safety system components actuated as designed in each unit. By approximately 0805 MST on October 27, 1991, the plants were stabilized in Mode 3 (HOT STANDBY). <br /><br /> The cause of the event was determined to be the expected plant response to a unique combination of circumstances. The event was precipitated by a grid fault resulting from a lightning strike on a substation feeder line. The fault which occurred was different from previous grid disturbance events (i.e., fault without ground). The generator output current at Palo Verde decreased triggering a momentary Power/Load Unbalance turbine protection actuation. This submittal also provides a Special Report in accordance with Technical Specification 3.5.2 ACTION b.
528 | 5281992012 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281992012R00.pdf | 1992-09-28 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | At approximately 2137 MST On September 28, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Unit 1 Main Turbine trip occurred followed by a reactor trip on high pressurizer pressure. The Shift Supervisor classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. At approximately 2250 MST on September 28, 1992, the plant was stabilized in Mode 3 (HOT STANDBY). No other safety system responses occurred and none were required. <br /><br /> APS Plant Engineering has determined that the cause of the reactor trip was the spurious, partial actuation of the Sub-synchronous Auxiliary Relay. The apparent cause of the actuation of the relay was the touching of an AC soldering iron to an energized 125V DC alarm circuit during performance of corrective maintenance. Contributing factors to the event included relay gap settings, which were less than the vendor specifications, and the sensitivity of the Auxiliary Relay to minor voltage transients.<br /><br /> The utilization of soldering irons on energized equipment was restricted and interim guidance for work on energized equipment was provided.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
528 | 5281992016 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281992016R00.pdf | 1992-12-08 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | At approximately 1430 MST on December 8, 1992, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Unit 1 main turbine trip occurred followed by a reactor trip on high pressurizer pressure. At approximately 1450 MST, on December 8, 1992, the plant was stabilized in Mode 3 (HOT STANDBY). The Shift Supervisor (utility, licensed) classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. No other safety system responses occurred and none were required. <br /><br /> APS Plant Engineering has determined that the apparent cause of the reactor trip was a turbine trip caused by the actuation of the Static Negative Sequence Time Over Current Relay following a grid perturbation when the relay incorrectly continued to count down after the disturbance cleared. The Static Negative Sequence Time Over Current Relay has been replaced in each Unit's Main Generator output control circuit with an updated model not susceptible to the timing problems identified in this investigation.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
528 | 5281993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281993001R00.pdf | 1993-01-30 | QR5 | Turbine Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 96 | At approximately 0603 MST on January 30, 1993, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 96 percent power when a Unit 1 Main Turbine trip occurred. Control Room operators initiated a manual reactor trip after receiving high pressurizer pressure pretrip alarms in anticipation of the Reactor Protection System high pressurizer pressure trip. <br /><br /> At approximately 0615 MST on January 30, 1993, Control Room operators stabilized the plant in Mode 3 (HOT STANDBY). The Shift Supervisor classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. No other safety system responses occurred and none were required. <br /><br /> APS Maintenance personnel have determined that the cause of the Main Turbine trip was due to the failure of Moisture Separator Reheater D Drain Tank high level controller. This resulted in a high level condition in Moisture Separator Reheater D which actuated the Main Turbine's electrical trip system. <br /><br /> No previous similar events have been reported pursuant to 10CFR50.73.
528 | 5281995008 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281995008R00.pdf | 1995-05-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 1 | P | CE | PO | 65 | On May 30, 1995, at approximately 2242 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 65 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System trip setpoint for low steam generator water level following the degradation of main feedwater flow. The Feedwater Control System effectively functioned to maintain levels until an Auxiliary Feedwater pump was placed in service to restore levels. Pre-trips for the Auxiliary Feedwater Actuation System (AFAS) were received on SG-2, but level was recovered prior to the setpoint for actuation of the AFAS. The Steam Bypass Control System responded as designed to control secondary system pressure. Required plant equipment and safety systems responded to the event as designed. required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 0000 MST on May 31, 1995, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip was initiated by the closure of Feedwater isolation valve (FWIV) 1JSGBUV0137. The valve closed as a result of a loose wire for the A solenoid for the FWIV. The wire bundle was moved during the replacement of the coil for the D solenoid. As corrective action all wire connections on the terminal boards on the Unit 1 FWIVs and Main Steam Isolation Valves were verified to be secure. The initial evaluation of personnel performance has not identified any Human Performance issues during this event. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 530/94-005 and 529/92-001.
528 | 5281995012 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281995012R00.pdf | 1995-11-26 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Palo Verde 1 | P | CE | PO | 100 | On November 26, 1995, at approximately 2100 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when the main turbine tripped on low condenser vacuum. A reactor power cutback was initiated upon the main turbine trip; however, due to the lockout of the other six steam bypass control valves (SBCVs) (to the condenser) on low condenser vacuum, only the two atmospheric SBCVs were available to maintain secondary pressure. A reactor trip resulted from a high water level in Steam Generator (SG) Number 1, and an Engineered Safety Feature Actuation System actuation of the Main Steam Isolation System also occurred due to the SG high water level. <br /><br /> The cause of the reactor trip was high steam generator water level in Steam Generator Number 1. A preliminary Personnel Performance Evaluation was conducted and no major Human Performance issues were identified. <br /><br /> On November 28 and 29, 1995, a system walkdown was performed in Units 2 and 3 that identified two vacuum breaker valves leaking on the 'A' and 'B' condenser shells in Unit 2. These valves were reworked on December 2, 1995.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
528 | 5281995014 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281995014R00.pdf | 1995-12-09 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Palo Verde 1 | P | CE | PO | 40 | POWER LEVEL - 040%. On December 9, 1995, at approximately 0320 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 40 percent power when a native desert animal (Ringtail Cat) caused a momentary phase to ground path on startup transformer NAN-X03 (non-class 1E) causing the Transformer Differential relay to trigger from a phase imbalance. This resulted in deenergization of non-class 13.8 kV buses NAN-S05, NAN-S03, and class 1E 4.16 kV bus PBA-S03 in Unit 1. Also, NAN-X03 has a second set of windings supplying Unit 2; when the transformer was isolated from the fault, this resulted in deenergizing non-class 13.8 kV buses NAN-S06 and NAN-S04, and class 1E 4.16 kV bus PBB-S04 in Unit 2. The loss of power to the class 1E 4.16 kV buses resulted in a valid ESFAS signal starting the EDGs. The loss of PBA-S03, in Unit 1, also resulted in the loss of non-class 1E instrument power to the feedwater and steam bypass control systems (FWCS and SBCS). <br /><br /> At approximately 0322 MST, a reactor trip occurred in Unit 1 when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. <br /><br /> The root cause for the Unit 1 reactor trip was determined to be a malfunction of the FWCS' power supply, NNN-D11, transfer switch. An evaluation of the adequacy of NNN-D11 to support the FWCS and SBCS during power losses is ongoing. Any corrective actions identified will be tracked under the APS Commitment Action Tracking System. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 529/95-005, 528/95-008, 530/94-007, 530/94-005, 530/93-001 and 529/92-001.
528 | 5281996004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281996004R00.pdf | 1996-08-10 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | At approximately 1549 MST on August 10, 1996, Palo Verde Units 1 and 3 were operating at approximately 100 percent power, when both reactors tripped on low departure from nucleate boiling ratio (DNBR) following a major grid perturbation. The grid perturbation was characterized by an initial substantial load decrease followed by a significant load demand increase. The reactor trip was generated due to power exceeding the variable over power trip (VOPT) setpoint within the core protection calculators (CPC). Power exceeded the VOPT setpoint when steam bypass control system (SBCS) valves (SBCV) opened in response to turbine load fluctuations induced by the grid perturbation. By approximately 1645 MST, both plants were stabilized in Mode 3 (HOT STANDBY) and the Unit 1 and Unit 3 shift supervisors classified the events as uncomplicated reactor trips. There were no ESF actuations and none were required. Required plant equipment and safety systems responded to the event as designed in each unit. <br /><br /> The grid disturbance originated in the Pacific Northwest when soaring temperatures wilted power lines, some of which sagged into trees and 'flashed-over' or short-circuited. The grid disturbance resulted in a massive Western power outage. As stated above, because the initiating event was a major grid perturbation and not a full load rejection, the generator output current decrease was only momentary. The opening of the SBCVs resulted in a reactor power transient and subsequent reactor trip.
528 | 5281997001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281997001R00.pdf | 1997-05-27 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On May 27, 1997, at approximately 0034 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low departure from nucleate boiling ratio (DNBR) following the load shed of two reactor coolant pumps (RCP). The non-Class 1E 13.8 kV electrical bus (NAN-S01) performed a load shed of two of the four RCPs on an indicated undervoltage signal. The core protection calculator (CPC) generated a reactor trip on low DNBR due to low RCP speed. By approximately 0352 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor classified the event as an uncomplicated reactor trip. There were no engineered safety features (ESF) actuations and none were required. Required safety systems responded to the event as designed.The cause of the indicated undervoltage signal and subsequent load shed was attributed to a degraded fuse on the bus voltage potential transformer (PT). As corrective action, the fuse was replaced. NAN-S01's PT and connections were checked satisfactory. A transportability review was performed to check the remaining non-Class 1E 4.16 kV and 13.8 kV PT fuses in Unit 1 associated with load shedding and synchronizing. Similar fuses in Units 2 and 3 have been checked.A previous similar event was reported in LER 529/89-009-00.
528 | 5281998002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281998002R00.pdf | 1998-02-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On February 22, 1998, at approximately 2221 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low steam generator number 2 (SG-2) water level due to a decrease in main feedwater flow. In addition to the reactor trip, the unit received an Engineered Safety Feature Actuation System actuation of the auxiliary feedwater system 2 (AFAS-2) on low SG-2 water level. On receipt of the AFAS-2, both emergency diesel generators started and ran unloaded as designed. By approximately 2259 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Manager classified the event as an uncomplicated reactor trip. All safety systems functioned as designed. There were no other safety system actuations and none were required.The reactor tripped on low SG-2 water level following the spurious closing of the economizer regulating valve by approximately 25 percent. A preliminary evaluation has determined that the apparent root cause of the economizer regulating valve closure is attributed to a failure of the dynamic compensator card in the compensated level signal circuitry which is an input to the feedwater control system 2 (FWCS-2) master controller. As corrective action, the FWCS-2 was quarantined. Following troubleshooting, the card was replaced and the unit restarted.No previous similar events have been reported pursuant to 10CFR50.73.
528 | 5281999001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281999001R00.pdf | 1999-03-10 | QR0 | RCS High Pressure (RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Palo Verde 1 | P | CE | PO | 100 | On March 10, 1999 at approximately 1325 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100% power, when a reactor trip occurred due to a loss of heat removal capability caused by improper operator intervention following a spurious closure of the main turbine control valves. An electrical malfunction caused the main turbine control valves to close decreasing the electrical load on the turbine. The steam bypass control system (SBCS) responded to maintain the loss of heat removal caused by the load shed. The control room supervisor directed the secondary operator to place the SBCS to emergency off which initiated a reduction in heat removal and resulted in a reactor coolant pressure increase to the high pressurizer pressure setpoint, subsequently tripping the reactor. In addition to the reactor trip, the unit received an engineered safety feature actuation system actuation of the main steam system (MSIS) on high steam generator-2 level due to the steam generator-2 economizer valve not staying fully closed and allowing level to reach the MSIS setpoint. At approximately 1335 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the shift manager classified the event as an uncomplicated reactor trip. All safety systems functioned as required. There were no other safety system actuations and none were required.The preliminary cause of the turbine control valves going closed was a failure of the throttle pressure sensing circuit. An equipment root cause of failure is in progress. The cause of the reactor trip was attributed to supervisory methods that did not ensure sufficient information was collected to support an operational decision.No previous similar events have been reported pursuant to 10CFR50.73.
528 | 5282002001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282002001R00.pdf | 2002-11-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 64 | On November 10, 2002 at approximately 2250 MST, Palo Verde Unit 1 was in Mode 1 (POWEROPERATION), operating at approximately 64 percent power when an automatic reactor trip occurred on low Departure from Nucleate Boiling Ratio (DNBR). The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to the misalignment of a Control Element Assembly (CEA) from its subgroup. The misalignment occurred due to a failed optical isolation card in the control system for the CEA. The reactor was stabilized in Mode 3 (HOT STANDBY), and the Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required.The cause of the reactor trip was a hardware failure that caused a CEA position deviation. Based on the CEA deviation, a large penalty factor was generated in both control element assembly calculators (CEAC1 and CEAC2), that resulted in an automatic reactor trip to occur on low DNBR. In the past three years, there have been no previous similar events reported pursuant to 10CFR50.73.
528 | 5282003002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282003002R01.pdf | 2003-03-27 | QL6 | Condenser Leakage | [45 empty] | Palo Verde 1 | P | CE | PO | 98 | On March 27, 2003 with Unit 1 operating in Mode 1, Power Operation, at approximately 97 percent power, a HOTWELL A HIGH SODIUM alarm was received in the chemistry laboratory at approximately 09:27 MST. Chemistry personnel responded to the alarm and determined that hotwell 1A sodium was trending up. The condensate system was operating in the demineralizer by-pass mode at the time of the event. Control room personnel were notified and the abnormal operating (AO) procedure, Condenser Tube Rupture, 40AO-9ZZ10, was entered. Steam generator sodium levels continued to increase and at approximately 09:43 MST, in accordance with the procedure, the Control Room Supervisor (CRS) directed a manual reactor trip be initiated.All controls rods fully inserted and the plant was stabilized in Mode 3, Hot Standby. No other safety systems actuated and none were required. Problems were encountered with maintaining letdown flow but the control room operators were able to control pressurizer level within acceptable limits. The plant was cooled down to Mode 5, Cold Shutdown, to cleanup SG chemistry and to repair the cause of the intrusion to the hotewell. The cause of the event was determined to be the failure of a previously installed main condenser tube plug. The cause of the plug failure has been determined to be a manufacturing defect that may have been aggrevated during the installation of the plug. The failed tube was replalced. No other similar events have been reported by Palo Verde in the past three years.
528 | 5282004006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282004006R01.pdf | 2004-06-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Palo Verde 1 | P | CE | PO | 100 | On June 14, 2004, at approximately 07:41 MST, a ground-fault occurred on the Western Area Power Authority 230kV Liberty substation to Westwing substation line (approximately 47 miles from the Palo Verde Nuclear Generating Station). A failure in the protective relaying resulted in the ground-fault not isolating from the local grid for approximately 38 seconds. The fault cascaded into the protective tripping of a number of 230kV and 525kV transmission lines, which ultimately led to the Loss of Offsite Power (LOOP) at the Palo Verde switchyard. In Unit 1 and 2, the LOOP caused each reactor to trip from 100 percent power on a Core Protection Calculator generated reactor trip on low Departure from Nucleate Boiling Ratio due to low Reactor Coolant Pump (RCP) shaft speed. Unit 3 tripped last and experienced a Variable Over Power Trip from approximately 109 percent power due to increased flow from the RCPs caused by an increase in voltage and frequency from the main turbine generator.The LOOP placed each Unit in a condition for "Notice of Unusual Event" (NUE). The Unit 2 Train "A"emergency diesel generator started, but failed to maintain electrical output during load sequencing and resulted in the declaration of an "Alert" in Unit 2 at 07:54 MST. The NUE for Units 1 & 3 was declared at 07:58 MST.No similar condition has been reported in the past three years.
528 | 5282005005 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282005005R00.pdf | 2005-08-26 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Palo Verde 1 | P | CE | SU | 3 | On August 26, 2005 at approximately 18:24 (MST), Unit 1 reactor tripped during a plant startup. Main Feedwater had been placed in service and the digital feedwater control system (DFWCS) was in automatic. Uncomfortable with the system performance, the secondary control room operator attempted to maintain steam generator (SG) level by taking manual control of the DFWCS and adjusting the level. After several attempts selecting the DFWCS from automatic to manual, excessive feed rate increased the SG water level to near its trip setpoint before feeding was secured. As the cooler water expanded, the high SG level setpoint was reached resulting in an engineered safety feature (ESF) actuation of the Main Steam Isolation System (MSIS) and a reactor Trip once the S/G reached 91.5 percent narrow range (NR) level. The high level trip was caused by a combination of individual and team human performance deficiencies and inadequate resolution of identified DFWCS issues. Operation's management removed affected personnel from shift duties until preliminary investigation determined extent of performance deficiencies and coached those individuals on personal accountability to ensure compliance with Operations Department Principles and procedures prior to resumption of shift duties.No similar condition has been reported in the past three years.
528 | 5282006006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282006006R00.pdf | 2006-10-21 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | All times listed in this event report are approximate and Mountain Standard Time (MST) unless otherwise indicated.At 15:49 hours on October 21, 2006, the PVNGS Unit 1 Reactor automatically tripped from 100% power due to Core Protection Calculator (CPC) generated Low DNBR trips. Prior to the reactor trip, Control Element Assembly (CEA) #29 position indication on Reed Switch Position Transmitter (RSPT) 'A' was observed fluctuating approximately between 142 - 150 inches withdrawn, resulting in numerous Control Element Assembly Calculator (CEAC) #1 deviation alarms from 14:40 hours until the time of trip. Following Operations Computer Systems (OCS) confirmation of the fluctuating field input signal for CEA #29, the Control Room staff was preparing to remove CEAC #1 from service. The automatic reactor trip occurred before the CEAC #1 inoperable (INOP) codes were placed into the CPCs.The Direct Cause of this event was fluctuations in the CEA #29 position indication signal sent from RSPT "A" to CEAC #1 due to excessive circuit resistance at a cable connector.In the past three years, Palo Verde experienced one similar trip event due to a fluctuating CEA position input signal.
528 | 5282010001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282010001R00.pdf | 2010-03-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On March 7, 2010, at approximately 1115, Mountain Standard Time, Unit 1 experienced an automatic reactor trip subsequent to a ground fault on a non-class 13.8 kV (Calvert) bus (1 E-NAN-A03). The ground fault on 1 E-NAN-A03 caused a loss of power to the non-class 13.8 kV bus 1 E-NAN-S01. Consequently, two of the four Reactor Coolant Pumps were de-energized resulting in the reactor trip. The Main Feedwater Pump B was manually tripped, and the Auxiliary Feedwater Pump B was manually started. Due to the loss of power on the affected non-class 1 E buses, several main turbine and main steam valves failed to close resulting in higher than normal post shutdown steam flow and an undesired Reactor Coolant System (RCS) cooldown. Auxiliary Operators manually closed the affected valves, but cooldown of the RCS continued due to seat leakage of some secondary system valves. The Main Steam Isolation Valves (MSIVs) were closed to mitigate the undesired RCS cooldown. Subsequently, it was determined prudent to cooldown to Mode 5 to establish plant conditions for the bus repair. No automatic engineered safety feature actuations occurred during the event and none were required. All safety-related buses remained energized from normal off-site power during and following the reactor trip. The bus was taken off-site for evaluation and repair prior to restarting Unit 1 on March 19, 2010. The event investigation revealed the fault was caused by a combination of water intrusion and degraded bus insulation. In the past three years, Palo Verde Nuclear Generating Station has not reported a similar event where the loss of a non-class power bus due to a bus failure resulted in a reactor trip.
528 | 5282011004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282011004R00.pdf | 2011-08-06 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On August 6, 2011, at approximately 1119 Mountain Standard Time, during the performance of surveillance test 40ST-9SF01, Control Element Assembly (CEA) Operability Checks, the Unit 1 reactor tripped due to an automatic actuation of the reactor protection system. The actuation occurred when CEA 37 of shutdown group B fully inserted causing a deviation of greater than 9.9 inches from other CEAs in its subgroup. This deviation generated a CEA calculator penalty factor and actuated the low departure from nucleate boiling ratio and the high local power density trips on all four core protection calculator channels. Following the reactor trip, plant operators observed CEA 16 of regulating group 5 did not indicate that it had fully inserted. While operators prepared to borate the reactor coolant system, full insertion indication for CEA 16 was received approximately 1.5 minutes following the reactor trip.The cause for the reactor trip was determined to be a loose terminal lug on the CEA power switch assembly which developed a high resistance connection and led to the improper operation of the control element drive mechanism upper gripper coil. As an immediate corrective action, the terminal lug was replaced and retested satisfactorily. Troubleshooting of CEA 16 did not identify any problems. Unit 1 returned to service and entered Mode 1 at 2140 on August 10, 2011.No similar conditions have been reported by Palo Verde in the past three years.
528 | 5282016002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282016002R00.pdf | 2016-09-07 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | On September 7, 2016, at 2131, with Unit 1 in Mode 1 and 100 percent power, the reactor was manually tripped and reactor coolant pumps were secured due to a control malfunction which prevented closure of a pressurizer spray valve. This event initiated from an unsuccessful attempt to transfer a non-class 120VAC instrument power bus from its normal source to its emergency/alternate source. The transfer was attempted to facilitate an inspection of an electrical load center which was sprayed with water earlier in the day by a leaking sprinkler head following Fire Protection (FP) Department routine testing of a FP water line. <br /><br /> The cause of the spray valve malfunction was a failed pneumatic volume booster in the spray valve actuator system combined with a current to pressure converter (I/P) calibration offset which resulted from a voltage transient during the unsuccessful electrical transfer. These conditions caused the spray valve to stay approximately five percent open when it received a close demand from the spray valve controller. The I/P converter and pneumatic volume booster were replaced and the spray valve was returned to service. Additional corrective actions will adjust preventive maintenance frequency on the pneumatic volume boosters. <br /><br /> In the past three years, PVNGS has not reported a similar event to the NRC.
528 | 5282018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282018001R00.pdf | 2018-02-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 1 | P | CE | PO | 100 | At approximately 2153 Mountain Standard Time on February 15, 2018, an automatic reactor trip of PVNGS Unit 1 occurred when two of four Reactor Coolant Pumps (RCPs) lost power and the Reactor Protection System (RPS) generated trips on all four channels for low departure from nucleate boiling ratio and high local power density following a main turbine generator trip. The two RCPs lost power due to the fast bus transfer feature being blocked in support of planned maintenance activities on Start-up Transformer (SUT) AENANX02. This prevented the RCPs from receiving power from the SUT after receipt of a trip signal from the main turbine generator. <br /><br /> The preliminary root cause of the Unit 1 main turbine generator and reactor trip has been attributed to the susceptibility of the Unit 1 excitation and voltage regulation system (EX2100e) Exciter Auxiliary I/O Interface Board (EAUX) to electrical noise which led to an excitation trip of the Unit 1 main turbine generator. This condition was corrected on February 17, 12018, by replacing the Unit 1 EX2100e EAUX with an updated version that is less susceptible to electrical noise and thereby reduces the possibility of a spurious main turbine generator trip. The root cause is still considered preliminary as the event investigation is still in progress. Any significant changes identified will be reported in a supplement to this Licensee Event Report upon completion of the investigation.<br /><br /> No other RPS actuation signals or actuations of plant engineered safety features systems occurred and all control element assemblies fully inserted into the reactor core. PVNGS Unit 2 and Unit 3 were operating at 100 percent power at the time of the event and were not impacted by the Unit 1 reactor trip. <br /><br /> No previous similar events have been reported by PVNGS in the last 3 years.
529 | 5291987004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291987004R01.pdf | 1987-04-16 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | POWER LEVEL - 100%. AT 1346 MST ON APRIL 16, 1987, PALO VERDE UNIT 2 WAS OPERATING AT 100 PERCENT POWER WHEN A REACTOR TRIP AND TURBINE TRIP OCCURRED. THE TRIP WAS CAUSED BY HIGH LOCAL POWER DENSITY (LPD) TRIP SIGNALS GENERATED BY THE CORE PROTECTION CALCULATORS (CPC). PRIOR TO THE TRIP, CONTROL ROOM OPERATORS AND ELECTRICAL MAINTENANCE PERSONNEL WERE IN THE PROCESS OF LOCATING A GROUND ON THE 'B' TRAIN 120 VAC - CLASS 1E BUS DISTRIBUTION PANEL 2E-PNB-D26. WHEN DISTRIBUTION BREAKER D2603 WAS OPENED AND RESHUT AN ERRONEOUS HIGH LPD TRIP SIGNAL WAS GENERATED ON ALL FOUR (4) PLANT PROTECTION SYSTEM CHANNELS RESULTING IN A REACTOR TRIP. THE ROOT CAUSE OF THIS EVENT WAS THE PARTIAL INTERRUPTION AND RESTORATION OF POWER TO THE CONTROL ELEMENT ASSEMBLY CALCULATOR (CEAC) RESULTING IN AN ERRONEOUS HIGH PENALTY FACTOR TRANSMISSION TO ALL CPC'S. THIS ANOMALY WAS KNOWN HOWEVER, THE ANOMALY WAS CONSIDERED TO BE A MINOR OPERATIONAL CONCERN. THE PROCESS USED FOR DETERMINING THE LOCATION OF GROUNDS WAS SYSTEMATIC AND IN ACCORDANCE WITH APPROVED PLANT PROCEDURES HOWEVER, OPERATIONS PERSONNEL WERE NOT AWARE OF THE INFORMATION CONCERNING THE ANOMALY. AS CORRECTIVE ACTION, THE EFFECTS OF CYCLING EACH BREAKER ON THE CLASS 1E INSTRUMENT AC DISTRIBUTION PANELS WILL BE INCORPORATED, AS APPROPRIATE, INTO OPERATIONS GUIDELINES.
529 | 5291987010 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291987010R00.pdf | 1987-06-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 1259 MST ON JUNE 4, 1987, PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION) AT 100 PERCENT POWER WHEN THE AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM INITIATED A REACTOR TRIP DUE TO A LOW LEVEL CONDITION IN STEAM GENERATOR 2. IMMEDIATELY FOLLOWING THE REACTOR TRIP, AUXILIARY FEEDWATER ACTUATION SIGNALS 1 AND 2 WERE RECEIVED. AT 1300 A CONTAINMENT ISOLATION ACTUATION SIGNAL AND A SAFETY INJECTION ACTUATION SIGNAL WERE RECEIVED DUE TO A LOW PRESSURIZER PRESSURE CONDITION. ALL SAFETY SYSTEMS AND COMPONENTS OPERATED AS DESIGNED. THE STEAM GENERATOR AND REACTOR COOLANT SYSTEM (RCS) PARAMETERS STABILIZED AND ALL ENGINEERED SAFETY FEATURES ACTUATIONS WERE RESET BY 1353. THIS SUBMITTAL ALSO PROVIDES SPECIAL REPORT 2-SR-87-019 FOR AN EMERGENCY CORE COOLING SYSTEM ACTUATION AND THE INJECTION OF WATER INTO THE RCS. THE ROOT CAUSE OF THE REACTOR TRIP WAS THE MALFUNCTION OF THE MECHANICAL INTERLOCK ON THE DIGITAL VOLT METER DISPLAY SELECT PUSH-BUTTONS ON A FEEDWATER CONTROL SYSTEM (FWCS) TEST PANEL. A SLIGHT MISALIGNMENT OF AN INTERLOCK CONTROL BAR RESULTED IN THE NEUTRON FLUX AND DOWNCOMER FLOW SIGNALS BEING SHORTED TOGETHER WHEN THE DOWNCOMER FLOW PUSH-BUTTON WAS DEPRESSED AND THE NEUTRON FLUX PUSH-BUTTON DID NOT AUTOMATICALLY RESET AS DESIGNED. THIS CAUSED ERRATIC FWCS BEHAVIOR AND EVENTUALLY RESULTED IN THE REACTOR TRIP.
529 | 5291987008 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291987008R00.pdf | 1987-07-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palo Verde 2 | P | CE | PO | 56 | POWER LEVEL - 056%. AT APPROXIMATELY 1842 MST ON JULY 22, 1987, PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION) WHEN A PLANT SHUTDOWN WAS INITIATED DUE TO A SUSPECTED STEAM GENERATOR (SG) TUBE LEAK IN SG 2. AT APPROXIMATELY 1850 MST, THE PLANT WAS AT APPROXIMATELY 56 PERCENT POWER WHEN UTILITY LICENSED OPERATORS MANUALLY TRIPPED THE REACTOR AFTER BOTH MAIN FEEDWATER PUMPS TRIPPED ON LOW SUCTION PRESSURE. ALL SYSTEMS AND COMPONENTS OPERATED AS DESIGNED. THE CAUSE OF THE REACTOR TRIP WAS A MANUAL TRIP BY A UTILITY LICENSED OPERATOR DUE TO A LOSS OF MAIN FEEDWATER PUMPS. THE CAUSE OF THE LOSS OF MAIN FEEDWATER PUMPS WAS DUE TO A PERSONNEL ERROR BY THE LICENSED OPERATOR IN THAT HE PLACED THE CONDENSATE DEMINERALIZER BYPASS VALVE IN AUTOMATIC BEFORE CLOSING THE CONDENSATE DEMINERALIZER OUTLET VALVE. THIS CAUSED A REDUCTION IN CONDENSATE FLOW TO THE MAIN FEEDWATER PUMPS WHICH RESULTED IN THE LOSS OF BOTH MAIN FEEDWATER PUMPS AND THE INITIATION OF A MANUAL REACTOR TRIP. PLACING THE CONDENSATE DEMINERALIZER BYPASS VALVE INTO AUTOMATIC PRIOR TO CLOSING THE CONDENSATE DEMINERALIZER OUTLET VALVE IS CONTRARY TO AN APPROVED PROCEDURE. AS CORRECTIVE ACTION TO PREVENT RECURRENCE, A NIGHT ORDER WAS WRITTEN TO INSTRUCT OPERATORS TO LEAVE THE BYPASS VALVE IN MANUAL IN THE EVENT ALL CONDENSATE DEMINERALIZERS ARE REMOVED FROM SERVICE. NO SIMILAR EVENTS HAVE OCCURRED.
529 | 5291987019 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291987019R00.pdf | 1987-11-22 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 2 | P | CE | PO | 7 | POWER LEVEL - 007%. AT APPROXIMATELY 1940 ON NOVEMBER 22, 1987 PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 7% REACTOR POWER WHEN A REACTOR TRIP OCCURRED AS A RESULT OF THE CORE'S AXIAL SHAPE INDEX (ASI) BEING OUT OF BOUNDS. THE TRIP OCCURRED AS THE UNIT WAS BEING STARTED UP AFTER BEING SHUTDOWN FOR APPROXIMATELY 40 HOURS. THE REACTOR TRIP WAS UNCOMPLICATED AND THE PLANT WAS STABILIZED VERY QUICKLY TERMINATING THE EVENT. THE ROOT CAUSE OF THE TRIP WAS A DEFICIENT PROCEDURE. THE PROCEDURE DID NOT PROVIDE ADEQUATE GUIDANCE TO ENSURE THAT ASI WAS VERIFIED TO BE WITHIN BOUNDS PRIOR TO RAISING POWER ABOVE THE POINT THAT THE CORE PROTECTION CALCULATOR (CPC) (JC) SHIFTED FROM A DEFAULT VALUE TO A CALCULATED VALUE. TO PREVENT RECURRENCE, PROCEDURAL ENHANCEMENTS HAVE BEEN IMPLEMENTED. ADDITIONALLY, A FAULT CONTACT (CNTR) IN THE REACTOR PROTECTION SYSTEM (RPS) (JC) CONTRIBUTED TO THE EVENT IN THAT A REACTOR TRIP OCCURRED ON A ONE-OF-FOUR COINCIDENCE VICE THE DESIGNED TWO-OF-FOUR COINCIDENCE. THE FAULTY CONTACT WAS REPLACED AND A ROOT CAUSE OF FAILURE WAS INITIATED TO PROVIDE FURTHER ANALYSIS. THERE HAVE BEEN NO PREVIOUS SIMILAR EVENTS.
529 | 5291988014 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291988014R00.pdf | 1988-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 2 | P | CE | PO | 10 | POWER LEVEL - 010%. AT APPROXIMATELY 0237 MST ON NOVEMBER 16, 1988 PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 10 PERCENT POWER WHEN A REACTOR TRIP OCCURRED. UNIT 2 WAS BEING SHUT DOWN TO IDENTIFY AND REPAIR A REACTOR COOLANT SYSTEM (RCS) LEAK, WHICH WAS WITHIN TECHNICAL SPECIFICATION LIMITS FOR CONTINUED OPERATION, WHEN THE TRIP OCCURRED AS A RESULT OF LOW STEAM GENERATOR WATER LEVEL. THE REACTOR TRIP WAS UNCOMPLICATED AND STABLE CONDITIONS WERE ACHIEVED AT APPROXIMATELY 0247 MST TERMINATING THE EVENT. THERE WERE NO ENGINEERED SAFETY FEATURE ACTUATIONS AND NONE WERE NECESSARY. THE CAUSE OF THE LOW STEAM GENERATOR WATER LEVEL WAS INADEQUATE FEEDWATER FLOW DUE TO MAIN FEEDWATER PUMP SPEED BEING TOO SLOW FOR THE EXISTING PLANT CONDITIONS. THE CAUSE OF THE RCS LEAK WAS EXCESS PACKING LEAKAGE AS A RESULT OF A BROKEN PACKING GLAND FOLLOWER BOLT ON AN INSTRUMENT ISOLATION VALVE. AS CORRECTIVE ACTION TO PREVENT RECURRENCE, PROCEDURAL CHANGES HAVE BEEN IMPLEMENTED, AN EVALUATION OF THE FEEDWATER PUMP CONTROL SYSTEM IS BEING PERFORMED, AND PROGRAMS FOR IMPLEMENTATION OF PLANT MODIFICATIONS WILL BE EVALUATED AND REVISED WHERE APPROPRIATE. THERE HAVE BEEN NO PREVIOUS SIMILAR EVENTS.
529 | 5291989003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291989003R01.pdf | 1989-02-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 0345 MST ON FEBRUARY 16, 1989, PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 100 PERCENT POWER WHEN A FEEDWATER CONTROL SYSTEM (FWCS) MALFUNCTION RESULTED IN A REACTOR TRIP DUE TO LOW LEVEL IN STEAM GENERATOR (SG) NUMBER 1. IMMEDIATELY PRIOR TO THE TRIP THE CONTROL ROOM STAFF OBSERVED BOTH SG LEVELS DECREASING. BOTH MASTER CONTROLLER OUTPUTS WERE CYCLING FULL SCALE. SG NUMBER 2 ECONOMIZER VALVE WAS 10 PERCENT OPEN. A CONTROL ROOM OPERATOR PLACED SG NUMBER 1 ECONOMIZER VALVE IN MANUAL AND INSERTED APPROXIMATELY 17 PERCENT OPEN DEMAND WHEN THE REACTOR TRIPPED. IMMEDIATELY FOLLOWING THE TRIP AN AUXILIARY FEEDWATER ACTUATION SIGNAL WAS INITIATED. AT APPROXIMATELY 0345 MST A SAFETY INJECTION ACTUATION SIGNAL (SIAS)/CONTAINMENT ISOLATION ACTUATION SIGNAL (CIAS) WAS GENERATED DUE TO THE OVERCOOLING OF THE REACTOR COOLANT SYSTEM. SG NUMBER 1 LEVEL CONTINUED TO INCREASE AND AT APPROXIMATELY 0347 MST A MAIN STEAM ISOLATION SIGNAL WAS RECEIVED AND TERMINATED THE COOLDOWN. THE CAUSE OF THE EVENT WAS A SMALL AMOUNT OF DEBRIS IN THE RESTRICTOR ON THE VERTICAL RELAY WITHIN THE ECONOMIZER VALVE PNEUMATIC POSITIONER. IMMEDIATE CORRECTIVE ACTION TAKEN WAS TO REPLACE THE PNEUMATIC RELAYS IN BOTH FWCS'S. THIS SUBMITTAL ALSO PROVIDES SPECIAL REPORT 2-SR-89-003 IN ACCORDANCE WITH TECHNICAL SPECIFICATION 3.5.2 ACTION B.
529 | 5291989009 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291989009R01.pdf | 1989-07-12 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON JULY 12, 1989 AT APPROXIMATELY 2212 MST PALO VERDE UNIT 2 WAS OPERATING AT APPROXIMATELY 100 PERCENT POWER WHEN 2 OF THE 4 REACTOR COOLANT PUMPS WERE LOAD SHED FROM THEIR POWER SUPPLY (BUS 2E-NAN-S02), RESULTING IN A REACTOR TRIP ON CALCULATED LOW DNBR DUE TO LOW REACTOR COOLANT FLOW. IMMEDIATELY FOLLOWING THE TRIP, A SAFETY INJECTION ACTUATION SIGNAL (SIAS) AND CONTAINMENT ISOLATION ACTUATION SIGNAL (CIAS) ENGINEERED SAFETY FEATURES OCCURRED ON LOW REACTOR COOLANT SYSTEM (RCS) PRESSURE. FOLLOWING THE EVENT, AT APPROXIMATELY 1529 MST ON JULY 13, 1989, A PORTION OF THE MAIN FEEDWATER SYSTEM (MFWS) WAS OVERPRESSURIZED. THE CAUSE OF THE LOAD SHED WAS A FAILED FUSE IN THE BUS POTENTIAL TRANSFORMER. THE CAUSE OF THE SIAS/CIAS WAS RCS DEPRESSURIZATION DUE TO IMPROPER STEAM BYPASS CONTROL SYSTEM (SBCS) RESPONSE AND LEAKING PRESSURIZER SPRAY VALVES. THE CAUSE OF THE MFWS OVERPRESSURIZATION WAS A FAILED CHECK VALVE. IMMEDIATE CORRECTIVE ACTION TAKEN WAS TO REPLACE THE FUSE. THIS SUBMITTAL ALSO PROVIDES A SPECIAL REPORT IN ACCORDANCE WITH TECHNICAL SPECIFICATION 3.5.2 ACTION B.
529 | 5291989010 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291989010R00.pdf | 1989-10-31 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 67 | POWER LEVEL - 067%. AT APPROXIMATELY 1646 MST ON OCTOBER 31, 1989, PALO VERDE UNIT 2 WAS IN MODE 1 (POWER OPERATION), OPERATING AT APPROXIMATELY 67% POWER WHEN A REACTOR TRIP OCCURRED WHICH RESULTED FROM A LOW DEPARTURE FROM NUCLEATE BOILING RATIO (DNBR) TRIP SIGNAL. THE DNBR TRIP SIGNAL WAS CAUSED BY AN ERRONEOUS POWER LEVEL INPUT FROM THE MIDDLE EXCORE DETECTOR TO THE CHANNEL 'B' CORE PROTECTION CALCULATOR. THE TRIP WAS UNCOMPLICATED AND SECONDARY PLANT RESPONSES OCCURRED AND NONE WERE REQUIRED. AT APPROXIMATELY 1656 MST ON OCTOBER 31, 1989, THE PLANT WAS STABILIZED IN MODE 3 (HOT STANDBY) AT NORMAL TEMPERATURE AND PRESSURE. THE CAUSE OF THE ERRONEOUS MIDDLE EXCORE DETECTOR INPUT POWER LEVEL SIGNAL TO THE CHANNEL 'B' CORE PROTECTION CALCULATOR IS SUSPECTED TO BE AN INTERMITTENT MALFUNCTION OF THE CHANNEL 'B' EXCORE LINEAR CALIBRATE SWITCH. AS INTERIM CORRECTIVE ACTION, A TEMPORARY MODIFICATION HAS BEEN INSTALLED TO BYPASS THE NORMAL OPERATING FUNCTIONS OF THE LINEAR CALIBRATE SWITCH. AS CORRECTIVE ACTION TO PREVENT RECURRENCE, ENGINEERING IS DEVELOPING A PERMANENT SOLUTION. THERE HAVE BEEN NO PREVIOUS SIMILAR OCCURRENCES REPORTED PURSUANT TO 10CFR50.73.
529 | 5291990001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291990001R00.pdf | 1990-02-23 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 24 | At approximately 2301 MST on February 23, 1990, Palo Verde Unit 2 was in Mode 1 (Power Operation) at approximately 24 percent power during a planned shutdown for a refueling outage when the reactor was manually tripped by a reactor operator because the Axial Shape Index was approaching its trip setpoint on the Core Protection Calculator. The reactor trip was diagnosed as an uncomplicated reactor trip. No other safety system responses occurred and none were required. At approximately 2311 MST on February 23, 1990, the plant was stabilized in Mode 3 (Hot Standby) at normal temperature and pressure. <br /><br /> The cause of the manual reactor trip was that the Axial Shape Index was approaching its trip setpoint during an end of core life shutdown. The corrective action was to trip the reactor and ensure the Axial Shape Index remained within limits. <br /><br /> A previous similar event was reported in LER 528/87-018-01.
529 | 5291991003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291991003R00.pdf | 1991-08-09 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 40 | At approximately 0648 MST on August 9, 1991, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 40 percent power when the reactor was manually tripped due to Axial Shape Index (ASI) approaching its trip setpoint on the Core Protection Calculator. At the time of this event, the reactor was being shut down due to the loss of Control Element Drive Mechanism cooling fans. Following the trip, two of the four reactor coolant pumps (RCPs) did not transfer to their alternate source of power and stopped. The remaining two RCPs supplied adequate forced circulation. The reactor trip was diagnosed as an uncomplicated reactor trip. No safety system responses occurred and none were required. At approximately 0658 MST the plant was stabilized in Mode 3 (HOT STANDBY) at normal temperature and pressure.<br /><br /> The cause of the manual reactor trip was ASI approaching its trip setpoint during shutdown. The corrective action was to trip the reactor and ensure ASI remained within limits.<br /><br /> Previous similar events were reported in LER 528/87-018-01 and LER 529/90-001-00.
529 | 5291991004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291991004R01.pdf | 1991-08-16 | QR5 | Turbine Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On August 16, 1991, at approximately 0839 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 64 percent power when a reactor trip occurred due to high pressurizer pressure. Immediately prior to the reactor trip, the Main Generator tripped initiating a Main Turbine trip. At approximately 0900 MST on August 16, 1991, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The event was diagnosed as an uncomplicated reactor trip. No other safety system responses occurred and none were required.<br /><br /> The reactor trip on high pressurizer pressure has been determined to be the normal plant response to a load rejection at 64 percent power with 7 of the 8 steam bypass control valves (SBCVs) in service. The cause of the reactor trip was a generator/turbine trip in combination with a cognitive personnel error by the Control Room personnel who did not comply with procedural requirements to have the 8 SBCVs in service at power levels below 75 percent. Control Room personnel were disciplined in accordance with the PVNGS Positive Discipline Program. The Main Generator trip was caused when a Generrex A.C./D.C. gate board's static switch failed and the Generrex excitation control system entered an abnormal state (i.e., excessively high field voltage, current and VARS). The gate board was replaced and the Generrex System was successfully retested and returned to service. <br /><br /> A previous similar event was reported in Unit 1 LER 528/90-006.
529 | 5291992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291992001R01.pdf | 1992-01-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 2 | P | CE | PO | 17 | At approximately 1653 MST on January 9, 1992, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 17 percent power when an automatic reactor trip occurred due to low level in the number 1 steam generator because a feedwater supply valve did not open automatically as required. The reactor trip occurred during power ascension following a refueling outage. Following the reactor trip, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The reactor trip was diagnosed as an uncomplicated reactor trip in accordance with the emergency plan implementing procedures. Prior to the automatic reactor trip, Control Room personnel began reducing power, started the "B" motor driven Auxiliary Feedwater pump and established auxiliary feedwater flow to the number 1 steam generator. No other safety system responses occurred and none were required. <br /><br /> The cause of the feedwater supply valve not opening was fatigue failure of wires connected to a switch assembly on the auto/manual controller for the valve. The fatigue failure of the wires prevented the feedwater supply valve from receiving an open signal from the main feedwater control system. The root cause of failure of the auto/manual controller switch assembly was fatigue failure. Contributing to this failure was that the controllers were manufactured from relatively brittle Norel plastic. As immediate corrective action the faulty controller was replaced. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
529 | 5291992002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291992002R01.pdf | 1992-03-23 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | At approximately 0953 MST on March 23, 1992, Palo Verde Units 2 and 3 were in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a reactor trip and Train A Loss of Power (LOP) Engineered Safety Feature Actuation System (ESFAS) actuation occurred in Unit 2, and a Train B LOP ESFAS occurred in Unit 3. A fault on a startup transformer disconnect switch occurred during the performance of preventive maintenance to exercise supply breakers to the Unit 2 Train A non-Class 1E 13.8 kV Switchgear Bus, resulting in a loss of offsite power to two of four reactor coolant pumps (RCP) in Unit 2 and subsequent reactor trip. This also resulted in a loss of power to the Unit 2 Train A and Unit 3 Train B Class 1E 4.16 kV buses, and LOP ESFAS actuations. The Unit 2 Train A Emergency Diesel Generator (EDG) and the Unit 3 Train B EDG started and loaded per design. All equipment functioned as designed. There were no other ESFAS actuations and none were required. Unit 3 continued to operate normally at 100 percent power throughout the event. <br /><br /> The event in Unit 2 was diagnosed as an uncomplicated reactor trip. At approximately 1020 MST on March 23, 1992, Unit 2 was stabilized in Mode 3 (HOT STANDBY) at normal temperature and pressure. <br /><br /> As corrective action, the three disconnect pole assembles on the disconnect switch were replaced.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
529 | 5291992006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291992006R00.pdf | 1992-11-13 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On November 13, 1992, at approximately 1354 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power, when the inadvertent deenergization of the Control Element Drive Mechanism (CEDM) Motor Generator (MG) Set 'B' caused a reactor trip. The Control Element Assemblies (CEAs) inserted into the reactor core, causing a Main Turbine trip and the quick opening and modulation of the Steam Bypass Control System (SBCS) valves. This resulted in a change in steam flow causing primary system pressure to decrease below the low pressurizer pressure Engineered Safety Feature System actuation setpoint of 1837 psia. A valid actuation of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure.<br /><br /> This event was investigated in accordance with the APS Incident Investigation Program. The root cause of the reactor trip was determined to be the inappropriate actuation of the CEDM MG Set 'B' remote motor stop button by an auxiliary operator (AO). The root cause of the SIAS and CIAS was the over-cooling of the reactor coolant system caused by a loss of post-trip to SIAS operating margin for the SBCS. Pursuant to Technical Specification 3.5.2, ACTION b, this LER also provides the Special Report required for a Emergency Core Cooling System actuation. <br /><br /> There have been no previous similar events where the inappropriate actuation of a CEDM MG set caused a reactor trip reported pursuant to 10CFR50.73.
529 | 5291993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291993001R02.pdf | 1993-03-14 | F1 | Steam Generator Tube Rupture PWR (SGTR) | [5 empty] | X | [18 empty] | X | [20 empty] | Palo Verde 2 | P | CE | PO | 98 | On March 14, 1993, at approximately 0434 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 98 percent power when a steam generator tube ruptured in Steam Generator 2. At approximately 0447 MST, the reactor was manually tripped due to low pressurizer level and pressure. Approximately 22 seconds later, valid actuations of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure. Pressurizer level was restored and a controlled cooldown and depressurization of the Reactor Coolant System (RCS) was conducted in accordance with approved procedures. A steam generator tube rupture in Steam Generator 2 was diagnosed, and the steam generator was successfully isolated. <br /><br /> This event was investigated in accordance with the PVNGS Incident Investigation Program. The rupture of the steam generator tube was due to intergranular attack/intergranular stress corrosion cracking (IGA/IGSCC) which occurred as a result of tube-to-tube crevice formation. The cause of the SIAS and CIAS was the loss of RCS inventory and the contraction of the RCS upon reactor trip. Pursuant to Technical Specifications 3.5.2, ACTION b, this LER also provides the Special Report required for an Emergency Core Cooling System actuation. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
529 | 5291993004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291993004R00.pdf | 1993-11-01 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Palo Verde 2 | P | CE | PO | 85 | On November 1, 1993, at approximately 0807 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at a approximately 85 percent steady-state power, when a reactor power cutback to approximately 45 percent power occurred following the loss of a main feedwater pump (MFWP), and at approximately 0808 MST, a reactor trip occurred on low steam generator water level. The reactor trip was initiated by a non-Class 1E 4.16 kV switchgear bus load shed which caused the loss of two condensate pumps and a heater drain pump. Both MFWPs tripped on low suction pressure. Immediately following the reactor trip, the SG-2 water level reached the RPS trip setpoint for low steam generator water level, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS-1 and AFAS-2) on low-low steam generator water level for both steam generators. Per design, the AFAS signals automatically started the Train A and Train B Emergency Diesel Generators. The steam generator water levels were restored using auxiliary feedwater. By approximately 0830 MST on November 1, 1993, the plant was stabilized in Mode 3 (HOT STANDBY) and the event was diagnosed as an uncomplicated reactor trip. No other safety system responses occurred and none were required. All plant equipment responded as designed. <br /><br /> The NBN-S01 load shed was caused by an insufficient electrical contact in a potential transformer (PT). The PT was adjusted and returned to service.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
529 | 5291994002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291994002R00.pdf | 1994-05-28 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 2 | P | CE | PO | 86 | On May 28, 1994, at approximately 1115 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) operating at approximately 86 percent power when the Unit sustained a reactor trip. The trip was due to a low Departure from Nucleate Boiling Ratio signal which was a result of Reactor Coolant Pump (RCP) 1B tripping on a phase-to-phase electrical fault. The plant responded normally to the event. No safety functions were challenged and no Engineered Safety Features Actuation System actuations were received or required. The Control Room Supervisor classified the event as an uncomplicated reactor trip at 1130 MST and the Unit was stabilized in Mode 3 (HOT STANDBY). Management has conducted briefings with Operation and Maintenance personnel regarding the circumstances of the event. The 1B RCP supply cables and the penetration termination box have been repaired. At approximately 1515 MST on June 2, 1994, the Plant Review Board reviewed the status of the recovery/restart plan and approved entry into Mode 2 (STARTUP). Unit 2 returned to 86 percent power at approximately 1235 MST on June 5, 1994. An investigation of the event is continuing. <br /><br /> There have been two previous similar events (LER 528/88-011 and 529/92-006) reported pursuant to 10CFR50.73.
529 | 5291994006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291994006R00.pdf | 1994-10-29 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On October 29, 1994, at approximately 2044 MST, Palo Verde Unit 2 was in MODE 1 (POWER OPERATION), operating at approximately 100 percent power when the reactor tripped on a low Departure from Nucleate Boiling Ratio (DNBR) trip signal. The trip signal was initiated from the Core Protection Calculators (CPC) after processing an erroneous DNBR penalty factor generated by Control Element Assembly Calculator (CEAC) #1. Required plant equipment and safety systems responded to the event as designed. and none were required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 2115 MST on October 29, 1994, the plant was stabilized in MODE 3 (HOT STANDBY). <br /><br /> The reactor trip was caused by an apparent malfunction in a processor board located in CEAC #1. As corrective action, the processor board was quarantined and replaced. An Equipment Root Cause Failure Analysis (ERCFA) was initiated on the processor board. <br /><br /> A previous similar event was reported in LER 528/89-004.
529 | 5291995005 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291995005R00.pdf | 1995-07-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On July 17, 1995, at approximately 2331 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. Immediately following the reactor trip an Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS) was received on SG-1 and SG-2 low levels. The loss of FW flow was the result of a momentary power loss (from NNN-D11) to the FW control system (FWCS) during a switching operation of the non-Class 1E 13.8 kV (NAN-S05) switchgear from the normal power supply (startup transformer X01) to the alternate power supply (startup transformer X02) in order to take startup transformer X01 out of service for maintenance. <br /><br /> When the switching operation was carried out, the breaker indications for startup transformers X01 and X02 did not change. Plant multiplexer (PMUX) indication problems led the operating crew to believe that the switching operation did not occur. Concerned about an inadvertent breaker closure, the operating crew reset the alternate supply breaker X02. This resulted in the deenergization of NAN-S05, NAN-S03, and the class 1E 4.16 kV bus (PBA-S03). <br /><br /> The root cause for the Unit 2 reactor trip was determined to be a failure of the initial design to consider FWCS responses to momentary power interruptions. An evaluation of the adequacy of NNN-D11 to support the FWCS and steam bypass control system (SBCS) is ongoing. Any corrective actions identified will be tracked under the APS Commitment Action Tracking System. <br /><br /> Previous similar events were reported pursuant to 10 CFR 50.73 in LERs 528/95-008, 530/94-007, 530/94-005, 530/93-001 and 529/92-001.
529 | 5291996001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291996001R00.pdf | 1996-01-21 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Palo Verde 2 | P | CE | PO | 100 | On January 21, 1996, at approximately 1130 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 1 (SG-1) water level reached the Reactor Protection System trip setpoint for low SG water level following the degradation of main feedwater (FW) flow. Immediately following the reactor trip an Engineered Safety Feature Actuation System (ESFAS) actuation of the Auxiliary Feedwater Actuation System (AFAS) was received on SG-1 and SG-2 due to low SG water levels. The loss of FW flow was due to the improper filling and venting of the 'C' condensate pump being restored to service after maintenance. When the condensate pump suction valve was partially opened, to allow filling of the suction piping, the two running condensate pumps became air bound. This resulted in the main FW pumps tripping on low suction pressure and the reactor tripping on SG low water level. As corrective action, filling and venting of condensate pumps has been proceduralized. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
529 | 5291997006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291997006R00.pdf | 1997-10-20 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On October 20, 1997, at approximately 1050 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel initiated a manual reactor trip following vibration and bearing temperature increases in reactor coolant pump (RCP) 2B. No other safety system actuations occurred and none were required. At approximately 1051 MST, Control Room personnel secured and quarantined RCP 2B. The event was classified as an uncomplicated reactor trip.An engineering evaluation determined that the apparent root cause is attributed to a failed lower journal bearing. The most probable cause of the bearing failure was intrusion of debris. The source and composition of the debris is unknown. As corrective action, the bearing assembly was disassembled, inspected, and rebuilt. A metallurgical examination of the bearing pads, shaft protection sleeve, and debris collected from the bearing assembly is currently ongoing.No previous similar events have been reported pursuant to 10CFR50.73.
529 | 5291999005 | https://lersearch.inl.gov/PDFView.ashx?DOC::5291999005R00.pdf | 1999-06-18 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On June 18, 1999, at approximately 2229 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low Departure from Nucleate Boiling Ratio (DNBR). The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to CPC sensor failures. By approximately 2245 MST, the reactor was stabilized in Mode 3 (HOT STANDBY). The Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required. Required safety systems, including Steam Bypass Control, responded to the event as designed.Although additional investigative activities remain to be completed, the cause of the reactor trip appears to be a hardware induced calculation error that resulted in an erroneous penalty factor being generated in control element assembly calculator (CEAC) #2.A previous similar event was reported in LER 50-529/94-006-00.
529 | 5292000001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292000001R00.pdf | 2000-08-26 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Palo Verde 2 | P | CE | PO | 100 | On August 26, 2000, at approximately 1539 Mountain Standard Time, Unit 2 was in Mode 1 (POWER OPERATION), when a loss of power to an "A" train logic control cabinet occurred causing all four main steam isolation valves (MSIVs) and the "A" train feedwater isolation valves (FWIVs) to close. An automatic reactor trip was initiated and the primary plant was stabilized in Mode 3 (HOT STANDBY) in forced circulation with both steam generators used for heat removal via the atmospheric dump valves. Subsequent to the reactor trip, one of the two 13.8 kV electrical distribution buses failed to complete a fast bus transfer which resulted in a loss of power to two of the four reactor coolant pumps. Operations personnel successfully cross-connected the electrical loads normally supplied by this bus to an available power source. In addition, reactor coolant system activity was monitored and acceptable operational limits were not exceeded. The event did not adversely affect the safe operation of the plant or the health and safety of the public. In the past three years there have been no similar events reported where a failed power supply caused the closure of MSIVs.
529 | 5292000007 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292000007R00.pdf | 2000-11-18 | QR5 | Turbine Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On November 18, 2000 at 1147 Mountain Standard Time (MST), Unit 2 was in MODE 1 (Power Operation), at approximately 45 percent rated thermal power when a reactor protection system actuation tripped the plant. Prior to the reactor trip, at approximately 1058 MST, Unit 2 had experienced a generator/turbine trip followed by a reactor power cutback.The turbine trip was the result of failed on-line maximum excitation limit and field current regulator circuit boards. The cause of the reactor trip was licensed operator cognitive error.There have been no previous similar events reported in the last three years.
529 | 5292001002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292001002R00.pdf | 2001-07-13 | QL5 | Partial Closure of MSIVs | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On July 13, 2001, at approximately 0821 Mountain Standard Time, Unit 2 was in Mode 1 (POWER OPERATION), when a logic board and pin connector in the "B" Train Main Steam and Feedwater Isolation System failed causing three of four main steam isolation valves (MSIVS) to close. The reactor tripped from 100% power on Reactor Protective System Low Departure from Nucleate Boiling Ratio (DNBR). This DNBR trip was due to an auxiliary trip generated by all four Core Protection Calculator channels. The auxiliary trip was the asymmetric steam generator transient trip function based on cold leg temperature differences between the two steam generators. All Control Element Assemblies fully inserted. Two SG #2 Main Steam Safety Valves lifted as expected due to the MSIVs fast-closing.The primary plant was stabilized in Mode 3 (HOT STANDBY) with forced circulation with both steam generators being used for heat removal via the atmospheric dump valves. The event did not adversely affect the health and safety of the public.In the past three years there have been no similar events reported where a failed logic board in the Main Steam and Feedwater Isolation System logic cabinet caused the closure of MSIVs and a subsequent reactor trip.
529 | 5292003001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292003001R01.pdf | 2003-07-29 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Palo Verde 2 | P | CE | PO | 98 | On July 29, 2003, at 1500 Mountain Standard Time (MST), Unit 2 was at approximately 98% power when pressurizer main spray valve RCE-100F failed in the full open position. Attempts to close the valve per the alarm response procedure were unsuccessful. At 1515 MST, control room personnel manually tripped the reactor. In accordance with the applicable alarm response procedure, control room personnel secured the reactor coolant pumps (RCPs) to stop the reactor coolant system (RCS) depressurization. Control element assemblies fully inserted into the reactor core. Safety related buses remained energized during and following the reactor trip. Automatic safety injection and containment isolation actuation system (SIAS/CIAS) actuations occurred following the reactor trip, as RCS pressure continued to lower to the reactor protection system setpoint. The RCS was cooled on natural circulation with secondary heat removal via the main condenser. By 1616 MST, a containment entry was made and RCE-100F was manually isolated. At 1715 MST, RCP 1A was restarted restoring forced circulation to the reactor core. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event.There were no previous events that involved the same underlying cause within the last three years.
529 | 5282004006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282004006R01.pdf | 2004-06-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Palo Verde 2 | P | CE | PO | 100 | On June 14, 2004, at approximately 07:41 MST, a ground-fault occurred on the Western Area Power Authority 230kV Liberty substation to Westwing substation line (approximately 47 miles from the Palo Verde Nuclear Generating Station). A failure in the protective relaying resulted in the ground-fault not isolating from the local grid for approximately 38 seconds. The fault cascaded into the protective tripping of a number of 230kV and 525kV transmission lines, which ultimately led to the Loss of Offsite Power (LOOP) at the Palo Verde switchyard. In Unit 1 and 2, the LOOP caused each reactor to trip from 100 percent power on a Core Protection Calculator generated reactor trip on low Departure from Nucleate Boiling Ratio due to low Reactor Coolant Pump (RCP) shaft speed. Unit 3 tripped last and experienced a Variable Over Power Trip from approximately 109 percent power due to increased flow from the RCPs caused by an increase in voltage and frequency from the main turbine generator.The LOOP placed each Unit in a condition for "Notice of Unusual Event" (NUE). The Unit 2 Train "A"emergency diesel generator started, but failed to maintain electrical output during load sequencing and resulted in the declaration of an "Alert" in Unit 2 at 07:54 MST. The NUE for Units 1 & 3 was declared at 07:58 MST.No similar condition has been reported in the past three years.
529 | 5292004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292004002R00.pdf | 2004-07-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On July 14, 2004 at approximately 0134 Mountain Standard Time (MST) Unit 2 was operating at100 percent power, Mode 1 (Power Operations), when the Unit experienced a reactor power cutback followed by an automatic reactor trip. At the time of the event, Palo Verde was in a severe thunderstorm in which several lightning strikes had landed in the vicinity of the Palo Verde switchyard. Approximately five seconds after the series of lightning strikes, the main generator tripped which in turn initiated a reactor power cutback. Approximately 11 seconds after the reactor power cutback, a low departure from nucleate boiling ratio (DNBR) reactor trip was initiated by the core protection calculators (CPCs) in response to a conservative calculation of update DNBR for plant conditions.The main generator tripped on a loss of generator field signal which was induced by the effects of the multiple lightning strikes in the vicinity of the Palo Verde switchyard. The cause of the reactor trip is attributed to overly conservative addressable constants for planar radial peaking factor in the CPCs which are used to calculate update DNBR.A similar reactor trip occurred in Unit 3 on June 7, 2004 (LER 50-530/2004-002)
529 | 5292006003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292006003R01.pdf | 2006-07-26 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Palo Verde 2 | P | CE | PO | 90 | On July 26, 2006, at 07:33 Mountain Standard Time (MST), Unit 2 was in Operating Mode 1, Power Operation, at approximately 90 percent rated thermal power with main turbine control valve #2 (CV#2) closed to complete maintenance on its position transducer and linkage arm. A jumper installed in the test button circuit kept CV#2 closed during the maintenance. After removal of the jumper and CV#2 from "test", the valve was allowed to re-open resulting in a series of control system responses causing reactor power to increase rapidly. The reactor tripped on core protection calculator high variable overpower at approximately 90 percent power, approximately 18 seconds after removing CV#2 from "test". No other safety system actuations occurred and none were required. The root cause of the event was an inadequate assessment of the risk associated with performing the valve maintenance on-line, resulting in implementation of an inadequate action plan for corrective maintenance which did not accommodate for the build up of condensate in the isolated main turbine piping associated with CV#2. This occurred due to a belief that the maintenance evolution was equivalent to control valve testing. All monthly CV testing in Unit 2 was suspended until the root cause of the plant transient was determined. A standing order was issued to prohibit performance of CV maintenance on-line, and remained in effect until adequate procedural guidance was provided for removal of a CV from service for on-line maintenance. A similar trip event caused by a main turbine upset occurred on June 7, 2004, in Unit 3, when a main turbine electro-hydraulic system malfunction caused main turbine control and intercept valves to close, resulting in a reactor trip.
529 | 5292007003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292007003R00.pdf | 2007-10-06 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On October 6, 2007, at approximately 10:39 MST, Chemistry personnel notified Operations personnel in the Unit 2 control room that main condenser sodium levels were increasing. At approximately 10:59 MST, Chemistry personnel determined and reported that steam generator (SG) sodium levels had increased to above 1 ppm, which is the reactor trip criterion specified by procedure. Unit 2 was manually tripped at 10:59 MST from 100 % power and Operations personnel implemented standard post trip actions. The NRC Resident Inspectors were notified of the reactor trip and the NRC Headquarters was notified via the ENS at 12:32 MST (ENS #43687). The direct cause of this event was sodium ingress into the Unit 2 condenser hotwell and steam generators due to a corroded and failed tube plug in the "D" condenser air removal (AR) system seal water cooler. The root cause of the event was an error in the tube plug selection process made in January of 2001 resulting from an inadequate assessment of the tube plug material by engineering personnel.To prevent recurrence, the Unit 2 Condenser AR "D" cooler and tubes were cleaned and the tube plugs were replaced. PVNGS Maintenance Engineering personnel will determine an alternate tube plug type for the condenser AR system seal water coolers which will not be subject to corrosion or galvanic interaction with the titanium tube sheets and tubes. The existing AR system seal water cooler plugs will be replaced with the alternate plug.One LER has been reported in the past 4 years identifying a manually initiated reactor trip resulting from secondary system contaminant ingress due to a different cause.
529 | 5292013002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292013002R00.pdf | 2013-12-02 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On December 2, 2013, Unit 2 was operating in Mode 1 at 100 percent power. At approximately 1758 Mountain Standard Time a reactor trip was automatically actuated when reactor coolant pump (RCP) 1A speed dropped below 95 percent of rated speed which generated low departure from nucleate boiling ratio and high local power density trips on all four channels of the plant protection system. The reactor trip was determined to be uncomplicated and the reactor trip procedure was implemented to stabilize the plant in Mode 3. Operations personnel subsequently determined the RCP 1A motor circuit breaker tripped on excessive phase differential current. <br /><br /> The probable cause of the RCP 1A motor circuit breaker trip was a high impedance fault within the C phase of the motor stator coil. The faulted RCP 1A motor was replaced with an on-site spare RCP motor and Unit 2 was returned to power operation on December 14, 2013. The faulted motor has been sent to an off-site facility for disassembly and root cause analysis. <br /><br /> No previous similar events involving an automatic RPS actuation due to a RCP motor failure have been reported to the NRC by PVNGS in the prior three years.
529 | 5292018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5292018001R00.pdf | 2018-05-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 2 | P | CE | PO | 100 | On May 23, 2018, at approximately 1128 Mountain Standard Time, the PVNGS Unit 2 control room received a reactor protection system alarm for low departure from nucleate boiling ratio and an automatic reactor trip occurred as a result of a dropped control element assembly (CEA). The trip occurred coincident with maintenance on control element drive mechanism control system (CEDMCS) fuses and fuse caps. <br /><br /> The cause of the dropped CEA and resulting Unit 2 trip was a CEDMCS lower logic assembly misalignment that caused difficulty seating circuit cards. Maintenance activities adversely affected card edge connections of the circuit card that led to a dropped control element assembly. Corrective actions restored the subgroups 15 and 16 circuit cards to a fully seated position. <br /><br /> No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Units 1 and 3 were not impacted. <br /><br /> No similar conditions have been reported by PVNGS in the past three years.
530 | 5301987004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301987004R00.pdf | 1987-12-17 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 3 | P | CE | PO | 50 | POWER LEVEL - 050%. AT APPROXIMATELY 0430 MST ON DECEMBER 17, 1987, PALO VERDE UNIT 3 WAS IN MODE 1 (POWER OPERATION) AT APPROXIMATELY 50% POWER WHEN A REACTOR (RX) TRIP OCCURRED AS A RESULT OF A DEVIATION IN POSITION OCCURRING BETWEEN PART LENGTH CONTROL ELEMENT ASSEMBLY (AA) SUBGROUPS. THE TRIP OCCURRED AS THE REACTOR WAS AT THE 50% TEST PLATEAU DURING POWER ASCENSION TESTING. THE REACTOR TRIP WAS UNCOMPLICATED AND THE PLANT WAS STABILIZED WITHIN 30 MINUTES TERMINATING THE EVENT. THERE WERE NO ENGINEERED SAFETY FEATURES (JE) ACTUATIONS. THE ROOT CAUSE OF THE TRIP WAS A MALFUNCTIONING LOGIC SEQUENCER CARD (ZC) IN THE CONTROL ELEMENT DRIVE MECHANISM CONTROL SYSTEM (CEDMCS)(AA). AS CORRECTIVE ACTION, THE CARD WAS REPLACED AND THE CEDMCS WAS VERIFIED TO BE OPERATING PROPERLY. ADDITIONAL PREVENTIVE CORRECTIVE ACTIONS ARE BEING IMPLEMENTED AS DISCUSSED IN THE TEXT OF THIS REPORT. FOLLOWING THE TRIP, A RELAY/CONTACT (94/CNTR) ASSEMBLY DID NOT OPERATE PROPERLY WHICH RESULTED IN THE CLASS 1E PRESSURIZER (PZR) HEATERS (EHTR) CONTINUING TO REMAIN ENERGIZED BELOW THE LOW LEVEL TRIP SETPOINT. AS CORRECTIVE ACTION, THE RELAY/CONTACT ASSEMBLY WAS REPLACED AND THE HEATERS WERE VERIFIED TO BE OPERATING PROPERLY. NO SIMILAR REACTOR TRIPS HAVE OCCURRED.
530 | 5301989001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301989001R03.pdf | 1989-03-03 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Palo Verde 3 | P | CE | PO | 98 | POWER LEVEL - 098%. ON MARCH 3, 1989 AT APPROXIMATELY 0102 MST PALO VERDE UNIT 3 WAS OPERATING AT APPROXIMATELY 98 PERCENT POWER WHEN AN ELECTRICAL GRID DISTURBANCE RESULTED IN THE MAIN GENERATOR OUTPUT BREAKERS OPENING. THIS RESULTED IN A REACTOR POWER CUTBACK (RPCB) AND STEAM BYPASS CONTROL SYSTEM (SBCS) ACTUATION. AN SBCS MALFUNCTION RESULTED IN A STEAM GENERATOR (S/G) NUMBER 2 LOW PRESSURE REACTOR TRIP, TURBINE TRIP, MAIN STEAM ISOLATION SIGNAL, AND CONTAINMENT ISOLATION ACTUATION SIGNAL AT APPROXIMATELY 0103 MST. APPROXIMATELY SIX SECONDS LATER, A SAFETY INJECTION ACTUATION SIGNAL OCCURRED AS A RESULT OF LOW PRESSURIZER PRESSURE. CONTROL ROOM PERSONNEL ATTEMPTED TO REMOVE DECAY HEAT AND CONTROL S/G PRESSURE UTILIZING THE ATMOSPHERIC DUMP VALVES (ADV'S). CONTROL ROOM PERSONNEL COULD NOT REMOTELY OPERATE THE ADV'S FROM THE CONTROL ROOM OR REMOTE SHUTDOWN PANEL. HEAT REMOVAL WAS SUBSEQUENTLY ESTABLISHED BY MANUALLY OPENING THE ADV'S. IN THE INTERIM, ONE MAIN STEAM SAFETY VALVE CYCLED TO REMOVE DECAY HEAT AND CONTROL S/G PRESSURE. THE CAUSE OF THE REACTOR TRIP WAS A MALFUNCTION IN THE SBCS. AN INDEPENDENT INVESTIGATION HAS BEEN CONDUCTED TO DETERMINE THE CAUSES OF THE PROBLEMS OCCURRING DURING THE EVENT. BASED UPON THE INVESTIGATION, APPROPRIATE CORRECTIVE MEASURES HAVE BEEN DEVELOPED. THIS SUBMITTAL ALSO PROVIDES A SPECIAL REPORT IN ACCORDANCE WITH TECH SPEC 3.5.2 ACTION B.
530 | 5301990004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301990004R00.pdf | 1990-04-14 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 3 | P | CE | PO | 81 | On April 14, 1990, at approximately 0358 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 81 percent power when a reactor trip occurred which resulted from a dropped shutdown group control element assembly (CEA). No other safety system responses occurred and none were required. The event was diagnosed as an uncomplicated reactor trip. At approximately 0413 MST on April 14, 1990, the plant was stabilized in Mode 3 (HOT STANDBY) at normal temperature and pressure.<br /><br /> The cause of the CEA dropping into the core was an optical isolator card malfunction. The malfunction was determined to be a random failure of a microchip on the card. As corrective action, the optical isolator card was replaced and successfully retested.<br /><br /> A similar event was reported in Unit 1 LER 528/85-088.
530 | 5301990007 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301990007R00.pdf | 1990-10-20 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On October 20, 1990, at approximately 1230 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a reactor trip occurred. A false steam header pressure signal caused the in-service (i.e. 7 of 8 valves) steam bypass control valves (SBCVs) to open causing an excess steam demand and the subsequent reactor trip. The resulting reactor power transient was terminated by the Core Protection Calculator (CPC). No other safety system responses occurred and none were required. The event was diagnosed as an uncomplicated reactor trip. At approximately 1245 MST on October 20, 1990, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. Subsequently, on October 22, 1990, APS Engineering determined that Unit 3 was in an unanalyzed condition that was outside its design basis. The Updated Final Safety Analysis Report Chapter 15 "Accident Analysis" assumed that only one SBCV would open due to a failure of the control system. <br /><br /> The false pressure signal which caused the SBCVs to open was determined to be a result of a power distribution module failure in a Balance of Plant analog instrument cabinet. The root cause of the power distribution module failure was determined to be a fault diode. The module has been replaced. The failure of the diode was a random, low frequency component failure. <br /><br /> Similar events were reported in Unit 1 LERs 86-006 and LER 86-053, and Unit 3 LER 89-001.
530 | 5301991003 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301991003R01.pdf | 1991-06-19 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On June 19, 1991, at approximately 1002 MST, a Spurious Containment Spray System actuation occurred during the performance of the monthly Engineered Safety Features Actuation System (ESFAS) surveillance testing of the Plant Protection System (PPS). Control Room personnel determined that the Containment Spray System actuation was not the result of a valid condition (i.e., high containment pressure) and terminated the containment spray flow. Control Room personnel manually tripped the reactor at approximately 1004 MST and stopped the four reactor coolant pumps at approximately 1007 MST, in accordance with an approved procedure. At approximately 1022 MST, on June 19, 1991, natural circulation cooling was verified and the plant was stabilized in Mode 3 (HOT STANDBY). No other safety system responses occurred and none were required.<br /><br /> The spurious Containment Spray System actuation was the result of the incorrect assembly of a logic matrix relay hold pushbutton test switch in the test circuitry located in the PPS cabinet. The pushbutton test switch was replaced. The other logic matrix relay hold pushbutton test switches in Units 1, 2 and 3 were inspected and found to be assembled correctly. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
530 | 5281991010 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281991010R00.pdf | 1991-10-27 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On October 27, 1991, at approximately 0722 MST, Palo Verde Units 1 and 3 were operating at approximately 100 percent power when a grid perturbation caused the Main Turbine Control System to fast close and immediately reopen the turbine control valves (TVCs). The momentary reduction in steam flow caused the steam bypass control valves in Units 1 and 3 to quick open. A reactor power cutback occurred in Unit 3, but not in Unit 1. Reactor trips in Units 1 and 3 occurred when reactor power exceeded the Core Protection Calculator Variable Overpower Trip setpoints. Immediately following the trips, Safety Injection Actuation System (SIAS) and Containment Isolation Actuation System (CIAS) Engineered Safety Feature Actuation System actuations occurred on low pressurizer pressure. All safety system components actuated as designed in each unit. By approximately 0805 MST on October 27, 1991, the plants were stabilized in Mode 3 (HOT STANDBY). <br /><br /> The cause of the event was determined to be the expected plant response to a unique combination of circumstances. The event was precipitated by a grid fault resulting from a lightning strike on a substation feeder line. The fault which occurred was different from previous grid disturbance events (i.e., fault without ground). The generator output current at Palo Verde decreased triggering a momentary Power/Load Unbalance turbine protection actuation. This submittal also provides a Special Report in accordance with Technical Specification 3.5.2 ACTION b.
530 | 5301991008 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301991008R00.pdf | 1991-11-14 | QR5 | Turbine Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | At approximately 1449 MST on November 14, 1991, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a lightning induced electrical fault on the A phase main transformer caused a generator trip, turbine trip, and reactor power cutback (RPCB). Approximately 35 seconds following these events, the reactor tripped on low Departure from Nucleate Boiling Ratio (DNBR) signals. The plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The Control Room shift supervisor classified the event as an uncomplicated reactor trip in accordance with the emergency plan implementing procedure. No other safety system responses occurred and none were required. The post trip review found that the low DNBR reactor trip was due to a control element assembly (CEA) subgroup deviation. During the post trip investigation, APS engineering discovered that a problem with the control element assembly calculator (CEAC) software design may have delayed the reactor trip for up to 16 seconds when a second CPC time delay was initiated. At the time of the second time delay, one CEA subgroup was thought to be misaligned greater than the allowed limit in the CPCs. <br /><br /> The cause of the second time delay was that the CEAC software design did not anticipate that there would be CEA slips lasting less than 0.5 seconds. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
530 | 5301992001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301992001R00.pdf | 1992-01-24 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Palo Verde 3 | P | CE | PO | 100 | On January 24, 1992, at approximately 1750 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a reactor trip occurred following a reactor power cutback which was initiated when Control Room personnel manually tripped the main feedwater pump "B" (MFWP). The MFWP "B" was tripped in an attempt to stabilize the suction pressure for the MFWP "A" following the receipt of MFWP low suction pressure trip alarms for both operating MFWPs. Following the reactor trip, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. At approximately 1816 MST, the event was classified as an uncomplicated reactor trip. All plant equipment responded as expected. No engineered safety feature actuation system actuations occurred and none were required. <br /><br /> The MFWP low suction pressure occurred when the MFWP mini-flow recirculation valves failed open on loss of instrument air pressure. As corrective action, the instrument air line was repaired. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
530 | 5301993001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301993001R00.pdf | 1993-02-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On February 4, 1993, at approximately 1523 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred due to Steam Generator Number 2 (SG-2) water level reaching the Reactor Protection System trip setpoint for low steam generator water level following the loss of Main Feedwater Pump A. Immediately following the reactor trip, a low steam generator water level alarm annunciated for SG-1, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS-1 and AFAS-2) on low-low steam generator water level for both steam generators. The Steam Bypass Control System responded as designed to control the secondary system pressure. The injection of auxiliary feedwater to the steam generators, combined with the quick-opening of the steam bypass control valves (SBCVs), caused reactor coolant temperature to decrease, which resulted in a primary system pressure decrease below the low pressurizer pressure setpoint of 1837 pounds per square inch absolute (psia). Valid ESFAS actuations of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure. The event was diagnosed as an uncomplicated reactor trip. By approximately 1559 MST on February 4, 1993, the plant was stabilized in Mode 3 (HOT STANDBY).<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73. This LER also serves as a Special Report prepared and submitted pursuant to Technical Specification (TS) 3.5.2 ACTION b and TS 6.9.2.
530 | 5301993004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301993004R00.pdf | 1993-11-03 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 3 | P | CE | PO | 24 | On November 3, 1993, at approximately 1619 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 24 percent power when Control Room personnel manually tripped the reactor when it was recognized that subgroup 5 of control element assembly (CEA) regulating group 4 had slipped into the reactor core during reactor power reduction. All CEAs inserted as designed. The reactor trip was followed by a Main Turbine/Main Generator trip. By approximately 1630 MST on November 3, 1993, the plant was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor diagnosed the event as an uncomplicated reactor trip. No Engineered Safety Feature Actuation System actuations occurred and none were required. All plant equipment responded as designed. <br /><br /> The cause of the subgroup 5 of CEA regulating group 4 slip could not be determined. No problems or abnormalities that could have contributed to the subgroup slip were found during the performance of the troubleshooting. Since the event could not be recreated, APS management determined that the most probable components that could cause the event (i.e., subgroup 5 supply breaker and phase synchronizing cards) would be replaced.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
530 | 5301994005 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301994005R00.pdf | 1994-08-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On August 19, 1994, at approximately 1319 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 1 (SG-1) water level reached the Reactor Protection System trip setpoint for low steam generator water level following the degradation of main feedwater flow. Immediately following the reactor trip, a low steam generator water level alarm annunciated for SG-1, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of the Auxiliary Feedwater Actuation System (AFAS-1) on low-low steam generator water level for SG-1. The Steam Bypass Control System responded as designed to control the secondary system pressure. Required plant equipment and safety systems responded to the event as designed. No other ESF actuations occurred and none were required. Steam generator water level was restored to normal using auxiliary feedwater flow. The Control Room Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 1356 MST on August 19, 1994, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip was initiated by an unexplained and unwarranted closing of the economizer valve on SG-1 which was later determined to be caused by an intermittent component failure of the feedwater control system (FWCS-1), most probably the master controller or associated circuitry. As corrective action, the controller was replaced.
530 | 5301994007 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301994007R00.pdf | 1994-08-30 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Palo Verde 3 | P | CE | PO | 100 | On August 30, 1994, at approximately 1500 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for high steam generator water level caused by an increase in main feedwater (MFW) flow. In addition to the reactor trip, the unit received an Engineered Safety Feature Actuation System (ESFAS) actuation of the Main Steam Isolation System (MSIS A and MSIS B) on high steam generator water level for SG-2. The MSIS necessitated the use by Control Room personnel of the auxiliary feedwater pump (AFWP-B) and the atmospheric dump valves (ADVs) to control secondary heat removal (AFWP-B was used to feed the steam generators and the ADVs were used to stabilize secondary temperature and pressure). Required plant equipment and safety systems responded to the event as designed. No other ESF actuations occurred and none were required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 1530 MST on August 30, 1994, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip on high SG-2 water level was initiated by a malfunction in the Feedwater Control System (FWCS-2) which was attributed to a failed FWCS-2 master controller power fuse. As corrective action, the master controller was replaced.
530 | 5281996004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5281996004R00.pdf | 1996-08-10 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | At approximately 1549 MST on August 10, 1996, Palo Verde Units 1 and 3 were operating at approximately 100 percent power, when both reactors tripped on low departure from nucleate boiling ratio (DNBR) following a major grid perturbation. The grid perturbation was characterized by an initial substantial load decrease followed by a significant load demand increase. The reactor trip was generated due to power exceeding the variable over power trip (VOPT) setpoint within the core protection calculators (CPC). Power exceeded the VOPT setpoint when steam bypass control system (SBCS) valves (SBCV) opened in response to turbine load fluctuations induced by the grid perturbation. By approximately 1645 MST, both plants were stabilized in Mode 3 (HOT STANDBY) and the Unit 1 and Unit 3 shift supervisors classified the events as uncomplicated reactor trips. There were no ESF actuations and none were required. Required plant equipment and safety systems responded to the event as designed in each unit. <br /><br /> The grid disturbance originated in the Pacific Northwest when soaring temperatures wilted power lines, some of which sagged into trees and 'flashed-over' or short-circuited. The grid disturbance resulted in a massive Western power outage. As stated above, because the initiating event was a major grid perturbation and not a full load rejection, the generator output current decrease was only momentary. The opening of the SBCVs resulted in a reactor power transient and subsequent reactor trip.
530 | 5301997002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5301997002R00.pdf | 1997-05-31 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On May 31, 1997, at approximately 2312 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred following the spurious opening of all four reactor trip switchgear (RTSG) breakers. The core protection calculator (CPC) generated a low departure from nucleate boiling ratio (DNBR) signal due to all control element assemblies (CEA) inserting. By approximately 2325 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor classified the event as an uncomplicated reactor trip. There were no engineered safety features (ESF) actuations and none were required. Required safety systems responded to the event as designed.The preliminary cause of all four RTSG breakers spuriously opening, and the subsequent reactor trip was attributed to a combination of two incorrectly assembled ring-tongue terminals, in conjunction with a missing jumper on the spare trip parameter, all within the BD matrix logic of the plant protection system (PPS). Maintenance and engineering personnel were troubleshooting previous spurious RTSG breaker openings at the time of the reactor trip. The wiring error and termination deficiencies are believed to have occurred during original construction by Combustion Engineering/Electro-Mechanics. The lugs were replaced and the jumper was installed. The other 5 matrices in Unit 3 were visually verified to have their jumpers installed.No previous similar events have been reported pursuant to 10CFR50.73.
530 | 5302001001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302001001R00.pdf | 2001-05-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 3 | P | CE | PO | 19 | On May 19, 2001 at 0306 Mountain Standard Time (MST), Unit 3 was in MODE 1 (Power Operation), at approximately 19 percent rated thermal power when the reactor automatically tripped on an Axial Shape Index (ASI) auxiliary trip signal from the Core Protection Calculator (CPC). Unit 3 was operating at 19 percent power to accommodate corrective maintenance to resolve a high vibration problem on the main turbine. The root cause of the trip was that the downpower game plan did not include CPC ASI predictions, Axial Offset Anomaly (AOA) effects on ASI, or previous downpower differences between predicted ASI and the core operating limit supervisory system (COLSS) ASI.There has been one similar event reported within the last three years in LER 2-2000-007-00.re changes and training.
530 | 5302003004 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302003004R00.pdf | 2003-07-28 | QR5 | Turbine Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 98 | On July 28, 2003, Unit 3 was in MODE 1. At approximately 18:54 Mountain Standard Time (MST), a sub-synchronous relay Lockout Trip was received during a grid perturbation resulting in a Main Turbine Trip. The reactor tripped from approximately 98% power on a Core Protection Calculator generated anticipatory Low DNBR Trip (Reactor Coolant Pump speed coast-down) when the automatic Fast Bus Transfer did not successfully transfer house loads back onto offsite power sources. Fast Bus Transfer logic prevented transfer due to momentary low voltage on the alternate supplies as a result of the fault. The subsequent loss of the 13.8kV non-class busses resulted in a loss of power to non-safety related AC buses. Another local utility, (Salt River Project) was performing switching operations in the Hassayampa Switchyard just prior to the grid disturbance. A human performance error left a grounding switch closed during the switching operation and a three-phase fault to ground occurred on the Hassayampa to Arlington Valley 500kV line, relaying off area power plants, including PVNGS Unit-3.The Control Room Supervisor diagnosed this event as a Loss of Forced Circulation, and the appropriate Emergency Operating Procedure (EOP: LOOP/LOFC) was entered. No Emergency Plan classification was required. On July 29, 2003 at approximately 00:44 MST, RCP 1A was restarted, restoring forced circulation. RCP lB was started a short time later. Unit 3 transitioned from the Loss of Forced Circulation EOP to the Mode 3 to Mode 5 Normal Operating Procedure. In the past three years, the station has not experienced a Reactor Trip with loss of Forced Circulation due to an Electrical Grid Disturbance.
530 | 5302004002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302004002R01.pdf | 2004-06-07 | QR3 | Reactivity Control Imbalance | [45 empty] | Palo Verde 3 | P | CE | PO | 99 | On June 7, 2004 at approximately 1458 hours (MST), Unit 3 was operating in Mode 1, Power Operations, at approximately 99 percent power when the main turbine intercept valves fast closed and the control valves ramped closed. The reactor power cutback and steam bypass control systems (RPCB and SBCS) responded to the large decrease in steam flow by inserting group 4 and 5 control rods into the core and opening steam bypass valves to reduce reactor power and maintain reactor coolant temperature. Approximately 10 seconds after the RPCB occurred, a low Departure from Nucleate Boiling Ratio (DNBR) reactor trip was initiated by the core protection calculators (CPCs) as a result of rodded radial peaking factor for the control rod configuration.The reason the main turbine intercept valves fast closed and the control valves ramped closed was attributed to a malfunction in the electro-hydraulic system. The cause of the reactor trip has been attributed to a diminished DNBR margin as a result of the rodded radial peaking factor for the control rod configuration that existed following the RPCB.Subsequent to this event, a similar event occurred when Unit 2 experienced a main turbine trip, RPCB, and subsequent reactor trip on low DNBR on July 14, 2004.
530 | 5282004006 | https://lersearch.inl.gov/PDFView.ashx?DOC::5282004006R01.pdf | 2004-06-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Palo Verde 3 | P | CE | PO | 100 | On June 14, 2004, at approximately 07:41 MST, a ground-fault occurred on the Western Area Power Authority 230kV Liberty substation to Westwing substation line (approximately 47 miles from the Palo Verde Nuclear Generating Station). A failure in the protective relaying resulted in the ground-fault not isolating from the local grid for approximately 38 seconds. The fault cascaded into the protective tripping of a number of 230kV and 525kV transmission lines, which ultimately led to the Loss of Offsite Power (LOOP) at the Palo Verde switchyard. In Unit 1 and 2, the LOOP caused each reactor to trip from 100 percent power on a Core Protection Calculator generated reactor trip on low Departure from Nucleate Boiling Ratio due to low Reactor Coolant Pump (RCP) shaft speed. Unit 3 tripped last and experienced a Variable Over Power Trip from approximately 109 percent power due to increased flow from the RCPs caused by an increase in voltage and frequency from the main turbine generator.The LOOP placed each Unit in a condition for "Notice of Unusual Event" (NUE). The Unit 2 Train "A"emergency diesel generator started, but failed to maintain electrical output during load sequencing and resulted in the declaration of an "Alert" in Unit 2 at 07:54 MST. The NUE for Units 1 & 3 was declared at 07:58 MST.No similar condition has been reported in the past three years.
530 | 5302006002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302006002R00.pdf | 2006-03-05 | QR8 | Spurious Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On March 5, 2006 at 07:10 Mountain Standard Time (MST) Palo Verde Unit 3 was in Mode 1 (Power Operations), operating at approximately 100 percent power, when an automatic reactor trip occurred on a low Departure from Nucleate Boiling Ratio (DNBR) input. The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to an invalid Control Element Assembly Calculator (CEAC) input. CEAC number 1 sensed positional data for Control Element Assembly (CEA) 60 that exceeded the allowed deviation and as a result generated a high penalty factor which was transmitted to all four CPC channels. This high penalty factor resulted in a CPC DNBR trip output, as per design. The reactor was stabilized in Mode 3 (HOT STANDBY), and the Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required.The cause of the reactor trip was an electronic component failure on a circuit board that caused an invalid (CEA) position deviation to CEAC number 1. The circuit board was replaced and the Unit was restarted.In the past three years, Palo Verde reported Reactor Protection System (RPS) actuations, but none associated with the same root cause.
530 | 5302006005 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302006005R01.pdf | 2006-07-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 3 | P | CE | PO | 55 | On July 1, 2006 at approximately 19:28 Mountain Standard Time (MST) Unit 3 was in Mode 1, Power Operation, at approximately 100 percent rated thermal power when a sight glass on a condensate demineralizer ruptured. This resulted in a low pressure condition at the suctions for both main feedwater pumps. One of the pumps tripped causing a reactor power cutback and subsequent decrease in reactor power to approximately 55 percent rated thermal power. Suction pressure to the other main feedwater pump remained low and a control room operator manually tripped the reactor. No engineered safety feature system actuations occurred and none were required.The sight glass rupture occurred because of undetected defects to the glass. The root cause was alternatives to single pane borosilicate glass were not recognized as being needed. The sight glass was replaced. The station will install condensate demineralizer sight glasses that are more resistant to catastrophic failiure.No similar event has been reported in the last three years.
530 | 5302006007 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302006007R00.pdf | 2006-10-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On October 19, 2006 at about 1147 Mountain Standard Time, Unit 3 was operating in Mode 1, Power Operation, at approximately 100% power when control room personnel initiated a manual reactor trip in response to lowering condenser hotwell level which had caused two of the three operating condensate pumps to trip coincident with degrading condenser vacuum.The cause of the hotwell level and condenser vacuum reduction was determined to be a failed open air operated valve on the condensate demineralizer drain header which created an opening from condenser shell "C" to atmosphere. The root cause of the event was determined to be that the challenge to the unit posed by degraded condenser vacuum created by an open SCN-UV-232 valve concurrent with condensate demineralizer service vessel draining evolutions was not addressed through single point vulnerability reviews. Procedures have been changed to require an in-line manual valve to be closed except during specific demineralizer rinsing operation.
530 | 5302008001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302008001R01.pdf | 2008-09-16 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 60 | On September 16, 2008, Unit 3 Operations personnel identified Motor Generator (MG) set 'A' was showing indications of being motorized due to an over-excited condition on MG set 'B'. The Control Element Drive Mechanism (CEDM) MG sets A and B supply power to the CEDM bus and are normally operated in parallel in order to support Control Element Assembly (CEA) movement in group mode. During trouble shooting activities, the 'B' MG set was removed from service while MG set 'A' provided power to the CEDMs. Upon removal from service, an undervoltage condition occurred on the CEDM system that resulted in a main turbine trip and initiated a reactor power cutback. Consistent with contingency actions established in the trouble shooting plan, a manual reactor trip was initiated.The direct cause of the MG set 'B' condition was the failure of a transistor on the excitation voltage power supply circuit board. One design-related root cause was identified for this event. The MG set 'B' excitation voltage regulation and suppression circuit boards were replaced. A plant modification which allows operators to override a failed automatic voltage regulator circuit on a degraded MG set until the load is shifted to the other MG set has been approved and is scheduled to be installed in all three units.Unit 3 was restarted on September 19, 2008.
530 | 5302008002 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302008002R00.pdf | 2008-09-27 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 34 | On September 27, 2008, at approximately 21:51 hours, Mountain Standard Time, Unit 3 control room operators initiated a manual reactor trip from approximately 34% rated thermal power in response to high vibrations on the main turbine. The main turbine vibrations were experienced during a required power reduction resulting from a steam generator chemistry excursion. The event was considered an uncomplicated reactor trip. No automatic engineered safety feature (ESF) actuations occurred during the event and none were required. All safety related buses remained energized from normal offsite power during and following the reactor trip.The cause of the reportable event was the decision by control room operators to initiate a manual reactor trip in response to the main turbine high vibrations. The operators chose to initiate the reactor trip earlier than intended in the planned shutdown in response to the high turbine vibrations. The reactor trip was not necessary to mitigate the consequences of the event.There have been manual reactor trips in the past at Palo Verde Nuclear Generating Station but none with causes similar to this event. As such, the corrective actions for those events would not have prevented this event.
530 | 5302009001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302009001R00.pdf | 2009-12-03 | QR6 | Manual Reactor Trip | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On December 3, 2009, at approximately 04:31, Mountain Standard Time, Unit 3 control room operators initiated a manual reactor trip from approximately 100 percent rated thermal power in response to a loss of instrument air (IA) to the containment building. The loss of IA caused a closure of the reactor coolant pump (RCP) seal bleed off isolation valve, redirecting RCP seal bleed off from the volume control tank (VCT) to the reactor drain tank (RDT). To prevent overfilling and breaching the RDT rupture disc, plant operators initiated a manual reactor trip. After tripping the reactor, all four RCPs were tripped and RCP seal bleed off was secured. Forced circulation was restored at 10:58 when a temporary modification was installed which aligned nitrogen to the IA system. No automatic engineered safety feature (ESF) actuations occurred during the event and none were required. All safety related buses remained energized from normal offsite power during and following the reactor trip.A solenoid coil failure on instrument air containment isolation valve (3JIAAUV0002) caused a loss of IA to the containment building. Consequently, the RCP seal bleed off isolation valve to the VCT closed which redirected RCP seal bleed off to the RDT and led plant operators to the decision to manually trip the reactor. The failed solenoid valve coil was replaced prior to restarting Unit 3 on December 5, 2009.Palo Verde Nuclear Generating Station reported a manual reactor trip of unit 2 in LER 529-2003-001-00 where instrument air was lost. The failure mechanism of the previous event was not similar to this event, and as such, the corrective actions for that event would not have prevented this event.
530 | 5302011001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302011001R00.pdf | 2011-01-19 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palo Verde 3 | P | CE | PO | 100 | On January 19, 2011, at approximately 1840 Mountain Standard Time, Unit 3 was at 100 percent power at normal operating temperature and normal operating pressure when the main feedwater pump A minimum flow recirculation valve (mini-flow valve) failed open causing a percentage of feedwater flow to be diverted to the condenser. Subsequently, Unit 3 experienced a reactor power cutback when main feedwater pump B tripped on low suction pressure. The combination of the main feedwater pump B trip and the main feedwater pump A mini-flow valve failure caused both steam generator water levels to lower causing an automatic reactor trip. Both steam generator levels continued to drop which initiated an auxiliary feedwater actuation signal. The plant was stabilized in Mode 3.The failed open mini-flow valve was caused by a failed diaphragm in a pneumatic 3-way precision relay within the mini-flow valve control loop. The relay was replaced and Unit 3 was returned to 100 percent power on January 23, 2011, at approximately 0100.No similar conditions have been reported by Palo Verde in the past three years.
530 | 5302018001 | https://lersearch.inl.gov/PDFView.ashx?DOC::5302018001R01.pdf | 2018-06-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palo Verde 3 | P | CE | PO | 100 | On June 27, 2018, at approximately 2257 Mountain Standard Time, the PVNGS Unit 3 Control Room received a feedwater control system trouble alarm due to a steam generator feedwater economizer valve position/demand deviation. Interaction with the malfunctioning economizer valve resulted in an unplanned movement of the economizer valve in the closed direction. This caused the main feedwater pump (MFWP) discharge pressure to increase tripping one of two operating MFWPs. This resulted in a rapid decrease in Steam Generator (SG) level that actuated a reactor protection system trip on low SG water level. Water level then rapidly rose to the SG high level trip set point because the malfunctioning economizer valve did not close. At that point an automatic main steam isolation signal occurred, requiring manual actuation of the auxiliary feedwater and essential spray pond (ultimate heat sink) systems. <br /><br /> The cause of the event was attributed to an auxiliary operator taking an action contrary to station requirements to block air venting from an economizer trip valve causing the valve to move in the closed direction.<br /><br /> Corrective actions include enhanced operations training on responding to economizer valve failures, specifically, and prescripted events placing operators in a perceived sense of urgency. Additional guidance and operating experience will be incorporated into the alarm response procedure for the feedwater control system.<br /><br /> No similar conditions have been reported by PVNGS in the past three years.
2020-01-28 12:01